## C207 B-F
Dimensions: Steel Pipe Flanges per AWWA C207 - Class B - F
US Units only
Note: Refer to ANSI/AWWA C207 for notes, design pressures, and additional minimum design requirements.
Note: Any column with "-" could relate to a note in the Standard or not be covered in the standard.
Note: Data columns from the reference standard may have been omitted
Note: All units are inches
AWWA Class | Nominal Pipe Size (NPS) | OD Flange (A) in. | ID Flange (B) in. | Bolt Number | Bolt Circle Diameter (C) in. | Diameter of Bolts in. | Flange Thickness (T)in.
B | 4 | 9 | 4.57 | 8 | 7.5 | 0.625 | 0.625
B | 5 | 10 | 5.66 | 8 | 8.5 | 0.75 | 0.625
B | 6 | 11 | 6.72 | 8 | 9.5 | 0.75 | 0.688
B | 8 | 13.5 | 8.72 | 8 | 11.75 | 0.75 | 0.688
B | 10 | 16 | 10.88 | 12 | 14.25 | 0.875 | 0.688
B | 12 | 19 | 12.88 | 12 | 17 | 0.875 | 0.688
B | 14 | 21 | 14.19 | 12 | 18.75 | 1 | 0.688
B | 16 | 23.5 | 16.19 | 16 | 21.25 | 1 | 0.688
B | 18 | 25 | 18.19 | 16 | 22.75 | 1.125 | 0.688
B | 20 | 27.5 | 20.19 | 20 | 25 | 1.125 | 0.688
B | 22 | 29.5 | 22.19 | 20 | 27.25 | 1.25 | 0.75
B | 24 | 32 | 24.19 | 20 | 29.5 | 1.25 | 0.75
B | 26 | 34.25 | — | 24 | 31.75 | 1.25 | 0.812
B | 28 | 36.5 | — | 28 | 34 | 1.25 | 0.875
B | 30 | 38.75 | — | 28 | 36 | 1.25 | 0.875
B | 32 | 41.75 | — | 28 | 38.5 | 1.5 | 0.938
B | 34 | 43.75 | — | 32 | 40.5 | 1.5 | 0.938
B | 36 | 46 | — | 32 | 42.75 | 1.5 | 1
B | 38 | 48.75 | — | 32 | 45.25 | 1.5 | 1
B | 40 | 50.75 | — | 36 | 47.25 | 1.5 | 1
B | 42 | 53 | — | 36 | 49.5 | 1.5 | 1.125
B | 44 | 55.25 | — | 40 | 51.75 | 1.5 | 1.125
B | 46 | 57.25 | — | 40 | 53.75 | 1.5 | 1.125
B | 48 | 59.5 | — | 44 | 56 | 1.5 | 1.25
B | 50 | 61.75 | — | 44 | 58.25 | 1.75 | 1.25
B | 52 | 64 | — | 44 | 60.5 | 1.75 | 1.25
B | 54 | 66.25 | — | 44 | 62.75 | 1.75 | 1.375
B | 60 | 73 | — | 52 | 69.25 | 1.75 | 1.5
B | 66 | 80 | — | 52 | 76 | 1.75 | 1.625
B | 72 | 86.5 | — | 60 | 82.5 | 1.75 | 1.75
B | 78 | 93 | — | 64 | 89 | 2 | 2
B | 84 | 99.75 | — | 64 | 95.5 | 2 | 2
B | 90 | 106.5 | — | 68 | 102 | 2.25 | 2.25
B | 96 | 113.25 | — | 68 | 108.5 | 2.25 | 2.25
B | 102 | 120 | — | 72 | 114.5 | 2.5 | 2.5
B | 108 | 126.75 | — | 72 | 120.75 | 2.5 | 2.5
B | 114 | 133.5 | — | 76 | 126.75 | 2.75 | 2.75
B | 120 | 140.25 | — | 76 | 132.75 | 2.75 | 2.75
B | 126 | 147 | — | 80 | 139.25 | 3 | 3
B | 132 | 153.75 | — | 80 | 145.75 | 3 | 3
B | 144 | 167.25 | — | 84 | 158.25 | 3.25 | 3.25
D | 4 | 9 | 4.57 | 8 | 7.5 | 0.625 | 0.625
D | 5 | 10 | 5.66 | 8 | 8.5 | 0.75 | 0.625
D | 6 | 11 | 6.72 | 8 | 9.5 | 0.75 | 0.688
D | 8 | 13.5 | 8.72 | 8 | 11.75 | 0.75 | 0.688
D | 10 | 16 | 10.88 | 12 | 14.25 | 0.875 | 0.688
D | 12 | 19 | 12.88 | 12 | 17 | 0.875 | 0.812
D | 14 | 21 | 14.19 | 12 | 18.75 | 1 | 0.938
D | 16 | 23.5 | 16.19 | 16 | 21.25 | 1 | 1
D | 18 | 25 | 18.19 | 16 | 22.75 | 1.125 | 1.062
D | 20 | 27.5 | 20.19 | 20 | 25 | 1.125 | 1.125
D | 22 | 29.5 | 22.19 | 20 | 27.25 | 1.25 | 1.188
D | 24 | 32 | 24.19 | 20 | 29.5 | 1.25 | 1.25
D | 26 | 34.25 | — | 24 | 31.75 | 1.25 | 1.312
D | 28 | 36.5 | — | 28 | 34 | 1.25 | 1.312
D | 30 | 38.75 | — | 28 | 36 | 1.25 | 1.375
D | 32 | 41.75 | — | 28 | 38.5 | 1.5 | 1.5
D | 34 | 43.75 | — | 32 | 40.5 | 1.5 | 1.5
D | 36 | 46 | — | 32 | 42.75 | 1.5 | 1.625
D | 38 | 48.75 | — | 32 | 45.25 | 1.5 | 1.625
D | 40 | 50.75 | — | 36 | 47.25 | 1.5 | 1.625
D | 42 | 53 | — | 36 | 49.5 | 1.5 | 1.75
D | 44 | 55.25 | — | 40 | 51.75 | 1.5 | 1.75
D | 46 | 57.25 | — | 40 | 53.75 | 1.5 | 1.75
D | 48 | 59.5 | — | 44 | 56 | 1.5 | 1.875
D | 50 | 61.75 | — | 44 | 58.25 | 1.75 | 2
D | 52 | 64 | — | 44 | 60.5 | 1.75 | 2
D | 54 | 66.25 | — | 44 | 62.75 | 1.75 | 2.125
D | 60 | 73 | — | 52 | 69.25 | 1.75 | 2.25
D | 66 | 80 | — | 52 | 76 | 1.75 | 2.5
D | 72 | 86.5 | — | 60 | 82.5 | 1.75 | 2.625
D | 78 | 93 | — | 64 | 89 | 2 | 2.75
D | 84 | 99.75 | — | 64 | 95.5 | 2 | 2.875
D | 90 | 106.5 | — | 68 | 102 | 2.25 | 3
D | 96 | 113.25 | — | 68 | 108.5 | 2.25 | 3.25
D | 102 | 120 | — | 72 | 114.5 | 2.5 | 3.25
D | 108 | 126.75 | — | 72 | 120.75 | 2.5 | 3.375
D | 114 | 133.5 | — | 76 | 126.75 | 2.75 | 3.5
D | 120 | 140.25 | — | 76 | 132.75 | 2.75 | 3.5
D | 126 | 147 | — | 80 | 139.25 | 3 | 3.75
D | 132 | 153.75 | — | 80 | 145.75 | 3 | 3.875
D | 144 | 167.25 | — | 84 | 158.25 | 3.25 | 4.125
E | 4 | 9 | 4.57 | 8 | 7.5 | 0.625 | 1.125
E | 5 | 10 | 5.66 | 8 | 8.5 | 0.75 | 1.188
E | 6 | 11 | 6.72 | 8 | 9.5 | 0.75 | 1.313
E | 8 | 13.5 | 8.72 | 8 | 11.75 | 0.75 | 1.5
E | 10 | 16 | 10.88 | 12 | 14.25 | 0.875 | 1.563
E | 12 | 19 | 12.88 | 12 | 17 | 0.875 | 1.75
E | 14 | 21 | 14.19 | 12 | 18.75 | 1 | 1.875
E | 16 | 23.5 | 16.19 | 16 | 21.25 | 1 | 2
E | 18 | 25 | 18.19 | 16 | 22.75 | 1.125 | 2.125
E | 20 | 27.5 | 20.19 | 20 | 25 | 1.125 | 2.375
E | 22 | 29.5 | 22.19 | 20 | 27.25 | 1.25 | 2.5
E | 24 | 32 | 24.19 | 20 | 29.5 | 1.25 | 2.625
E | 26 | 34.25 | — | 24 | 31.75 | 1.25 | 2.75
E | 28 | 36.5 | — | 28 | 34 | 1.25 | 2.75
E | 30 | 38.75 | — | 28 | 36 | 1.25 | 2.875
E | 32 | 41.75 | — | 28 | 38.5 | 1.5 | 3
E | 34 | 43.75 | — | 32 | 40.5 | 1.5 | 3
E | 36 | 46 | — | 32 | 42.75 | 1.5 | 3.125
E | 38 | 48.75 | — | 32 | 45.25 | 1.5 | 3.125
E | 40 | 50.75 | — | 36 | 47.25 | 1.5 | 3.25
E | 42 | 53 | — | 36 | 49.5 | 1.5 | 3.375
E | 44 | 55.25 | — | 40 | 51.75 | 1.5 | 3.375
E | 46 | 57.25 | — | 40 | 53.75 | 1.5 | 3.438
E | 48 | 59.5 | — | 44 | 56 | 1.5 | 3.5
E | 50 | 61.75 | — | 44 | 58.25 | 1.75 | 3.5
E | 52 | 64 | — | 44 | 60.5 | 1.75 | 3.625
E | 54 | 66.25 | — | 44 | 62.75 | 1.75 | 3.75
E | 60 | 73 | — | 52 | 69.25 | 1.75 | 3.875
E | 66 | 80 | — | 52 | 76 | 1.75 | 4.25
E | 72 | 86.5 | — | 60 | 82.5 | 1.75 | 4.375
E | 78 | 93 | — | 64 | 89 | 2 | 4.75
E | 84 | 99.75 | — | 64 | 95.5 | 2 | 4.75
E | 90 | 106.5 | — | 68 | 102 | 2.25 | 5.125
E | 96 | 113.25 | — | 68 | 108.5 | 2.25 | 5.125
E | 102 | 120 | — | 72 | 114.5 | 2.5 | 5.5
E | 108 | 126.75 | — | 72 | 120.75 | 2.5 | 5.5
E | 114 | 133.5 | — | 76 | 126.75 | 2.75 | 5.875
E | 120 | 140.25 | — | 76 | 132.75 | 2.75 | 5.875
E | 126 | 147 | — | 80 | 139.25 | 3 | 6.25
E | 132 | 153.75 | — | 80 | 145.75 | 3 | 6.25
E | 144 | 167.25 | — | 84 | 158.25 | 3.25 | 6.75
F | 4 | 10 | 4.57 | 8 | 7.88 | 0.75 | 1.13
F | 5 | 11 | 5.66 | 8 | 9.25 | 0.75 | 1.21
F | 6 | 12.5 | 6.73 | 12 | 10.62 | 0.75 | 1.31
F | 8 | 15 | 8.73 | 12 | 13 | 0.875 | 1.31
F | 10 | 17.5 | 10.88 | 16 | 15.25 | 1 | 1.5
F | 12 | 20.5 | 12.88 | 16 | 17.75 | 1.125 | 1.63
F | 14 | 23 | 14.19 | 20 | 20.25 | 1.125 | 1.94
F | 16 | 25.5 | 16.19 | 20 | 22.5 | 1.25 | 2.14
F | 18 | 28 | 18.19 | 24 | 24.75 | 1.25 | 2.25
F | 20 | 30.5 | 20.19 | 24 | 27 | 1.25 | 2.33
F | 22 | 33 | 22.19 | 24 | 29.25 | 1.25 | 2.5
F | 24 | 36 | 24.19 | 24 | 32 | 1.5 | 2.69
F | 26 | 38.25 | — | 28 | 34.5 | 1.75 | 3
F | 28 | 40.75 | — | 28 | 37 | 1.75 | 3.13
F | 30 | 43 | — | 28 | 39.25 | 1.75 | 3.15
F | 32 | 45.25 | — | 28 | 41.5 | 1.75 | 3.25
F | 34 | 47.5 | — | 28 | 43.5 | 1.75 | 3.38
F | 36 | 50 | — | 32 | 46 | 2 | 3.46
F | 38 | 52.25 | — | 32 | 48 | 2 | 3.5
F | 40 | 54.25 | — | 36 | 50.25 | 2 | 3.63
F | 42 | 57 | — | 36 | 52.75 | 2 | 3.81
F | 44 | 59.25 | — | 36 | 55 | 2 | 4
F | 46 | 61.5 | — | 40 | 57.25 | 2 | 4.13
F | 48 | 65 | — | 40 | 60.75 | 2 | 4.5

## 16.1 25 - 250
Dimensions: Cast Iron Flanges per ASME B16.1 Class 25 - 250
[10 empty] | US & Metric Units Separated by yellow column |  |  |  | (US Unites, Inches) | Metric Units, milimeters)
Note: Refer to ANSI/ASME B16.1 for notes, pressures, and minimum design requirements.
Note: Any column with "-" relate to a note in the standard or may not be covered in the standard.
Note: Data columns from the reference standard may have been omitted
Note: US units are inches, Metric Units are milimeters
Note: Studs are measured parallel to the axis (L) from the first to the thread without the chamfers (points).
Note: Hex bolts are measured from under the head to the top of the bolt
ASME | Flange Class | Nominal Pipe Size (NPS) | Diameter Flange (O) | Min Thickness Flange (Q) | Hub- Min Diameter (X) | Hub- Min Length (Y) | Hub- Min Thread Length (T) | Raised Face Diameter (W) | Bolting- # of Bolts | Bolt Hole- Diameter Bolt Circle | Bolt Hole- Diameter Bolt Holes | Bolting- Bolt Diameter | Bolting- Length of Bolts | Bolting- Length of Stud Bolts | Diameter Flange (O) | Min Thickness Flange (Q) | Hub- Min Diameter (X) | Hub- Min Length (Y) | Hub- Min Thread Length (T) | Raised Face Diameter (W) | Bolting- # of Bolts | Bolt Hole- Diameter Bolt Circle | Bolt Hole- Diameter Bolt Holes | Bolting- Bolt Diameter | Bolting- Length of Bolts | Bolting- Length of Stud Bolts
16.1 | 25 | 4 | 9 | 0.75 | 5.31 | 1.31 | … | … | 8 | 7.5 | 0.75 | 0.625 | 2.5 | … | 230 | 19 | 135 | 33 | … | … | 8 | 191 | 19.05 | 15.875 | 64 | …
16.1 | 25 | 5 | 10 | 0.75 | 6.44 | 1.44 | … | … | 8 | 8.5 | 0.75 | 0.625 | 2.5 | … | 255 | 19 | 164 | 37 | … | … | 8 | 216 | 19.05 | 15.875 | 64 | …
16.1 | 25 | 6 | 11 | 0.75 | 7.56 | 1.56 | … | … | 8 | 9.5 | 0.75 | 0.625 | 2.5 | … | 280 | 19 | 192 | 40 | … | … | 8 | 241 | 19.05 | 15.875 | 64 | …
16.1 | 25 | 8 | 13.5 | 0.75 | 9.69 | 1.75 | … | … | 8 | 11.75 | 0.75 | 0.625 | 2.5 | … | 345 | 19 | 246 | 45 | … | … | 8 | 299 | 19.05 | 15.875 | 64 | …
16.1 | 25 | 10 | 16 | 0.88 | 11.94 | 1.94 | … | … | 12 | 14.25 | 0.75 | 0.625 | 3 | … | 405 | 22.2 | 303 | 49 | … | … | 12 | 368 | 19.05 | 15.875 | 70 | …
16.1 | 25 | 12 | 19 | 1 | 14.06 | 2.19 | … | … | 12 | 17 | 0.75 | 0.625 | 3 | … | 485 | 25.4 | 357 | 56 | … | … | 12 | 432 | 19.05 | 15.875 | 76 | …
16.1 | 25 | 14 | 21 | 1.12 | 15.37 | 2.25 | … | … | 12 | 18.75 | 0.875 | 0.75 | 3.5 | … | 535 | 28.6 | 391 | 57 | … | … | 12 | 476 | 22.225 | 19.05 | 89 | …
16.1 | 25 | 16 | 23.5 | 1.12 | 17.5 | 2.5 | … | … | 16 | 21.25 | 0.875 | 0.75 | 3.5 | … | 595 | 28.6 | 445 | 64 | … | … | 16 | 540 | 22.225 | 19.05 | 89 | …
16.1 | 25 | 18 | 25 | 1.25 | 19.62 | 2.69 | … | … | 16 | 22.75 | 0.875 | 0.75 | 4 | … | 635 | 31.8 | 498 | 68 | … | … | 16 | 578 | 22.225 | 19.05 | 95 | …
16.1 | 25 | 20 | 27.5 | 1.25 | 21.75 | 2.88 | … | … | 20 | 25 | 0.875 | 0.75 | 4 | … | 700 | 31.8 | 552 | 78 | … | … | 20 | 635 | 22.225 | 19.05 | 95 | …
16.1 | 25 | 24 | 32 | 1.38 | 26 | 3.25 | … | … | 20 | 29.5 | 0.875 | 0.75 | 4 | … | 815 | 34.9 | 560 | 83 | … | … | 20 | 749 | 22.225 | 19.05 | 102 | …
16.1 | 25 | 30 | 38.75 | 1.5 | … | … | … | … | 28 | 36 | 1 | 0.875 | 4.5 | … | 985 | 38.1 | … | … | … | … | 28 | 914 | 25.4 | 22.225 | 114 | …
16.1 | 25 | 36 | 46 | 1.62 | … | … | … | … | 32 | 42.75 | 1 | 0.875 | 5 | … | 1170 | 41.3 | … | … | … | … | 32 | 1085 | 25.4 | 22.225 | 121 | …
16.1 | 25 | 42 | 53 | 1.75 | … | … | … | … | 36 | 49.5 | 1.125 | 1 | 5.5 | … | 1345 | 44.5 | … | … | … | … | 36 | 1257 | 28.575 | 25.4 | 133 | …
16.1 | 25 | 48 | 59.5 | 2 | … | … | … | … | 44 | 56 | 1.125 | 1 | 6 | … | 1510 | 50.8 | … | … | … | … | 44 | 1422 | 28.575 | 25.4 | 146 | …
16.1 | 25 | 54 | 66.25 | 2.25 | … | … | … | … | 44 | 62.75 | 1.125 | 1 | 6.5 | … | 1685 | 57.2 | … | … | … | … | 44 | 1594 | 28.575 | 25.4 | 159 | …
16.1 | 25 | 60 | 73 | 2.25 | … | … | … | … | 52 | 69.25 | 1.25 | 1.125 | 6.5 | … | 1855 | 57.2 | … | … | … | … | 52 | 1759 | 31.75 | 28.575 | 159 | …
16.1 | 25 | 72 | 86.5 | 2.5 | … | … | … | … | 60 | 82.5 | 1.25 | 1.125 | 7 | … | 2195 | 63.5 | … | … | … | … | 60 | 2095 | 31.75 | 28.575 | 172 | …
16.1 | 25 | 84 | 99.75 | 2.75 | … | … | … | … | 64 | 95.5 | 1.375 | 1.25 | 7.5 | … | 2535 | 69.9 | … | … | … | … | 64 | 2425 | 34.925 | 31.75 | 191 | …
16.1 | 25 | 96 | 113.25 | 3 | … | … | … | … | 68 | 108.5 | 1.375 | 1.25 | 8 | … | 2875 | 76.2 | … | … | … | … | 68 | 2756 | 34.925 | 31.75 | 203 | …
16.1 | 125 | 1 | 4.25 | 0.44 | 1.94 | 0.69 | … | … | 4 | 3.12 | 0.625 | 0.5 | 2 | … | 110 | 11.1 | 49 | 18 | … | … | 4 | 79 | 15.875 | 12.7 | 45 | …
16.1 | 125 | 1.25 | 4.62 | 0.5 | 2.31 | 0.81 | … | … | 4 | 3.5 | 0.625 | 0.5 | 2 | … | 115 | 12.7 | 59 | 21 | … | … | 4 | 89 | 15.875 | 12.7 | 51 | …
16.1 | 125 | 1.5 | 5 | 0.56 | 2.56 | 0.88 | … | … | 4 | 3.88 | 0.625 | 0.5 | 2 | … | 125 | 14.3 | 65 | 22 | … | … | 4 | 98 | 15.875 | 12.7 | 51 | …
16.1 | 125 | 2 | 6 | 0.62 | 3.06 | 1 | … | … | 4 | 4.75 | 0.75 | 0.625 | 2.5 | … | 150 | 15.9 | 78 | 25 | … | … | 4 | 121 | 19.05 | 15.875 | 57 | …
16.1 | 125 | 2.5 | 7 | 0.69 | 3.56 | 1.12 | … | … | 4 | 5.5 | 0.75 | 0.625 | 2.5 | … | 180 | 17.5 | 91 | 29 | … | … | 4 | 140 | 19.05 | 15.875 | 64 | …
16.1 | 125 | 3 | 7.5 | 0.75 | 4.25 | 1.19 | … | … | 4 | 6 | 0.75 | 0.625 | 2.5 | … | 190 | 19 | 108 | 30 | … | … | 4 | 152 | 19.05 | 15.875 | 64 | …
16.1 | 125 | 3.5 | 8.5 | 0.81 | 4.81 | 1.25 | … | … | 8 | 7 | 0.75 | 0.625 | 3 | … | 215 | 20.6 | 122 | 32 | … | … | 8 | 178 | 19.05 | 15.875 | 70 | …
16.1 | 125 | 4 | 9 | 0.94 | 5.31 | 1.31 | … | … | 8 | 7.5 | 0.75 | 0.625 | 3 | … | 230 | 23.8 | 135 | 33 | … | … | 8 | 191 | 19.05 | 15.875 | 76 | …
16.1 | 125 | 5 | 10 | 0.94 | 6.44 | 1.44 | … | … | 8 | 8.5 | 0.875 | 0.75 | 3 | … | 255 | 23.8 | 164 | 37 | … | … | 8 | 216 | 22.225 | 19.05 | 76 | …
16.1 | 125 | 6 | 11 | 1 | 7.56 | 1.56 | … | … | 8 | 9.5 | 0.875 | 0.75 | 3.5 | … | 280 | 25.4 | 192 | 40 | … | … | 8 | 241 | 22.225 | 19.05 | 83 | …
16.1 | 125 | 8 | 13.5 | 1.12 | 9.69 | 1.75 | … | … | 8 | 11.75 | 0.875 | 0.75 | 3.5 | … | 345 | 28.6 | 246 | 45 | … | … | 8 | 299 | 22.225 | 19.05 | 89 | …
16.1 | 125 | 10 | 16 | 1.19 | 11.94 | 1.94 | … | … | 12 | 14.25 | 1 | 0.875 | 4 | … | 405 | 30.2 | 303 | 49 | … | … | 12 | 362 | 25.4 | 22.225 | 95 | …
16.1 | 125 | 12 | 19 | 1.25 | 14.06 | 2.19 | … | … | 12 | 17 | 1 | 0.875 | 4 | … | 485 | 31.8 | 357 | 56 | … | … | 12 | 432 | 25.4 | 22.225 | 95 | …
16.1 | 125 | 14 | 14 | 1.38 | 15.38 | 2.25 | … | … | 12 | 18.75 | 1.125 | 1 | 4.5 | … | 535 | 35.1 | 391 | 57 | … | … | 12 | 476 | 28.575 | 25.4 | 108 | …
16.1 | 125 | 16 | 23.5 | 1.44 | 17.5 | 2.5 | … | … | 16 | 21.25 | 1.125 | 1 | 4.5 | … | 595 | 36.5 | 445 | 64 | … | … | 16 | 540 | 28.575 | 25.4 | 114 | …
16.1 | 125 | 18 | 25 | 1.56 | 19.62 | 2.69 | … | … | 16 | 22.75 | 1.25 | 1.125 | 5 | … | 635 | 39.7 | 499 | 68 | … | … | 16 | 578 | 31.75 | 28.575 | 121 | …
16.1 | 125 | 20 | 27.5 | 1.69 | 21.75 | 2.88 | … | … | 20 | 25 | 1.25 | 1.125 | 5 | … | 700 | 42.9 | 553 | 73 | … | … | 20 | 635 | 31.75 | 28.575 | 127 | …
16.1 | 125 | 24 | 32 | 1.88 | 26 | 3.25 | … | … | 20 | 29.5 | 1.375 | 1.25 | 5.5 | … | 815 | 47.6 | 660 | 83 | … | … | 20 | 749 | 34.925 | 31.75 | 140 | …
16.1 | 125 | 30 | 38.75 | 2.12 | … | … | … | … | 28 | 36 | 1.375 | 1.25 | 6.5 | … | 985 | 54 | … | … | … | … | 28 | 914 | 34.925 | 31.75 | 159 | …
16.1 | 125 | 36 | 46 | 2.38 | … | … | … | … | 32 | 42.75 | 1.625 | 1.5 | 7 | 9 | 1170 | 60.3 | … | … | … | … | 32 | 1086 | 41.275 | 38.1 | 178 | 222
16.1 | 125 | 42 | 53 | 2.62 | … | … | … | … | 36 | 49.5 | 1.625 | 1.5 | 7.5 | 9.5 | 1345 | 66.7 | … | … | … | … | 36 | 1257 | 41.275 | 38.1 | 191 | 235
16.1 | 125 | 48 | 59.5 | 2.75 | … | … | … | … | 44 | 56 | 1.625 | 1.5 | 8 | 9.5 | 1510 | 69.9 | … | … | … | … | 44 | 1422 | 41.275 | 38.1 | 197 | 242
16.1 | 125 | 54 (-) | 66.25 | 3 | … | … | … | … | 44 | 62.75 | 2 | 1.75 | 8.5 | 10.5 | 1685 | 76.2 | … | … | … | … | 44 | 1594 | 50.8 | 44.45 | 216 | 267
16.1 | 125 | 60 (-) | 73 | 3.12 | … | … | … | … | 52 | 69.25 | 2 | 1.75 | 9 | 11 | 1855 | 79.4 | … | … | … | … | 52 | 1759 | 50.8 | 44.45 | 222 | 273
16.1 | 125 | 66 (-) | 80 | 3.38 | … | … | … | … | 52 | 76 | 2 | 1.75 | 9.5 | 11.5 | 2032 | 85.7 | … | … | … | … | 52 | 1930 | 50.8 | 44.45 | 241 | 292
16.1 | 125 | 72 (-) | 86.5 | 3.5 | … | … | … | … | 60 | 82.5 | 2 | 1.75 | 9.5 | 11.5 | 2195 | 88.9 | … | … | … | … | 60 | 2096 | 50.8 | 44.45 | 241 | 292
16.1 | 125 | 78 (-) | 93 | 3.75 | … | … | … | … | 64 | 89 | 2.25 | 2 | 10.5 | 12.5 | 2365 | 95.3 | … | … | … | … | 64 | 2261 | 57.15 | 50.8 | 267 | 318
16.1 | 125 | 84 (-) | 99.75 | 3.88 | … | … | … | … | 64 | 95.5 | 2.25 | 2 | 10.5 | 13 | 2535 | 98.4 | … | … | … | … | 64 | 2426 | 57.15 | 50.8 | 267 | 324
16.1 | 125 | 90 (-) | 106.5 | 4.12 | … | … | … | … | 68 | 102 | 2.5 | 2.25 | 11.5 | 14 | 2720 | 104.6 | … | … | … | … | 68 | 2591 | 63.5 | 57.15 | 292 | 357
16.1 | 125 | 96 (-) | 113.25 | 4.25 | … | … | … | … | 68 | 108.5 | 2.5 | 2.25 | 11.5 | 14 | 2875 | 108 | … | … | … | … | 68 | 2756 | 63.5 | 57.15 | 292 | 356
16.1 | 250 | 1 | 4.88 | 0.69 | 2.06 | 0.88 | 0.68 | 2.69 | 4 | 3.5 | 0.75 | 0.62 | 2.5 | … | 125 | 17.5 | 52 | 22 | 18 | 68 | 4 | 89 | 19.05 | 15.748 | 64 | …
16.1 | 250 | 1.25 | 5.25 | 0.75 | 2.5 | 1 | 0.81 | 3.06 | 4 | 3.88 | 0.75 | 0.62 | 2.5 | … | 135 | 19 | 64 | 25 | 19 | 78 | 4 | 98 | 19.05 | 15.748 | 64 | …
16.1 | 250 | 1.5 | 6.12 | 0.81 | 2.75 | 1.12 | 0.87 | 3.56 | 4 | 4.5 | 0.875 | 0.75 | 3 | … | 155 | 20.6 | 70 | 29 | 22 | 91 | 4 | 114 | 22.225 | 19.05 | 70 | …
16.1 | 250 | 2 | 6.5 | 0.88 | 3.31 | 1.25 | 1 | 4.19 | 8 | 5 | 0.75 | 0.62 | 3 | … | 165 | 22.2 | 84 | 32 | 25 | 106 | 8 | 127 | 19.05 | 15.748 | 70 | …
16.1 | 250 | 2.5 | 7.5 | 1 | 3.94 | 1.43 | 1.13 | 4.94 | 8 | 5.88 | 0.875 | 0.75 | 3.5 | … | 190 | 25.4 | 100 | 37 | 29 | 125 | 8 | 149 | 22.225 | 19.05 | 83 | …
16.1 | 250 | 3 | 8.25 | 1.12 | 4.62 | 1.56 | 1.19 | 5.69 | 8 | 6.62 | 0.875 | 0.75 | 3.5 | … | 210 | 28.6 | 118 | 40 | 31 | 144 | 8 | 168 | 22.225 | 19.05 | 89 | …
16.1 | 250 | 3.5 | 9 | 1.19 | 5.25 | 1.62 | 1.25 | 6.31 | 8 | 7.25 | 0.875 | 0.75 | 3.5 | … | 230 | 30.2 | 133 | 41 | 32 | 160 | 8 | 184 | 22.225 | 19.05 | 89 | …
16.1 | 250 | 4 | 10 | 1.25 | 5.75 | 1.75 | 1.31 | 6.94 | 8 | 7.88 | 0.875 | 0.75 | 4 | … | 255 | 31.8 | 146 | 44 | 33 | 176 | 8 | 200 | 22.225 | 19.05 | 95 | …
16.1 | 250 | 5 | 11 | 1.38 | 7 | 1.88 | 1.44 | 8.31 | 8 | 9.25 | 0.875 | 0.75 | 4 | … | 280 | 34.9 | 178 | 48 | 36 | 211 | 8 | 235 | 22.225 | 19.05 | 102 | …
16.1 | 250 | 6 | 12.5 | 1.44 | 8.12 | 1.94 | 1.56 | 9.69 | 12 | 10.62 | 0.875 | 0.75 | 4 | … | 320 | 36.5 | 206 | 49 | 39 | 246 | 12 | 270 | 22.225 | 19.05 | 102 | …
16.1 | 250 | 8 | 15 | 1.62 | 10.25 | 2.19 | 1.75 | 11.94 | 12 | 13 | 1.125 | 0.88 | 4.5 | … | 380 | 41.3 | 260 | 56 | 43 | 303 | 12 | 330 | 28.575 | 22.352 | 114 | …
16.1 | 250 | 10 | 17.5 | 1.88 | 12.62 | 2.38 | 1.94 | 14.06 | 16 | 15.25 | 1.25 | 1 | 5.5 | … | 445 | 47.6 | 321 | 60 | 49 | 357 | 16 | 387 | 31.75 | 25.4 | 131 | …
16.1 | 250 | 12 | 20.5 | 2 | 14.75 | 2.56 | 2.19 | 16.44 | 16 | 17.75 | 1.25 | 1.12 | 5.5 | … | 520 | 50.8 | 375 | 65 | 54 | 418 | 16 | 451 | 31.75 | 28.448 | 140 | …
16.1 | 250 | 14 | 23 | 2.12 | 16.25 | 2.69 | 2.25 | 18.94 | 20 | 20.25 | 1.375 | 1.12 | 6 | … | 585 | 54 | 413 | 68 | 57 | 481 | 20 | 514 | 34.925 | 28.448 | 152 | …
16.1 | 250 | 16 | 25 | 2.25 | 18.38 | 2.88 | 2.5 | 21.06 | 20 | 22.5 | 1.375 | 1.25 | 6.5 | … | 650 | 57.2 | 467 | 73 | 62 | 535 | 20 | 572 | 34.925 | 31.75 | 159 | …
16.1 | 250 | 18 | 28 | 2.38 | … | … | … | 23.31 | 24 | 24.75 | 1.375 | 1.25 | 6.5 | … | 710 | 60.3 | … | … | … | 592 | 24 | 629 | 34.925 | 31.75 | 165 | …
16.1 | 250 | 20 | 30.5 | 2.5 | … | … | … | 25.56 | 24 | 27 | 1.375 | 1.25 | 7 | … | 775 | 63.5 | … | … | … | 649 | 24 | 686 | 34.925 | 31.75 | 172 | …
16.1 | 250 | 24 | 36 | 2.75 | … | … | … | 30.31 | 24 | 32 | 1.625 | 1.5 | 7.5 | 9.5 | 915 | 69.8 | … | … | … | 770 | 24 | 813 | 41.275 | 38.1 | 191 | 241
16.1 | 250 | 30 | 43 | 3 | … | … | … | 37.19 | 28 | 39.25 | 2 | 1.75 | 8.5 | 10.5 | 1090 | 76.2 | … | … | … | 945 | 28 | 997 | 50.8 | 44.45 | 216 | 268
16.1 | 250 | 36 (-) | 50 | 3.38 | … | … | … | 43.69 | 32 | 46 | 2.25 | 2 | 9.5 | 12 | 1270 | 85.7 | … | … | … | 1110 | 32 | 1168 | 57.15 | 50.8 | 241 | 298
16.1 | 250 | 42 (-) | 57 | 3.69 | … | … | … | 50.44 | 36 | 52.75 | 2.25 | 2 | 10 | 12.5 | 1450 | 93.7 | … | … | … | 1281 | 36 | 1340 | 57.15 | 50.8 | 254 | 318
16.1 | 250 | 48 (-) | 65 | 4 | … | … | … | 58.44 | 40 | 60.75 | 2.25 | 2 | 11 | 13 | 1650 | 101.6 | … | … | … | 1484 | 40 | 1543 | 57.15 | 50.8 | 273 | 330

## 16.5 150_300
[14 empty] | Dimensions: Steel Pipe Flanges per ASME B16.5 Class 150 - 300 | [7 empty] | (US Unites, Inches) | Metric Units, milimeters)
US & Metric Units Separated by yellow column
Note: Refer to ANSI/ASME B16.5 for notes, pressures, and minimum design requirements.
Note: Any column with "-" relate to a note in the standard or is not be covered in the standard.
Note: Data columns from the reference standard may have been omitted
Note: US units are inches, Metric Units are milimeters
Note: Studs are measured parallel to the axis (L) from the first to the thread without the chamfers (points).
Note: Hex bolts are measured from under the head to the top of the bolt
| All | All | All | All | All | All | All | All | All | All | Th, SO, SW, WN | La | La | La | Th, SO, SW | SO, SW | WN | WN | WN, SW | SW | Th | Th | All | All | All | All | All | All | All | All | Th, SO, SW, WN | La | La | La | Th, SO, SW | SO, SW | WN | WN | WN, SW | SW | Th | Th
TYPE | Flange Class | Nominal Pipe Size (NPS) | Outside Diameter Flange (O) | Drilling-Diameter Bolt Circle (W) | Drilling-Diameter Bolt Holes | Drilling-Number of Bolts | Drilling-Bolt Diameter | Stud Bolts (L)-Raised Face | Machine Bolts (L) - Raised face | Diameter of Hub (X) | Min Thickness Flange (tf) | Min Thickness Lap Joint (tf) | Bore- Min Lapped (B2) | Length Through Hub- Lapped (Y2) | Length Through Hub-Threaded Slip on/Socket Welding (Y1) | Bore- Min Slip On Socket Weld (B1) | Diameter Beginning Chamfer Weld Neck (A) | Length Through Hub Bore Weld Neck (Y3) | Bore- Weld Neck/Socket Weld (B3) | Depth of socket (D) | Min Thread Length Threaded (T) | Min Counterbore Threaded Flange (Q) | Outside Diameter Flange (O) | Diameter Bolt Circle (W) | Drilling-Diameter Bolt Holes | Drilling-Number of Bolts | Drilling-Bolt Diameter | Stud Bolts (L)- Raised Face | Machine Bolts (L)- Raised Face | Diameter of Hub (X) | Min Thickness Flange (tf) | Min Thickness Lap Joint (tf) | Bore- Min Lapped (B2) | Length Through Hub- Lapped (Y2) | Length through Hub-Threaded/Slip-on/Socket Weld (Y1) mm | Bore- Min Slip On Socket Weld (B1) | Diameter Beginning Chamfer Welding Neck (A) | Length Through Bore- Welding Neck (Y3) | Bore- Weld Neck/Socket Weld (B3) | Depth of socket (D) | Min Thread Length Threaded (T) | Min Counterbore Threaded Flange (Q)
ASME 16.5 | 150 | 0.5 | 3.5 | 2.38 | 0.625 | 4 | 0.5 | 2.25 | 2 | 1.19 | 0.38 | 0.44 | 0.9 | 0.62 | 0.56 | 0.88 | 0.84 | 1.81 | 0.62 | 0.38 | 0.62 | - | 89 | 60.5 | 15.875 | 4 | 12.7 | 55 | 50 | 30 | 9.7 | 11.2 | 22.9 | 16 | 14 | 22.4 | 21.3 | 46 | 15.748 | 10 | 16 | -
ASME 16.5 | 150 | 0.75 | 3.88 | 2.75 | 0.625 | 4 | 0.5 | 2.5 | 2 | 1.5 | 0.44 | 0.5 | 1.11 | 0.62 | 0.56 | 1.09 | 1.05 | 2 | 0.82 | 0.44 | 0.62 | - | 99 | 69.8 | 15.875 | 4 | 12.7 | 65 | 50 | 38 | 11.2 | 12.7 | 28.2 | 16 | 14 | 27.7 | 26.7 | 51 | 20.8 | 11 | 16 | -
ASME 16.5 | 150 | 1 | 4.25 | 3.12 | 0.625 | 4 | 0.5 | 2.5 | 2.25 | 1.94 | 0.5 | 0.56 | 1.38 | 0.69 | 0.62 | 1.36 | 1.32 | 2.12 | 1.05 | 0.5 | 0.69 | - | 108 | 79.2 | 15.875 | 4 | 12.7 | 65 | 55 | 49 | 12.7 | 14.2 | 35.1 | 18 | 16 | 34.5 | 33.5 | 54 | 26.7 | 13 | 18 | -
ASME 16.5 | 150 | 1.25 | 4.62 | 3.5 | 0.625 | 4 | 0.5 | 2.75 | 2.25 | 2.31 | 0.56 | 0.62 | 1.72 | 0.81 | 0.75 | 1.7 | 1.66 | 2.19 | 1.38 | 0.56 | 0.81 | - | 117 | 88.9 | 15.875 | 4 | 12.7 | 70 | 55 | 59 | 14.2 | 15.7 | 43.7 | 21 | 19 | 43.2 | 42.2 | 56 | 35.1 | 14 | 21 | -
ASME 16.5 | 150 | 1.5 | 5 | 3.88 | 0.625 | 4 | 0.5 | 2.75 | 2.5 | 2.56 | 0.62 | 0.69 | 1.97 | 0.88 | 0.81 | 1.95 | 1.9 | 2.83 | 1.61 | 0.62 | 0.88 | - | 127 | 98.6 | 15.875 | 4 | 12.7 | 70 | 65 | 65 | 15.9 | 17.5 | 50 | 22 | 21 | 49.5 | 48.3 | 60 | 40.9 | 16 | 22 | -
ASME 16.5 | 150 | 2 | 6 | 4.75 | 0.75 | 4 | 0.625 | 3.25 | 2.75 | 3.06 | 0.69 | 0.75 | 2.46 | 1 | 0.94 | 2.44 | 2.38 | 2.44 | 2.07 | 0.69 | 1 | - | 152 | 120.6 | 19.05 | 4 | 15.875 | 85 | 70 | 78 | 17.5 | 19 | 62.5 | 25 | 24 | 61.9 | 60.5 | 62 | 52.6 | 18 | 25 | -
ASME 16.5 | 150 | 2.5 | 7 | 5.5 | 0.75 | 4 | 0.625 | 3.5 | 3 | 3.56 | 0.81 | 0.88 | 2.97 | 1.12 | 1.06 | 2.94 | 2.88 | 2.69 | 2.47 | 0.75 | 1.12 | - | 178 | 139.7 | 19.05 | 4 | 15.875 | 90 | 75 | 90 | 20.6 | 22.4 | 75.4 | 28 | 27 | 74.7 | 73.2 | 68 | 62.7 | 19 | 28 | -
ASME 16.5 | 150 | 3 | 7.5 | 6 | 0.75 | 4 | 0.625 | 3.5 | 3 | 4.25 | 0.88 | 0.94 | 3.6 | 1.19 | 1.12 | 3.57 | 3.5 | 2.69 | 3.07 | 0.81 | 1.19 | - | 190 | 152.4 | 19.05 | 4 | 15.875 | 90 | 75 | 108 | 22.4 | 23.9 | 91.4 | 30 | 28 | 90.7 | 88.9 | 68 | 78 | 21 | 30 | -
ASME 16.5 | 150 | 3.5 | 8.5 | 7 | 0.75 | 8 | 0.625 | 3.5 | 3 | 4.81 | 0.88 | 0.94 | 4.1 | 1.25 | 1.19 | 4.07 | 4 | 2.75 | 3.55 | 0.88 | 1.25 | - | 216 | 177.8 | 19.05 | 8 | 15.875 | 90 | 75 | 122 | 22.4 | 23.9 | 104.1 | 32 | 30 | 103.4 | 101.6 | 70 | 90.2 | 22.352 | 32 | -
ASME 16.5 | 150 | 4 | 9 | 7.5 | 0.75 | 8 | 0.625 | 3.5 | 3 | 5.31 | 0.88 | 0.94 | 4.6 | 1.31 | 1.25 | 4.57 | 4.5 | 2.94 | 4.03 | 0.94 | 1.31 | - | 229 | 190.5 | 19.05 | 8 | 15.875 | 90 | 75 | 135 | 22.4 | 23.9 | 116.8 | 33 | 32 | 116.1 | 114.3 | 75 | 102.4 | 23.876 | 33 | -
ASME 16.5 | 150 | 5 | 10 | 8.5 | 0.875 | 8 | 0.75 | 3.75 | 3.25 | 6.44 | 0.88 | 0.94 | 5.69 | 1.44 | 1.38 | 5.66 | 5.56 | 3.44 | 5.05 | 0.94 | 1.44 | - | 254 | 215.9 | 22.225 | 8 | 19.05 | 95 | 85 | 164 | 22.4 | 23.9 | 144.5 | 37 | 35 | 143.8 | 141.2 | 87 | 128.3 | 23.876 | 37 | -
ASME 16.5 | 150 | 6 | 11 | 9.5 | 0.875 | 8 | 0.75 | 4 | 3.25 | 7.56 | 0.94 | 1 | 6.75 | 1.56 | 1.5 | 6.72 | 6.63 | 3.44 | 6.07 | 1.6 | 1.56 | - | 279 | 241.3 | 22.225 | 8 | 19.05 | 100 | 85 | 192 | 23.9 | 25.4 | 171.4 | 40 | 38 | 170.7 | 168.4 | 87 | 154.2 | 40.64 | 40 | -
ASME 16.5 | 150 | 8 | 13.5 | 11.75 | 0.875 | 8 | 0.75 | 4.25 | 3.5 | 9.69 | 1.06 | 1.12 | 8.75 | 1.75 | 1.69 | 8.72 | 8.63 | 3.94 | 7.98 | 1.25 | 1.75 | - | 343 | 298.4 | 22.225 | 8 | 19.05 | 110 | 90 | 246 | 26.9 | 28.4 | 222.2 | 44 | 43 | 221.5 | 219.2 | 100 | 202.7 | 31.75 | 44 | -
ASME 16.5 | 150 | 10 | 16 | 14.25 | 1 | 12 | 0.875 | 4.5 | 4 | 12 | 1.12 | 1.19 | 10.92 | 1.94 | 1.88 | 10.88 | 10.75 | 3.94 | 10.02 | 1.31 | 1.94 | - | 406 | 362 | 25.4 | 12 | 22.225 | 115 | 100 | 305 | 28.4 | 30.2 | 277.4 | 49 | 48 | 276.4 | 273 | 100 | 254.5 | 33.274 | 49 | -
ASME 16.5 | 150 | 12 | 19 | 17 | 1 | 12 | 0.875 | 4.75 | 4 | 14.38 | 1.19 | 1.25 | 12.92 | 2.19 | 2.12 | 12.88 | 12.75 | 4.44 | 12 | 1.56 | 2.19 | - | 483 | 431.8 | 25.4 | 12 | 22.225 | 120 | 100 | 365 | 30.2 | 31.8 | 328.2 | 56 | 54 | 327.2 | 323.8 | 113 | 304.8 | 39.624 | 56 | -
ASME 16.5 | 150 | 14 | 21 | 18.75 | 1.125 | 12 | 1 | 5.25 | 4.5 | 15.75 | 1.31 | 1.38 | 14.18 | 3.12 | 2.19 | 14.14 | 14 | 4.94 | - | 1.63 | 2.25 | - | 533 | 476.2 | 28.575 | 12 | 25.4 | 135 | 115 | 400 | 33.3 | 35.1 | 360.2 | 79 | 56 | 359.2 | 355.6 | 125 | - | 41.402 | 57 | -
ASME 16.5 | 150 | 16 | 23.5 | 21.25 | 1.125 | 16 | 1 | 5.25 | 4.5 | 18 | 1.38 | 1.44 | 16.19 | 3.44 | 2.44 | 16.16 | 16 | 4.94 | - | 1.75 | 2.5 | - | 597 | 539.8 | 28.575 | 16 | 25.4 | 135 | 115 | 457 | 35.1 | 36.6 | 411.2 | 87 | 62 | 410.5 | 406.4 | 125 | - | 44.45 | 64 | -
ASME 16.5 | 150 | 18 | 25 | 22.75 | 1.25 | 16 | 1.125 | 5.75 | 5 | 19.88 | 1.5 | 1.56 | 18.2 | 3.81 | 2.62 | 18.18 | 18 | 5.44 | - | 1.94 | 2.69 | - | 635 | 577.8 | 31.75 | 16 | 28.575 | 145 | 125 | 505 | 38.1 | 39.6 | 462.3 | 97 | 67 | 461.8 | 457.2 | 138 | - | 49.276 | 68 | -
ASME 16.5 | 150 | 20 | 27.5 | 25 | 1.25 | 20 | 1.125 | 6.25 | 5.5 | 22 | 1.62 | 1.69 | 20.25 | 4.06 | 2.81 | 20.2 | 20 | 5.62 | - | 2.13 | 2.88 | - | 693 | 635 | 31.75 | 20 | 28.575 | 160 | 140 | 559 | 41.1 | 42.9 | 514.4 | 103 | 71 | 513.1 | 508 | 143 | - | 54.102 | 73 | -
ASME 16.5 | 150 | 22 | 29.5 | 27.25 | 1.375 | 20 | 1.25 | 6.75 | 6 | 24 | 1.75 | 1.81 | 22.25 | 4.25 | 3.06 | 22.22 | 22 | 5.82 | - | 2.38 | 3.13 | - | 749 | 692.2 | 34.925 | 20 | 31.75 | 170 | 150 | 610 | 44.4 | 46 | 565.2 | 108 | 78 | 564.4 | 558.8 | 148 | - | 60.452 | 80 | -
ASME 16.5 | 150 | 24 | 32 | 29.5 | 1.375 | 20 | 1.25 | 6.75 | 6 | 26.12 | 1.81 | 1.88 | 24.25 | 4.38 | 3.19 | 24.25 | 24 | 5.94 | - | 2.5 | 3.25 | - | 813 | 749.3 | 34.925 | 20 | 31.75 | 170 | 150 | 663 | 46 | 47.8 | 616 | 111 | 81 | 616 | 609.6 | 151 | - | 63.5 | 83 | -
ASME 16.5 | 300 | 0.5 | 3.75 | 2.62 | 0.625 | 4 | 0.5 | 2.5 | 2.25 | 1.5 | 0.5 | 0.56 | 0.9 | 0.88 | 0.81 | 0.88 | 0.84 | 2 | 0.62 | 0.38 | 0.62 | 0.93 | 95 | 66.5 | 15.875 | 4 | 12.7 | 65 | 55 | 38 | 12.7 | 14.2 | 22.9 | 22 | 21 | 22.4 | 21.3 | 51 | 15.7 | 10 | 16 | 23.6
ASME 16.5 | 300 | 0.75 | 4.62 | 3.25 | 0.75 | 4 | 0.625 | 3 | 2.5 | 1.88 | 0.56 | 0.62 | 1.11 | 1 | 0.94 | 1.09 | 1.05 | 2.19 | 0.82 | 0.44 | 0.62 | 1.14 | 117 | 82.6 | 19.05 | 4 | 15.875 | 75 | 65 | 48 | 14.2 | 15.7 | 28.2 | 25 | 24 | 27.7 | 26.7 | 56 | 20.8 | 11 | 16 | 29
ASME 16.5 | 300 | 1 | 4.88 | 3.5 | 0.75 | 4 | 0.625 | 3 | 2.5 | 2.12 | 0.62 | 0.69 | 1.38 | 1.06 | 1 | 1.36 | 1.32 | 2.38 | 1.05 | 0.5 | 0.69 | 1.41 | 124 | 88.9 | 19.05 | 4 | 15.875 | 75 | 65 | 54 | 15.7 | 17.5 | 35.1 | 27 | 25 | 34.5 | 33.5 | 60 | 26.7 | 13 | 18 | 35.8
ASME 16.5 | 300 | 1.25 | 5.25 | 3.88 | 0.75 | 4 | 0.625 | 3.25 | 2.75 | 2.5 | 0.69 | 0.75 | 1.72 | 1.06 | 1 | 1.7 | 1.66 | 2.5 | 1.38 | 0.56 | 0.81 | 1.75 | 133 | 98.6 | 19.05 | 4 | 15.875 | 85 | 70 | 64 | 17.5 | 19 | 43.7 | 27 | 25 | 43.2 | 42.2 | 64 | 35.1 | 14 | 21 | 44.4
ASME 16.5 | 300 | 1.5 | 6.12 | 4.5 | 0.875 | 4 | 0.75 | 3.5 | 3 | 2.75 | 0.75 | 0.81 | 1.97 | 1.16 | 1.13 | 1.95 | 1.9 | 2.63 | 1.61 | 0.62 | 0.88 | 1.98 | 155 | 114.3 | 22.225 | 4 | 19.05 | 90 | 75 | 70 | 19 | 20.6 | 50 | 30 | 29 | 49.5 | 48.3 | 67 | 40.9 | 16 | 22 | 50.3
ASME 16.5 | 300 | 2 | 6.5 | 5 | 0.75 | 8 | 0.625 | 3.5 | 3 | 3.31 | 0.81 | 0.88 | 2.46 | 1.31 | 1.25 | 2.44 | 2.38 | 2.69 | 2.07 | 0.69 | 1.12 | 2.5 | 165 | 127 | 19.05 | 8 | 15.875 | 90 | 75 | 84 | 20.6 | 22.4 | 62.5 | 33 | 32 | 62 | 60.5 | 68 | 52.6 | 17 | 28 | 63.5
ASME 16.5 | 300 | 2.5 | 7.5 | 5.88 | 0.875 | 8 | 0.75 | 4 | 3.25 | 3.94 | 0.94 | 1 | 2.97 | 1.5 | 1.44 | 2.94 | 2.88 | 2.94 | 2.47 | 0.75 | 1.25 | 3 | 190 | 149.4 | 22.225 | 8 | 19.05 | 100 | 85 | 100 | 23.9 | 25.4 | 75.4 | 38 | 37 | 74.7 | 73.2 | 75 | 62.7 | 19 | 32 | 76.2
ASME 16.5 | 300 | 3 | 8.25 | 6.62 | 0.875 | 8 | 0.75 | 4.25 | 3.5 | 4.62 | 1.06 | 1.12 | 3.6 | 1.69 | 1.63 | 3.57 | 3.5 | 3.06 | 3.07 | 0.81 | 1.25 | 3.63 | 210 | 168.1 | 22.225 | 8 | 19.05 | 110 | 90 | 117 | 26.9 | 28.4 | 91.4 | 43 | 41 | 90.7 | 88.9 | 78 | 78 | 21 | 32 | 92.2
ASME 16.5 | 300 | 3.5 | 9 | 7.25 | 0.875 | 8 | 0.75 | 4.25 | 3.75 | 5.25 | 1.12 | 1.19 | 4.1 | 1.75 | 1.69 | 4.07 | 4 | 3.13 | 3.55 | … | 1.44 | 4.13 | 229 | 184.2 | 22.225 | 8 | 19.05 | 110 | 95 | 133 | 28.4 | 30.2 | 104.1 | 44 | 43 | 103.4 | 101.6 | 80 | 90.2 | … | 37 | 104.9
ASME 16.5 | 300 | 4 | 10 | 7.88 | 0.875 | 8 | 0.75 | 4.5 | 3.75 | 5.75 | 1.19 | 1.25 | 4.6 | 1.88 | 1.82 | 4.57 | 4.5 | 3.32 | 4.03 | … | 1.44 | 4.63 | 254 | 200.2 | 22.225 | 8 | 19.05 | 115 | 95 | 146 | 30.2 | 31.8 | 116.8 | 48 | 46 | 116.1 | 114.3 | 84 | 102.4 | … | 37 | 117.6
ASME 16.5 | 300 | 5 | 11 | 9.25 | 0.875 | 8 | 0.75 | 4.75 | 4.25 | 7 | 1.31 | 1.38 | 5.69 | 2 | 1.94 | 5.66 | 5.56 | 3.82 | 5.05 | … | 1.69 | 5.69 | 279 | 235 | 22.225 | 8 | 19.05 | 120 | 110 | 178 | 33.3 | 35.1 | 144.5 | 51 | 49 | 143.8 | 141.2 | 97 | 128.3 | … | 43 | 144.5
ASME 16.5 | 300 | 6 | 12.5 | 10.62 | 0.875 | 12 | 0.75 | 4.75 | 4.25 | 8.12 | 1.38 | 1.44 | 6.75 | 2.06 | 2 | 6.72 | 6.63 | 3.82 | 6.07 | … | 1.81 | 6.75 | 318 | 269.7 | 22.225 | 12 | 19.05 | 120 | 110 | 206 | 35.1 | 36.6 | 171.4 | 52 | 51 | 170.7 | 168.4 | 97 | 154.2 | … | 46 | 171.4
ASME 16.5 | 300 | 8 | 15 | 13 | 1 | 12 | 0.875 | 5.5 | 4.75 | 10.25 | 1.56 | 1.62 | 8.75 | 2.44 | 2.38 | 8.72 | 8.63 | 4.32 | 7.98 | … | 2 | 8.75 | 381 | 330.2 | 25.4 | 12 | 22.225 | 140 | 120 | 260 | 39.6 | 41.1 | 222.2 | 62 | 60 | 221.5 | 219.2 | 110 | 202.7 | … | 51 | 222.2
ASME 16.5 | 300 | 10 | 17.5 | 15.25 | 1.125 | 16 | 1 | 6.25 | 5.5 | 12.62 | 1.81 | 1.88 | 10.92 | 3.75 | 2.56 | 10.88 | 10.75 | 4.56 | 10.02 | … | 2.19 | 10.88 | 444 | 387.4 | 28.575 | 16 | 25.4 | 160 | 140 | 321 | 46 | 47.8 | 277.4 | 95 | 65 | 276.4 | 273 | 116 | 254.5 | … | 56 | 276.4
ASME 16.5 | 300 | 12 | 20.5 | 17.75 | 1.25 | 16 | 1.125 | 6.75 | 5.75 | 14.75 | 1.94 | 2 | 12.92 | 4 | 2.82 | 12.88 | 12.75 | 5.06 | 12 | … | 2.38 | 12.94 | 521 | 450.8 | 31.75 | 16 | 28.575 | 170 | 145 | 375 | 49.3 | 50.8 | 328.2 | 102 | 72 | 327.2 | 323.8 | 129 | 304.8 | … | 60 | 328.7
ASME 16.5 | 300 | 14 | 23 | 20.25 | 1.25 | 20 | 1.125 | 7 | 6.25 | 16.75 | 2.06 | 2.12 | 14.18 | 4.38 | 2.94 | 14.14 | 14 | 5.56 | - | … | 2.5 | 14.19 | 584 | 514.4 | 31.75 | 20 | 28.575 | 180 | 160 | 425 | 52.3 | 53.8 | 360.2 | 111 | 75 | 359.2 | 355.6 | 141 | - | … | 64 | 360.4
ASME 16.5 | 300 | 16 | 25.5 | 22.5 | 1.375 | 20 | 1.25 | 7.5 | 6.5 | 19 | 2.19 | 2.25 | 16.19 | 4.75 | 3.19 | 16.16 | 16 | 5.69 | - | … | 2.69 | 16.19 | 648 | 571.5 | 34.925 | 20 | 31.75 | 190 | 165 | 483 | 55.6 | 57.2 | 411.2 | 121 | 81 | 410.5 | 406.4 | 145 | - | … | 68 | 411.2
ASME 16.5 | 300 | 18 | 28 | 24.75 | 1.375 | 24 | 1.25 | 7.75 | 6.75 | 21 | 2.31 | 2.38 | 18.2 | 5.12 | 3.44 | 18.18 | 18 | 6.19 | - | … | 2.75 | 18.19 | 711 | 628.6 | 34.925 | 24 | 31.75 | 195 | 170 | 533 | 58.7 | 60.5 | 462.3 | 130 | 87 | 461.8 | 457.2 | 157 | - | … | 70 | 462
ASME 16.5 | 300 | 20 | 30.5 | 27 | 1.375 | 24 | 1.25 | 8 | 7.25 | 23.12 | 2.44 | 2.5 | 20.25 | 5.5 | 3.69 | 20.2 | 20 | 6.32 | - | … | 2.88 | 20.19 | 775 | 685.8 | 34.925 | 24 | 31.75 | 205 | 185 | 587 | 62 | 63.5 | 514.4 | 140 | 94 | 513.1 | 508 | 161 | - | … | 73 | 512.8
ASME 16.5 | 300 | 22 | 33 | 29.25 | 1.625 | 24 | 1.5 | 9 | 8 | 25.25 | 2.56 | 2.62 | 22.25 | 5.69 | 3.94 | 22.22 | 22 | 6.44 | - | … | … | … | 838 | 743 | 41.275 | 24 | 38.1 | 230 | 205 | 641 | 65 | 66.5 | 565.2 | 145 | 100 | 564.4 | 558.8 | 164 | - | … | … | …
ASME 16.5 | 300 | 24 | 36 | 32 | 1.625 | 24 | 1.5 | 9 | 8 | 27.62 | 2.69 | 2.75 | 24.25 | 6 | 4.13 | 24.25 | 24 | 6.56 | - | … | 3.25 | 24.19 | 914 | 812.8 | 41.275 | 24 | 38.1 | 230 | 205 | 702 | 68.3 | 68.8 | 616 | 152 | 105 | 616 | 609.6 | 167 | - | … | 83 | 614.4

## 16.5 400-2500
[20 empty] | (US Unites, Inches) | Metric Units, milimeters)
Dimensions: Steel Pipe Flanges per ASME B16.5 Class 400 - 2500
US & Metric Units Separated by yellow column
Note: Refer to ANSI/ASME B16.5 for notes, pressures, and minimum design requirements.
Note: Any column with "-" relate to a note in the standard or is not be covered in the standard.
Note: Data columns from the reference standard may have been omitted
Note: US units are inches, Metric Units are milimeters
Note: Studs are measured parallel to the axis (L) from the first to the thread without the chamfers (points).
Note: Hex bolts are measured from under the head to the top of the bolt
| All | All | All | All | All | All | All | All | All | All | All | La | La | Th, SO, SW | SO, SW | WN | WN | SW | Th | Th | All | All | All | All | All | All | All | All | All | La | La | Th, SO, SW | SO, SW | WN | WN | SW | Th | Th
TYPE | Flange Class | Nominal Pipe Size (NPS) | Outside Diameter Flange (O) | Drilling-Diameter Bolt Circle (W) | Drilling-Diameter Bolt Holes | Drilling-Number of Bolts | Drilling-Bolt Diameter | Stud Bolts (L)-Raised Face | Machine Bolts (L) - Raised face | Diameter of Hub (X) | Min Thickness Flange (tf) | Bore- Min Lapped (B2) | Length Through Hub- Lapped (Y2) | Length Through Hub-Threaded Slip on/Socket Welding (Y1) | Bore- Min Slip On Socket Weld (B1) | Diameter Beginning Chamfer Welding Neck (A) | Length Through Hub Bore Welding Neck (Y3) | Depth of socket (D) | Min Thread Length Threaded (T) | Min Counterbore Threaded Flange (Q) | Outside Diameter Flange (O) | Diameter Bolt Circle (W) | Drilling-Diameter Bolt Holes | Drilling-Number of Bolts | Drilling-Bolt Diameter | Stud Bolts (L)- Raised Face | Machine Bolts (L)- Raised Face | Diameter of Hub (X) | Min Thickness Flange (tf) | Bore- Min Lapped (B2) | Length Through Hub- Lapped (Y2) | Length through Hub-Threaded/Slip-on/Socket Weld (Y1) | Bore- Min Slip On Socket Weld (B1) | Diameter Beginning Chamfer Welding Neck (A) | Length Through Bore- Welding Neck (Y3) | Depth of socket (D) | Min Thread Length Threaded (T) | Min Counterbore Threaded Flange (Q)
ASME 16.5 | 400 | 0.5 | 3.75 | 2.62 | 0.625 | 4 | 0.5 | - | - | 1.5 | 0.56 | 0.9 | 0.88 | 0.88 | 0.88 | 0.84 | 2.06 | 0.38 | 0.62 | - | 95 | 66.5 | 15.875 | 4 | 12.7 | - | - | 38.1 | 14.224 | 22.86 | 22.352 | 22.352 | - | - | - | - | - | -
ASME 16.5 | 400 | 0.75 | 4.62 | 3.25 | 0.75 | 4 | 0.625 | - | - | 1.88 | 0.62 | 1.11 | 1 | 1 | 1.09 | 1.05 | 2.25 | 0.44 | 0.62 | - | 117 | 82.6 | 19.05 | 4 | 15.875 | - | - | 47.752 | 15.748 | 28.194 | 25.4 | 25.4 | - | - | - | - | - | -
ASME 16.5 | 400 | 1 | 4.88 | 3.5 | 0.75 | 4 | 0.625 | - | - | 2.12 | 0.69 | 1.38 | 1.06 | 1.06 | 1.36 | 1.32 | 2.44 | 0.5 | 0.69 | - | 124 | 88.9 | 19.05 | 4 | 15.875 | - | - | 53.848 | 17.526 | 35.052 | 26.924 | 26.924 | - | - | - | - | - | -
ASME 16.5 | 400 | 1.25 | 5.25 | 3.88 | 0.75 | 4 | 0.625 | - | - | 2.5 | 0.81 | 1.72 | 1.12 | 1.12 | 1.7 | 1.66 | 2.62 | 0.56 | 0.81 | - | 133 | 98.6 | 19.05 | 4 | 15.875 | - | - | 63.5 | 20.574 | 43.688 | 28.448 | 28.448 | - | - | - | - | - | -
ASME 16.5 | 400 | 1.5 | 6.12 | 4.5 | 0.875 | 4 | 0.75 | - | - | 2.75 | 0.88 | 1.97 | 1.25 | 1.25 | 1.95 | 1.9 | 2.75 | 0.62 | 0.88 | - | 155 | 114.3 | 22.225 | 4 | 19.05 | - | - | 69.85 | 22.352 | 50.038 | 31.75 | 31.75 | - | - | - | - | - | -
ASME 16.5 | 400 | 2 | 6.5 | 5 | 0.75 | 8 | 0.625 | - | - | 3.31 | 1 | 2.46 | 1.44 | 1.44 | 2.44 | 2.38 | 2.88 | 0.69 | 1.12 | - | 165 | 127 | 19.05 | 8 | 15.875 | - | - | 84.074 | 25.4 | 62.484 | 36.576 | 36.576 | - | - | - | - | - | -
ASME 16.5 | 400 | 2.5 | 7.5 | 5.88 | 0.875 | 8 | 0.75 | - | - | 3.94 | 1.12 | 2.97 | 1.62 | 1.62 | 2.94 | 2.88 | 3.12 | 0.75 | 1.25 | - | 190 | 149.4 | 22.225 | 8 | 19.05 | - | - | 100.076 | 28.448 | 75.438 | 41.148 | 41.148 | - | - | - | - | - | -
ASME 16.5 | 400 | 3 | 8.25 | 6.62 | 0.875 | 8 | 0.75 | - | - | 4.62 | 1.25 | 3.6 | 1.81 | 1.81 | 3.57 | 3.5 | 3.25 | 0.81 | 1.38 | - | 210 | 168.1 | 22.225 | 8 | 19.05 | - | - | 117.348 | 31.75 | 91.44 | 45.974 | 45.974 | - | - | - | - | - | -
ASME 16.5 | 400 | 3.5 | 9 | 7.25 | 1 | 8 | 0.875 | - | - | 5.25 | 1.38 | 4.1 | 1.94 | 1.94 | 4.07 | 4 | 3.38 | - | 1.56 | - | 229 | 184.2 | 25.4 | 8 | 22.225 | - | - | 133.35 | 35.052 | 104.14 | 49.276 | 49.276 | - | - | - | - | - | -
ASME 16.5 | 400 | 4 | 10 | 7.88 | 1 | 8 | 0.875 | 5.5 | 5.25 | 5.75 | 1.38 | 4.63 | 2 | 2 | 4.57 | 4.5 | 3.5 | - | 1.44 | 4.63 | 254 | 200.2 | 25.4 | 8 | 22.225 | 140 | 135 | 146.05 | 35.052 | 117.602 | 50.8 | 50.8 | 116.1 | 114.3 | 51 | - | 37 | 117.6
ASME 16.5 | 400 | 5 | 11 | 9.25 | 1 | 8 | 0.875 | 5.75 | 5.25 | 7 | 1.5 | 5.69 | 2.12 | 2.12 | 5.66 | 5.56 | 4 | - | 1.69 | 5.69 | 279 | 235 | 25.4 | 8 | 22.225 | 145 | 135 | 177.8 | 38.1 | 144.526 | 53.848 | 53.848 | 143.8 | 141.2 | 54 | - | 43 | 144.5
ASME 16.5 | 400 | 6 | 12.5 | 10.62 | 1 | 12 | 0.875 | 6 | 5.75 | 8.12 | 1.62 | 6.75 | 2.25 | 2.25 | 6.72 | 6.63 | 4.06 | - | 1.81 | 6.75 | 318 | 269.7 | 25.4 | 12 | 22.225 | 150 | 145 | 206.248 | 41.148 | 171.45 | 57.15 | 57.15 | 170.7 | 168.4 | 57 | - | 46 | 171.4
ASME 16.5 | 400 | 8 | 15 | 13 | 1.125 | 12 | 1 | 6.75 | 6.5 | 10.25 | 1.88 | 8.75 | 2.69 | 2.69 | 8.72 | 8.63 | 4.62 | - | 2 | 8.75 | 381 | 330.2 | 28.575 | 12 | 25.4 | 170 | 165 | 260.35 | 47.752 | 222.25 | 68.326 | 68.326 | 221.5 | 219.2 | 68 | - | 51 | 222.2
ASME 16.5 | 400 | 10 | 17.5 | 15.25 | 1.25 | 16 | 1.125 | 7.5 | 7.25 | 12.62 | 2.12 | 10.92 | 4 | 2.88 | 10.88 | 10.75 | 4.88 | - | 2.19 | 10.88 | 444 | 387.4 | 31.75 | 16 | 28.575 | 190 | 185 | 320.548 | 53.848 | 277.368 | 101.6 | 101.6 | 276.4 | 273 | 73 | - | 56 | 276.4
ASME 16.5 | 400 | 12 | 20.5 | 17.75 | 1.375 | 16 | 1.25 | 8 | 7.75 | 14.75 | 2.25 | 12.92 | 4.25 | 3.12 | 12.88 | 12.75 | 5.38 | - | 2.38 | 12.94 | 521 | 450.8 | 34.925 | 16 | 31.75 | 205 | 195 | 374.65 | 57.15 | 328.168 | 107.95 | 107.95 | 327.2 | 323.8 | 79 | - | 60 | 328.7
ASME 16.5 | 400 | 14 | 23 | 20.25 | 1.375 | 20 | 1.25 | 8.25 | 8 | 16.75 | 2.38 | 14.18 | 4.62 | 3.31 | 14.14 | 14 | 5.88 | - | 2.5 | 14.19 | 584 | 514.4 | 34.925 | 20 | 31.75 | 210 | 205 | 425.45 | 60.452 | 360.172 | 117.348 | 117.348 | 359.2 | 355.6 | 84 | - | 64 | 360.4
ASME 16.5 | 400 | 16 | 25.5 | 23 | 1.5 | 20 | 1.375 | 8.75 | 8.5 | 19 | 2.5 | 16.19 | 5 | 3.69 | 16.16 | 16 | 6 | - | 2.69 | 16.19 | 648 | 571.5 | 38.1 | 20 | 34.925 | 220 | 215 | 482.6 | 63.5 | 411.226 | 127 | 127 | 410.5 | 406.4 | 94 | - | 68 | 411.2
ASME 16.5 | 400 | 18 | 28 | 24.75 | 1.5 | 24 | 1.375 | 9 | 8.75 | 21 | 2.62 | 18.2 | 5.38 | 3.88 | 18.18 | 18 | 6.5 | - | 2.75 | 18.19 | 711 | 628.6 | 38.1 | 24 | 34.925 | 230 | 220 | 533.4 | 66.548 | 462.28 | 136.652 | 136.652 | 461.8 | 457.2 | 99 | - | 70 | 462
ASME 16.5 | 400 | 20 | 30.5 | 27 | 1.625 | 24 | 1.5 | 9.5 | 9.25 | 23.12 | 2.75 | 20.25 | 5.75 | 4 | 20.2 | 20 | 6.62 | - | 2.88 | 20.19 | 775 | 685.8 | 41.275 | 24 | 38.1 | 240 | 235 | 587.248 | 69.85 | 514.35 | 146.05 | 146.05 | 513.1 | 508 | 102 | - | 73 | 512.8
ASME 16.5 | 400 | 22 | 33 | 29.25 | 1.75 | 24 | 1.625 | 10 | 9.75 | 25.25 | 2.88 | 22.25 | 6 | 4.25 | 22.22 | 22 | 6.75 | - | … | … | 838 | 743 | 44.45 | 24 | 41.275 | 255 | 250 | 641.35 | 73.152 | 565.15 | 152.4 | 152.4 | 564.4 | 558.8 | 108 | - | … | …
ASME 16.5 | 400 | 24 | 36 | 32 | 1.875 | 24 | 1.75 | 10.5 | 10.25 | 27.62 | 3 | 24.25 | 6.25 | 4.5 | 24.25 | 24 | 6.88 | - | 3.25 | 24.19 | 914 | 812.8 | 47.625 | 24 | 44.45 | 265 | 260 | 701.548 | 76.2 | 615.95 | 158.75 | 158.75 | 616 | 609.6 | 114 | - | 83 | 614.4
ASME 16.5 | 600 | 0.5 | 3.75 | 2.62 | 0.625 | 4 | 0.5 | 3 | 2.75 | 1.5 | 0.56 | 0.9 | 0.88 | 0.88 | 0.88 | 0.84 | 2.06 | 0.38 | 0.62 | 0.93 | 95 | 66.5 | 15.875 | 4 | 12.7 | 75 | 70 | 38.1 | 14.224 | 22.86 | 22.352 | 22.352 | 22.4 | 21.3 | 22 | 10 | 16 | 23.6
ASME 16.5 | 600 | 0.75 | 4.62 | 3.25 | 0.75 | 4 | 0.625 | 3.5 | 3.25 | 1.88 | 0.62 | 1.11 | 1 | 1 | 1.09 | 1.05 | 2.25 | 0.44 | 0.62 | 1.14 | 117 | 82.6 | 19.05 | 4 | 15.875 | 90 | 85 | 47.752 | 15.748 | 28.194 | 25.4 | 25.4 | 27.7 | 26.7 | 25 | 11 | 16 | 29
ASME 16.5 | 600 | 1 | 4.88 | 3.5 | 0.75 | 4 | 0.625 | 3.5 | 3.25 | 2.12 | 0.69 | 1.38 | 1.06 | 1.06 | 1.36 | 1.32 | 2.44 | 0.5 | 0.69 | 1.41 | 124 | 88.9 | 19.05 | 4 | 15.875 | 90 | 85 | 53.848 | 17.526 | 35.052 | 26.924 | 26.924 | 34.5 | 33.5 | 27 | 13 | 18 | 35.8
ASME 16.5 | 600 | 1.25 | 5.25 | 3.88 | 0.75 | 4 | 0.625 | 3.75 | 3.5 | 2.5 | 0.81 | 1.72 | 1.12 | 1.12 | 1.7 | 1.66 | 2.62 | 0.56 | 0.81 | 1.75 | 133 | 98.6 | 19.05 | 4 | 15.875 | 95 | 90 | 63.5 | 20.574 | 43.688 | 28.448 | 28.448 | 43.2 | 42.2 | 28 | 14 | 21 | 44.4
ASME 16.5 | 600 | 1.5 | 6.12 | 4.5 | 0.875 | 4 | 0.75 | 4.25 | 4 | 2.75 | 0.88 | 1.97 | 1.25 | 1.25 | 1.95 | 1.9 | 2.75 | 0.62 | 0.88 | 1.99 | 155 | 114.3 | 22.225 | 4 | 19.05 | 110 | 100 | 69.85 | 22.352 | 50.038 | 31.75 | 31.75 | 49.5 | 48.3 | 32 | 16 | 22 | 50.5
ASME 16.5 | 600 | 2 | 6.5 | 5 | 0.75 | 8 | 0.625 | 4.25 | 4 | 3.31 | 1 | 2.46 | 1.44 | 1.44 | 2.44 | 2.38 | 2.88 | 0.69 | 1.12 | 0.25 | 165 | 127 | 19.05 | 8 | 15.875 | 110 | 100 | 84.074 | 25.4 | 62.484 | 36.576 | 36.576 | 62 | 60.5 | 37 | 18 | 28 | 63.5
ASME 16.5 | 600 | 2.5 | 7.5 | 5.88 | 0.875 | 8 | 0.75 | 4.75 | 4.5 | 3.94 | 1.12 | 2.97 | 1.62 | 1.62 | 2.94 | 2.88 | 3.12 | 0.75 | 1.25 | 3 | 190 | 149.4 | 22.225 | 8 | 19.05 | 120 | 115 | 100.076 | 28.448 | 75.438 | 41.148 | 41.148 | 74.7 | 73.2 | 41 | 19 | 32 | 76.2
ASME 16.5 | 600 | 3 | 8.25 | 6.62 | 0.875 | 8 | 0.75 | 5 | 4.75 | 4.62 | 1.25 | 3.6 | 1.81 | 1.81 | 3.57 | 3.5 | 3.25 | 0.81 | 1.38 | 3.63 | 210 | 168.1 | 22.225 | 8 | 19.05 | 125 | 120 | 117.348 | 31.75 | 91.44 | 45.974 | 45.974 | 90.7 | 88.9 | 46 | 21 | 35 | 92.2
ASME 16.5 | 600 | 3.5 | 9 | 7.25 | 1 | 8 | 0.875 | 5.5 | 5.25 | 5.25 | 1.38 | 4.1 | 1.94 | 1.94 | 4.07 | 4 | 3.38 | … | 1.56 | 4.13 | 229 | 184.2 | 25.4 | 8 | 22.225 | 140 | 135 | 133.35 | 35.052 | 104.14 | 49.276 | 49.276 | 103.4 | 101.6 | 49 | … | 40 | 104.9
ASME 16.5 | 600 | 4 | 10.75 | 8.5 | 1 | 8 | 0.875 | 5.75 | 5.5 | 6 | 1.5 | 4.6 | 2.12 | 2.12 | 4.57 | 4.5 | 4 | … | 1.62 | 4.63 | 273 | 215.9 | 25.4 | 8 | 22.225 | 145 | 140 | 152.4 | 38.1 | 116.84 | 53.848 | 53.848 | 116.1 | 114.3 | 54 | … | 41 | 117.6
ASME 16.5 | 600 | 5 | 13 | 10.5 | 1.125 | 8 | 1 | 6.5 | 6.25 | 7.44 | 1.75 | 5.69 | 2.38 | 2.38 | 5.66 | 5.56 | 4.5 | … | 1.88 | 5.69 | 330 | 266.7 | 28.575 | 8 | 25.4 | 165 | 160 | 188.976 | 44.45 | 144.526 | 60.452 | 60.452 | 143.8 | 141.2 | 60 | … | 48 | 144.5
ASME 16.5 | 600 | 6 | 14 | 11.5 | 1.125 | 12 | 1 | 6.75 | 6.5 | 8.75 | 1.88 | 6.75 | 2.62 | 2.62 | 6.72 | 6.63 | 4.62 | … | 2 | 6.75 | 356 | 292.1 | 28.575 | 12 | 25.4 | 170 | 165 | 222.25 | 47.752 | 171.45 | 66.548 | 66.548 | 170.7 | 168.4 | 67 | … | 51 | 171.4
ASME 16.5 | 600 | 8 | 16.5 | 13.75 | 1.25 | 12 | 1.125 | 7.5 | 7.25 | 10.75 | 2.19 | 8.75 | 3 | 3 | 8.72 | 8.63 | 5.25 | … | 2.25 | 8.75 | 419 | 349.2 | 31.75 | 12 | 28.575 | 190 | 185 | 273.05 | 55.626 | 222.25 | 76.2 | 76.2 | 221.5 | 219.2 | 76 | … | 57 | 222.2
ASME 16.5 | 600 | 10 | 20 | 17 | 1.375 | 16 | 1.25 | 8.5 | 8.25 | 13.5 | 2.5 | 10.92 | 4.38 | 3.38 | 10.88 | 10.75 | 6 | … | 2.56 | 10.88 | 508 | 431.8 | 34.925 | 16 | 31.75 | 215 | 210 | 342.9 | 63.5 | 277.368 | 111.252 | 111.252 | 276.2 | 273 | 86 | … | 65 | 276.4
ASME 16.5 | 600 | 12 | 22 | 19.25 | 1.375 | 20 | 1.25 | 8.75 | 8.5 | 15.75 | 2.62 | 12.92 | 4.62 | 3.62 | 12.88 | 12.75 | 6.12 | … | 2.75 | 12.94 | 559 | 489 | 34.925 | 20 | 31.75 | 220 | 215 | 400.05 | 66.548 | 328.168 | 117.348 | 117.348 | 327 | 323.8 | 92 | … | 70 | 328.7
ASME 16.5 | 600 | 14 | 23.75 | 20.75 | 1.5 | 20 | 1.375 | 9.25 | 9 | 17 | 2.75 | 14.18 | 5 | 3.69 | 14.14 | 14 | 6.5 | … | 2.88 | 14.19 | 603 | 527 | 38.1 | 20 | 34.925 | 235 | 230 | 431.8 | 69.85 | 360.172 | 127 | 127 | 359.2 | 355.6 | 94 | … | 73 | 360.4
ASME 16.5 | 600 | 16 | 27 | 23.75 | 1.625 | 20 | 1.5 | 10 | 9.75 | 19.5 | 3 | 16.19 | 5.5 | 4.19 | 16.16 | 16 | 7 | … | 3.06 | 16.19 | 686 | 603.2 | 41.275 | 20 | 38.1 | 255 | 250 | 495.3 | 76.2 | 411.226 | 139.7 | 139.7 | 410.5 | 406.4 | 106 | … | 78 | 411.2
ASME 16.5 | 600 | 18 | 29.25 | 25.75 | 1.75 | 20 | 1.625 | 10.75 | 10.5 | 21.5 | 3.25 | 18.2 | 6 | 4.62 | 18.18 | 18 | 7.25 | … | 3.12 | 18.19 | 743 | 654 | 44.45 | 20 | 41.275 | 275 | 265 | 546.1 | 82.55 | 462.28 | 152.4 | 152.4 | 461.8 | 457.2 | 117 | … | 79 | 462
ASME 16.5 | 600 | 20 | 32 | 28.5 | 1.75 | 24 | 1.625 | 11.25 | 11 | 24 | 3.5 | 20.25 | 6.5 | 5 | 20.2 | 20 | 7.5 | … | 3.25 | 20.19 | 813 | 723.9 | 44.45 | 24 | 41.275 | 285 | 280 | 609.6 | 88.9 | 514.35 | 165.1 | 165.1 | 513.1 | 508 | 127 | … | 83 | 512.8
ASME 16.5 | 600 | 22 | 34.25 | 30.62 | 1.875 | 24 | 1.75 | 12 | … | 26.25 | 3.75 | 22.25 | 6.88 | 5.25 | 22.22 | 22 | 7.75 | … | … | … | 870 | 777.7 | 47.625 | 24 | 44.45 | 305 | … | 666.75 | 95.25 | 565.15 | 174.752 | 174.752 | 564.4 | 558.8 | 133 | … | … | …
ASME 16.5 | 600 | 24 | 37 | 33 | 2 | 24 | 1.875 | 13 | 12.75 | 28.25 | 4 | 24.25 | 7.25 | 5.5 | 24.25 | 24 | 8 | … | 3.62 | 24.19 | 940 | 838.2 | 50.8 | 24 | 47.625 | 330 | 325 | 717.55 | 101.6 | 615.95 | 184.15 | 184.15 | 616 | 609.6 | 140 | … | 92 | 614.4
ASME 16.5 | 900 | 0.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ASME 16.5 | 900 | 0.75 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ASME 16.5 | 900 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ASME 16.5 | 900 | 1.25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ASME 16.5 | 900 | 1.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ASME 16.5 | 900 | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ASME 16.5 | 900 | 2.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ASME 16.5 | 900 | 3 | 9.5 | 7.5 | 1 | 8 | 0.875 | 5.75 | 5.75 | 5 | 1.5 | 3.6 | 2.12 | 2.12 | 3.57 | 3.5 | 4 | - | 1.62 | 3.63 | 241 | 190.5 | 25.4 | 8 | 22.225 | 145 | 145 | 127 | 38.1 | 91.44 | 53.848 | 53.848 | 90.7 | 88.9 | 54 | - | 41 | 92.2
ASME 16.5 | 900 | 4 | 11.5 | 9.25 | 1.25 | 8 | 1.125 | 6.75 | 6.75 | 6.25 | 1.75 | 4.6 | 2.75 | 2.75 | 4.57 | 4.5 | 4.5 | - | 1.88 | 4.63 | 292 | 235 | 31.75 | 8 | 28.575 | 170 | 170 | 158.75 | 44.45 | 116.84 | 69.85 | 69.85 | 116.1 | 114.3 | 70 | - | 48 | 117.6
ASME 16.5 | 900 | 5 | 13.75 | 11 | 1.375 | 8 | 1.25 | 7.5 | 7.5 | 7.5 | 2 | 5.69 | 3.12 | 3.12 | 5.66 | 5.56 | 5 | - | 2.12 | 5.69 | 349 | 279.4 | 34.925 | 8 | 31.75 | 190 | 190 | 190.5 | 50.8 | 144.526 | 79.248 | 79.248 | 143.8 | 141.2 | 79 | - | 54 | 144.5
ASME 16.5 | 900 | 6 | 15 | 12.5 | 1.25 | 12 | 1.125 | 7.5 | 7.75 | 9.25 | 2.19 | 6.75 | 3.38 | 3.38 | 6.72 | 6.63 | 5.5 | - | 2.25 | 6.75 | 381 | 317.5 | 31.75 | 12 | 28.575 | 190 | 195 | 234.95 | 55.626 | 171.45 | 85.852 | 85.852 | 170.7 | 168.4 | 86 | - | 57 | 171.4
ASME 16.5 | 900 | 8 | 18.5 | 15.5 | 1.5 | 12 | 1.375 | 8.75 | 8.75 | 11.75 | 2.5 | 8.75 | 4.5 | 4 | 8.72 | 8.63 | 6.38 | - | 2.5 | 8.75 | 470 | 393.7 | 38.1 | 12 | 34.925 | 220 | 220 | 298.45 | 63.5 | 222.25 | 114.3 | 114.3 | 221.5 | 219.2 | 102 | - | 64 | 222.2
ASME 16.5 | 900 | 10 | 21.5 | 18.5 | 1.5 | 16 | 1.375 | 9.25 | 9.25 | 14.5 | 2.75 | 10.92 | 5 | 4.25 | 10.88 | 10.75 | 7.25 | - | 2.81 | 10.88 | 546 | 469.9 | 38.1 | 16 | 34.925 | 235 | 235 | 368.3 | 69.85 | 277.368 | 127 | 127 | 276.4 | 273 | 108 | - | 71 | 276.4
ASME 16.5 | 900 | 12 | 24 | 21 | 1.5 | 20 | 1.375 | 10 | 10 | 16.5 | 3.12 | 12.92 | 5.62 | 4.62 | 12.88 | 12.75 | 7.88 | - | 3 | 12.94 | 610 | 533.4 | 38.1 | 20 | 34.925 | 255 | 255 | 419.1 | 79.248 | 328.168 | 142.748 | 142.748 | 327.2 | 323.8 | 117 | - | 76 | 328.7
ASME 16.5 | 900 | 14 | 25.25 | 22 | 1.625 | 20 | 1.5 | 10.75 | 11 | 17.75 | 3.38 | 14.18 | 6.12 | 5.12 | 14.14 | 14 | 8.38 | - | 3.25 | 14.19 | 641 | 558.8 | 41.275 | 20 | 38.1 | 275 | 280 | 450.85 | 85.852 | 360.172 | 155.448 | 155.448 | 359.2 | 355.6 | 130 | - | 83 | 360.4
ASME 16.5 | 900 | 16 | 27.75 | 24.25 | 1.75 | 20 | 1.625 | 11.25 | 11.5 | 20 | 3.5 | 16.19 | 6.5 | 5.25 | 16.16 | 16 | 8.5 | - | 3.38 | 16.19 | 705 | 616 | 44.45 | 20 | 41.275 | 285 | 290 | 508 | 88.9 | 411.226 | 165.1 | 165.1 | 410.5 | 406.4 | 133 | - | 86 | 411.2
ASME 16.5 | 900 | 18 | 31 | 27 | 2 | 20 | 1.875 | 12.75 | 13.25 | 22.25 | 4 | 18.2 | 7.5 | 6 | 18.18 | 18 | 9 | - | 3.5 | 18.19 | 787 | 685.8 | 50.8 | 20 | 47.625 | 325 | 335 | 565.15 | 101.6 | 462.28 | 190.5 | 190.5 | 461.8 | 457.2 | 152 | - | 89 | 462
ASME 16.5 | 900 | 20 | 33.75 | 29.5 | 2.125 | 20 | 2 | 13.75 | 14.25 | 24.5 | 4.25 | 20.25 | 8.25 | 6.25 | 20.2 | 20 | 9.75 | - | 3.62 | 20.19 | 857 | 749.3 | 53.975 | 20 | 50.8 | 350 | 360 | 622.3 | 107.95 | 514.35 | 209.55 | 209.55 | 513.1 | 508 | 159 | - | 92 | 512.8
ASME 16.5 | 900 | 24 | 41 | 35.5 | 2.625 | 20 | 2.5 | 17.25 | 18 | 29.5 | 5.5 | 24.25 | 10.5 | 8 | 24.25 | 24 | 11.5 | - | 4 | 24.19 | 1041 | 901.7 | 66.675 | 20 | 63.5 | 440 | 455 | 749.3 | 139.7 | 615.95 | 266.7 | 266.7 | 616 | 609.6 | 203 | - | 102 | 614.4
ASME 16.5 | 1500 | 0.5 | 4.75 | 3.25 | 0.875 | 4 | 0.75 | 4.25 | 4 | 1.5 | 0.88 | 0.9 | 1.25 | 1.25 | 0.88 | 0.84 | 2.28 | 0.38 | 0.88 | 0.93 | 121 | 82.6 | 22.225 | 4 | 19.05 | 110 | 100 | 38.1 | 22.352 | 22.86 | 31.75 | 31.75 | 22.4 | 21.3 | 32 | 10 | 22 | 23.6
ASME 16.5 | 1500 | 0.75 | 5.12 | 3.5 | 0.875 | 4 | 0.75 | 4.5 | 4.25 | 1.75 | 1 | 1.11 | 1.38 | 1.38 | 1.09 | 1.05 | 2.75 | 0.44 | 1 | 1.14 | 130 | 88.9 | 22.225 | 4 | 19.05 | 115 | 110 | 44.45 | 25.4 | 28.194 | 35.052 | 35.052 | 27.7 | 26.7 | 35 | 11 | 25 | 29
ASME 16.5 | 1500 | 1 | 5.88 | 4 | 1 | 4 | 0.875 | 5 | 4.75 | 2.06 | 1.12 | 1.38 | 1.62 | 1.62 | 1.36 | 1.32 | 2.88 | 0.5 | 1.12 | 1.41 | 149 | 101.6 | 25.4 | 4 | 22.225 | 125 | 120 | 52.324 | 28.448 | 35.052 | 41.148 | 41.148 | 34.5 | 33.5 | 41 | 13 | 28 | 35.8
ASME 16.5 | 1500 | 1.25 | 6.25 | 4.38 | 1 | 4 | 0.875 | 5 | 4.75 | 2.5 | 1.12 | 1.72 | 1.62 | 1.62 | 1.7 | 1.66 | 2.88 | 0.56 | 1.19 | 1.75 | 159 | 111.1 | 25.4 | 4 | 22.225 | 125 | 120 | 63.5 | 28.448 | 43.688 | 41.148 | 41.148 | 43.2 | 42.2 | 41 | 14 | 30 | 44.4
ASME 16.5 | 1500 | 1.5 | 7 | 4.88 | 1.125 | 4 | 1 | 5.5 | 5.25 | 2.75 | 1.25 | 1.97 | 1.75 | 1.75 | 1.95 | 1.9 | 3.25 | 0.62 | 1.25 | 1.99 | 178 | 124 | 28.575 | 4 | 25.4 | 140 | 135 | 69.85 | 31.75 | 50.038 | 44.45 | 44.45 | 49.5 | 48.3 | 44 | 16 | 32 | 50.5
ASME 16.5 | 1500 | 2 | 8.5 | 6.5 | 1 | 8 | 0.875 | 5.75 | 5.5 | 4.12 | 1.5 | 2.46 | 2.25 | 2.25 | 2.44 | 2.38 | 4 | 0.69 | 1.5 | 2.5 | 216 | 165.1 | 25.4 | 8 | 22.225 | 145 | 140 | 104.648 | 38.1 | 62.484 | 57.15 | 57.15 | 62 | 60.5 | 57 | 18 | 38 | 63.5
ASME 16.5 | 1500 | 2.5 | 9.62 | 7.5 | 1.125 | 8 | 1 | 6.25 | 6 | 4.88 | 1.62 | 2.97 | 2.5 | 2.5 | 2.94 | 2.88 | 4.12 | 0.75 | 1.88 | 3 | 244 | 190.5 | 28.575 | 8 | 25.4 | 160 | 150 | 123.952 | 41.148 | 75.438 | 63.5 | 63.5 | 74.7 | 73.2 | 64 | 19 | 48 | 76.2
ASME 16.5 | 1500 | 3 | 10.5 | 8 | 1.125 | 8 | 1.125 | 7 | 6.75 | 5.25 | 1.88 | 3.6 | 2.88 | … | … | 3.5 | 4.62 | … | … | … | 267 | 203.2 | 28.575 | 8 | 28.575 | 180 | 170 | 133.35 | 47.752 | 91.44 | 73.152 | 73.152 | … | 88.9 | … | … | … | …
ASME 16.5 | 1500 | 4 | 12.25 | 9.5 | 1.375 | 8 | 1.25 | 7.75 | 7.5 | 6.38 | 2.12 | 4.6 | 3.56 | … | … | 4.5 | 4.88 | … | … | … | 311 | 241.3 | 34.925 | 8 | 31.75 | 195 | 190 | 162.052 | 53.848 | 116.84 | 90.424 | 90.424 | … | 114.3 | … | … | … | …
ASME 16.5 | 1500 | 5 | 14.75 | 11.5 | 1.625 | 8 | 1.5 | 9.75 | 9.5 | 7.75 | 2.88 | 5.69 | 4.12 | … | … | 5.56 | 6.12 | … | … | … | 375 | 292.1 | 41.275 | 8 | 38.1 | 250 | 240 | 196.85 | 73.152 | 144.526 | 104.648 | 104.648 | … | 141.2 | … | … | … | …
ASME 16.5 | 1500 | 6 | 15.5 | 12.5 | 1.5 | 12 | 1.375 | 10.25 | 10 | 9 | 3.25 | 6.75 | 4.69 | … | … | 6.63 | 6.75 | … | … | … | 394 | 317.5 | 38.1 | 12 | 34.925 | 260 | 255 | 228.6 | 82.55 | 171.45 | 119.126 | 119.126 | … | 168.4 | … | … | … | …
ASME 16.5 | 1500 | 8 | 19 | 15.5 | 1.75 | 12 | 1.625 | 11.5 | 11.25 | 11.5 | 3.62 | 8.75 | 5.62 | … | … | 8.63 | 8.38 | … | … | … | 483 | 393.7 | 44.45 | 12 | 41.275 | 290 | 285 | 292.1 | 91.948 | 222.25 | 142.748 | 142.748 | … | 219.2 | … | … | … | …
ASME 16.5 | 1500 | 10 | 23 | 19 | 2 | 12 | 1.875 | 13.25 | 13 | 14.5 | 4.25 | 10.92 | 7 | … | … | 10.75 | 10 | … | … | … | 584 | 482.6 | 50.8 | 12 | 47.625 | 335 | 330 | 368.3 | 107.95 | 277.368 | 177.8 | 177.8 | … | 273 | … | … | … | …
ASME 16.5 | 1500 | 12 | 26.5 | 22.5 | 2.125 | 16 | 2 | 14.75 | 14.5 | 17.75 | 4.88 | 12.92 | 8.62 | … | … | 12.75 | 11.12 | … | … | … | 673 | 571.5 | 53.975 | 16 | 50.8 | 375 | 370 | 450.85 | 123.952 | 328.168 | 218.948 | 218.948 | … | 323.8 | … | … | … | …
ASME 16.5 | 1500 | 14 | 29.5 | 25 | 2.375 | 16 | 2.25 | 16 | 15.75 | 19.5 | 5.25 | 14.18 | 9.5 | … | … | 14 | 11.75 | … | … | … | 749 | 635 | 60.325 | 16 | 57.15 | 405 | 400 | 495.3 | 133.35 | 360.172 | 241.3 | 241.3 | … | 355.6 | … | … | … | …
ASME 16.5 | 1500 | 16 | 32.5 | 27.75 | 2.625 | 16 | 2.5 | 17.5 | 17.25 | 21.75 | 5.75 | 16.19 | 10.25 | … | … | 16 | 12.25 | … | … | … | 826 | 704.8 | 66.675 | 16 | 63.5 | 445 | 440 | 552.45 | 146.05 | 411.226 | 260.35 | 260.35 | … | 406.4 | … | … | … | …
ASME 16.5 | 1500 | 18 | 36 | 30.5 | 2.875 | 16 | 2.75 | 19.5 | 19.25 | 23.5 | 6.38 | 18.2 | 10.88 | … | … | 18 | 12.88 | … | … | … | 914 | 774.7 | 73.025 | 16 | 69.85 | 495 | 490 | 596.9 | 162.052 | 462.28 | 276.352 | 276.352 | … | 457.2 | … | … | … | …
ASME 16.5 | 1500 | 20 | 38.75 | 32.75 | 3.125 | 16 | 3 | 21.25 | 21 | 25.25 | 7 | 20.25 | 11.5 | … | … | 20 | 14 | … | … | … | 984 | 831.8 | 79.375 | 16 | 76.2 | 540 | 535 | 641.35 | 177.8 | 514.35 | 292.1 | 292.1 | … | 508 | … | … | … | …
ASME 16.5 | 1500 | 24 | 46 | 39 | 3.625 | 16 | 3 | 24.25 | 24 | 30 | 8 | 24.25 | 13 | … | … | 24 | 16 | … | … | … | 1168 | 990.6 | 92.075 | 16 | 76.2 | 615 | 610 | 762 | 203.2 | 615.95 | 330.2 | 330.2 | … | 609.6 | … | … | … | …
ASME 16.5 | 2500 | 0.5 | 5.25 | 3.5 | 0.875 | 4 | 0.75 | 4.75 | 4.5 | 1.69 | 1.19 | 0.9 | 1.56 | 1.56 | - | 0.84 | 2.88 | - | 1.12 | 0.93 | 133 | 88.9 | 22.225 | 4 | 19.05 | 120 | 115 | 42.926 | 30.226 | 22.86 | 39.624 | 39.624 | - | 21.3 | 40 | - | 28 | 23.6
ASME 16.5 | 2500 | 0.75 | 5.5 | 3.75 | 0.875 | 4 | 0.75 | 5 | 4.75 | 2 | 1.25 | 1.11 | 1.69 | 1.69 | - | 1.05 | 3.12 | - | 1.25 | 1.14 | 140 | 95.2 | 22.225 | 4 | 19.05 | 125 | 120 | 50.8 | 31.75 | 28.194 | 42.926 | 42.926 | - | 26.7 | 43 | - | 32 | 29
ASME 16.5 | 2500 | 1 | 6.25 | 4.25 | 1 | 4 | 0.875 | 5.5 | 5.25 | 2.25 | 1.38 | 1.38 | 1.88 | 1.88 | - | 1.32 | 3.5 | - | 1.38 | 1.41 | 159 | 108 | 25.4 | 4 | 22.225 | 140 | 135 | 57.15 | 35.052 | 35.052 | 47.752 | 47.752 | - | 33.5 | 52 | - | 35 | 35.8
ASME 16.5 | 2500 | 1.25 | 7.25 | 5.12 | 1.125 | 4 | 1 | 6 | 5.75 | 2.88 | 1.5 | 1.72 | 2.06 | 2.06 | - | 1.66 | 3.75 | - | 1.5 | 1.75 | 184 | 130 | 28.575 | 4 | 25.4 | 150 | 145 | 73.152 | 38.1 | 43.688 | 52.324 | 52.324 | - | 42.2 | 60 | - | 38 | 44.4
ASME 16.5 | 2500 | 1.5 | 8 | 5.75 | 1.25 | 4 | 1.125 | 6.75 | 6.5 | 3.12 | 1.75 | 1.97 | 2.38 | 2.38 | - | 1.9 | 4.38 | - | 1.75 | 1.99 | 203 | 146 | 31.75 | 4 | 28.575 | 170 | 165 | 79.248 | 44.45 | 50.038 | 60.452 | 60.452 | - | 48.3 | 70 | - | 44 | 50.5
ASME 16.5 | 2500 | 2 | 9.25 | 6.75 | 1.125 | 8 | 1 | 7 | 6.75 | 3.75 | 2 | 2.46 | 2.75 | 2.75 | - | 2.38 | 5 | - | 2 | 2.5 | 235 | 171.4 | 28.575 | 8 | 25.4 | 180 | 170 | 95.25 | 50.8 | 62.484 | 69.85 | 69.85 | - | 60.5 | 79 | - | 51 | 63.5
ASME 16.5 | 2500 | 2.5 | 10.5 | 7.75 | 1.25 | 8 | 1.125 | 7.75 | 7.5 | 4.5 | 2.25 | 2.97 | 3.12 | 3.12 | - | 2.88 | 5.62 | - | 2.25 | 3 | 267 | 196.8 | 31.75 | 8 | 28.575 | 195 | 190 | 114.3 | 57.15 | 75.438 | 79.248 | 79.248 | - | 73.2 | … | - | 57 | 76.2
ASME 16.5 | 2500 | 3 | 12 | 9 | 1.375 | 8 | 1.25 | 8.75 | 8.5 | 5.25 | 2.62 | 3.6 | 3.62 | … | - | 3.5 | 6.62 | - | … | … | 305 | 228.6 | 34.925 | 8 | 31.75 | 220 | 215 | 133.35 | 66.548 | 91.44 | 91.948 | 91.948 | - | 88.9 | … | - | … | …
ASME 16.5 | 2500 | 4 | 14 | 10.75 | 1.625 | 8 | 1.5 | 10 | 9.75 | 6.5 | 3 | 4.6 | 4.25 | … | - | 4.5 | 7.5 | - | … | … | 356 | 273 | 41.275 | 8 | 38.1 | 255 | 250 | 165.1 | 76.2 | 116.84 | 107.95 | 107.95 | - | 114.3 | … | - | … | …
ASME 16.5 | 2500 | 5 | 16.5 | 12.75 | 1.875 | 8 | 1.75 | 11.75 | 11.5 | 8 | 3.62 | 5.69 | 5.12 | … | - | 5.56 | 9 | - | … | … | 419 | 323.8 | 47.625 | 8 | 44.45 | 300 | 290 | 203.2 | 91.948 | 144.526 | 130.048 | 130.048 | - | 141.2 | … | - | … | …
ASME 16.5 | 2500 | 6 | 19 | 14.5 | 2.125 | 8 | 2 | 13.5 | 13.25 | 9.25 | 4.25 | 6.75 | 6 | … | - | 6.63 | 10.75 | - | … | … | 483 | 368.3 | 53.975 | 8 | 50.8 | 345 | 335 | 234.95 | 107.95 | 171.45 | 152.4 | 152.4 | - | 168.4 | … | - | … | …
ASME 16.5 | 2500 | 8 | 21.75 | 17.25 | 2.125 | 12 | 2 | 15 | 14.75 | 12 | 5 | 8.75 | 7 | … | - | 8.63 | 12.5 | - | … | … | 552 | 438.2 | 53.975 | 12 | 50.8 | 380 | 375 | 304.8 | 127 | 222.25 | 177.8 | 177.8 | - | 219.2 | … | - | … | …
ASME 16.5 | 2500 | 10 | 26.5 | 21.25 | 2.625 | 12 | 2.5 | 19.25 | 19 | 14.75 | 6.5 | 10.92 | 9 | … | - | 10.75 | 16.5 | - | … | … | 673 | 539.8 | 66.675 | 12 | 63.5 | 490 | 485 | 374.65 | 165.1 | 277.368 | 228.6 | 228.6 | - | 273 | … | - | … | …
ASME 16.5 | 2500 | 12 | 30 | 24.38 | 2.875 | 12 | 2.75 | 21.25 | 21 | 17.38 | 7.25 | 12.92 | 10 | … | - | 12.75 | 18.25 | - | … | … | 762 | 619.3 | 73.025 | 12 | 69.85 | 540 | 535 | 441.452 | 184.15 | 328.168 | 254 | 254 | - | 323.8 | … | - | … | …
…
…
…
…
…
…
…
…
…
…
…
23.6
29
35.8
44.4
50.5
63.5
76.2
…
…
…
…
…
…
…

## 16.47 Series A 150 - 300
Dimensions: Steel Pipe Flanges per ASME B16.47 Series A Class 150 - 300
|  |  |  | US & Metric Units Separated by yellow column | [8 empty] | US Units, inches | Metric Units, milimeters
Note: Refer to ANSI/ASME B16.47 for notes, pressures, and minimum design requirements.
Note: Any column with "-" is relateto a note in the reference standard or may not be covered in the standard.
Note: Data columns from the reference standard may have been omitted
Note: US units are inches, Metric Units are milimeters
Note: Studs are measured parallel to the axis (L) from the first to the thread without the chamfers (points).
Note: Hex bolts are measured from under the head to the top of the bolt
ASME | Flange Class | Nominal Pipe Size (NPS) | Outside Diameter Flange (O) | Min Thickness Flange (T) | Length Through Hub (Y) | Diameter of Hub (X) | Hub Diameter Top (A) | Raised Face Diameter (R) | Drilling-Daimeter Bolt Circle | Drilling- # Bolt Holes | Drilling- Diameter Bolt Hole | Diameter of Bolt | Length of Bolts- Stud Bolt Raised Face (.06 in) | Outside Diameter Flange (O) | Min Thickness Flange- WNF | Length Through Hub (Y) | Diameter of Hub (X) | Hub Diameter Top (A) | Raised Face Diameter (R) | Drilling-Daimeter Bolt Circle | Drilling- # Bolt Holes | Drilling- Diameter Bolt Hole | Diameter of Bolt | Length of Bolts- Stud Bolt Raised Face (1.6 mm)
16.47 Series A | 300 | 26 | 38.25 | 3.07 | 7.19 | 28.38 | 26 | 29.5 | 34.5 | 28 | 1.75 | 1.625 | 10.5 | 972 | 78 | 183 | 721 | 660.4 | 749 | 876.3 | 28 | 44.45 | 41.275 | 270
16.47 Series A | 300 | 28 | 40.75 | 3.32 | 7.69 | 30.5 | 28 | 31.5 | 37 | 28 | 1.75 | 1.625 | 11 | 1035 | 84.3 | 195 | 775 | 711.2 | 800 | 939.8 | 28 | 44.45 | 41.275 | 280
16.47 Series A | 300 | 30 | 43 | 3.57 | 8.19 | 32.56 | 30 | 33.75 | 39.25 | 28 | 1.875 | 1.75 | 11.75 | 1092 | 90.7 | 208 | 827 | 762 | 857 | 997 | 28 | 47.625 | 44.45 | 300
16.47 Series A | 300 | 32 | 45.25 | 3.82 | 8.69 | 34.69 | 32 | 36 | 41.5 | 28 | 2 | 1.875 | 12.75 | 1149 | 97 | 221 | 881 | 812.8 | 914 | 1054.1 | 28 | 50.8 | 47.625 | 320
16.47 Series A | 300 | 34 | 47.5 | 3.94 | 9.07 | 36.88 | 34 | 38 | 43.5 | 28 | 2 | 1.875 | 13 | 1206 | 100.1 | 230 | 937 | 863.6 | 965 | 1104.9 | 28 | 50.8 | 47.625 | 330
16.47 Series A | 300 | 36 | 50 | 4.07 | 9.44 | 39 | 36 | 40.25 | 46 | 32 | 2.125 | 2 | 13.5 | 1270 | 103.4 | 240 | 991 | 914.4 | 1022 | 1168.4 | 32 | 53.975 | 50.8 | 340
16.47 Series A | 300 | 38 | 46 | 4.19 | 7.06 | 39.12 | 38 | 40.5 | 43 | 32 | 1.625 | 1.5 | 12.5 | 1168 | 106.4 | 179 | 994 | 965.2 | 1029 | 1092.2 | 32 | 41.275 | 38.1 | 32
16.47 Series A | 300 | 40 | 48.75 | 4.44 | 7.56 | 41.25 | 40 | 42.75 | 45.5 | 32 | 1.75 | 1.625 | 13.25 | 1238 | 112.8 | 192 | 1048 | 1016 | 1086 | 1155.7 | 32 | 44.45 | 41.275 | 340
16.47 Series A | 300 | 42 | 50.75 | 4.63 | 7.82 | 43.25 | 42 | 44.75 | 47.5 | 32 | 1.75 | 1.625 | 13.75 | 1289 | 117.6 | 199 | 1099 | 1066.8 | 1137 | 1206.5 | 32 | 44.45 | 41.275 | 350
16.47 Series A | 300 | 44 | 53.25 | 4.82 | 8.06 | 45.25 | 44 | 47 | 49.75 | 32 | 1.875 | 1.75 | 14.5 | 1353 | 122.4 | 205 | 1149 | 1117.6 | 1194 | 1263.6 | 32 | 47.625 | 44.45 | 365
16.47 Series A | 300 | 46 | 55.75 | 5 | 8.44 | 47.38 | 46 | 49 | 52 | 28 | 2 | 1.875 | 15 | 1416 | 127 | 214 | 1203 | 1168.4 | 1245 | 1320.8 | 28 | 50.8 | 47.625 | 380
16.47 Series A | 300 | 48 | 57.75 | 5.19 | 8.75 | 49.38 | 48 | 51.25 | 54 | 32 | 2 | 1.875 | 15.5 | 1467 | 131.8 | 222 | 1254 | 1219.2 | 1302 | 1371.6 | 32 | 50.8 | 47.625 | 390
16.47 Series A | 300 | 50 | 60.25 | 5.44 | 9.07 | 51.38 | 50 | 53.5 | 56.25 | 32 | 2.125 | 2 | 16 | 1530 | 138.2 | 230 | 1305 | 1270 | 1359 | 1428.8 | 32 | 53.975 | 50.8 | 410
16.47 Series A | 300 | 52 | 62.25 | 5.63 | 9.32 | 53.38 | 52 | 55.5 | 58.25 | 32 | 2.125 | 2 | 16.5 | 1581 | 143 | 237 | 1356 | 1320.8 | 1410 | 1479.6 | 32 | 53.975 | 50.8 | 420
16.47 Series A | 300 | 54 | 65.25 | 5.94 | 9.88 | 55.5 | 54 | 57.75 | 61 | 28 | 2.375 | 2.25 | 17.5 | 1657 | 150.9 | 251 | 1410 | 1371.6 | 1467 | 1549.4 | 28 | 60.325 | 57.15 | 450
16.47 Series A | 300 | 56 | 67.25 | 6 | 10.19 | 57.62 | 56 | 59.75 | 63 | 28 | 2.375 | 2.25 | 17.75 | 1708 | 152.4 | 259 | 1464 | 1422.4 | 1518 | 1600.2 | 28 | 60.325 | 57.15 | 450
16.47 Series A | 300 | 58 | 69.25 | 6.19 | 10.44 | 59.62 | 58 | 62 | 65 | 32 | 2.375 | 2.25 | 18.25 | 1759 | 157.2 | 265 | 1514 | 1473.2 | 1575 | 1651 | 32 | 60.325 | 57.15 | 465
16.47 Series A | 300 | 60 | 71.25 | 6.38 | 10.69 | 61.62 | 60 | 64 | 67 | 32 | 2.375 | 1.25 | 18.75 | 1810 | 160.1 | 272 | 1565 | 1524 | 1626 | 1701.8 | 32 | 60.325 | 31.75 | 475
16.47 Series A | 150 | 26 | 34.25 | 2.63 | 4.69 | 26.62 | 26 | 29.5 | 31.75 | 24 | 1.375 | 1.25 | 8.75 | 870 | 66.8 | 119 | 676 | 660.4 | 749 | 806.4 | 24 | 34.925 | 31.75 | 225
16.47 Series A | 150 | 28 | 36.5 | 2.75 | 4.88 | 28.62 | 28 | 31.5 | 34 | 28 | 1.375 | 1.25 | 9 | 927 | 69.8 | 124 | 727 | 711.2 | 800 | 863.6 | 28 | 34.925 | 31.75 | 230
16.47 Series A | 150 | 30 | 38.75 | 2.88 | 5.32 | 30.75 | 30 | 33.75 | 36 | 28 | 1.375 | 1.25 | 9.25 | 984 | 73.2 | 135 | 781 | 762 | 857 | 914.4 | 28 | 34.925 | 31.75 | 235
16.47 Series A | 150 | 32 | 41.75 | 3.13 | 5.63 | 32.75 | 32 | 36 | 38.5 | 28 | 1.625 | 1.5 | 10.5 | 1060 | 79.5 | 143 | 832 | 812.8 | 914 | 977.9 | 28 | 41.275 | 38.1 | 265
16.47 Series A | 150 | 34 | 43.75 | 3.19 | 5.82 | 34.75 | 34 | 38 | 40.5 | 32 | 1.625 | 1.5 | 10.5 | 1111 | 81 | 148 | 883 | 863.6 | 965 | 1028.7 | 32 | 41.275 | 38.1 | 270
16.47 Series A | 150 | 36 | 46 | 3.5 | 6.13 | 36.75 | 36 | 40.25 | 42.75 | 32 | 1.625 | 1.5 | 11.25 | 1168 | 88.9 | 156 | 933 | 914.4 | 1022 | 1085.8 | 32 | 41.275 | 38.1 | 285
16.47 Series A | 150 | 38 | 48.75 | 3.38 | 6.13 | 39 | 38 | 42.25 | 45.25 | 32 | 1.625 | 1.5 | 11 | 1238 | 85.9 | 156 | 991 | 965.2 | 1073 | 1149.4 | 32 | 41.275 | 38.1 | 280
16.47 Series A | 150 | 40 | 50.75 | 3.5 | 6.38 | 41 | 40 | 44.25 | 47.25 | 36 | 1.625 | 1.5 | 11.25 | 1289 | 88.9 | 162 | 1041 | 1016 | 1124 | 1200.2 | 36 | 41.275 | 38.1 | 285
16.47 Series A | 150 | 42 | 53 | 3.75 | 6.69 | 43 | 42 | 47 | 49.5 | 36 | 1.625 | 1.5 | 11.75 | 1346 | 95.2 | 170 | 1092 | 1066.8 | 1194 | 1257.3 | 36 | 41.275 | 38.1 | 300
16.47 Series A | 150 | 44 | 55.25 | 3.94 | 6.94 | 45 | 44 | 49 | 51.75 | 40 | 1.625 | 1.5 | 12 | 1403 | 100.1 | 176 | 1143 | 1117.6 | 1245 | 1314.4 | 40 | 41.275 | 38.1 | 305
16.47 Series A | 150 | 46 | 57.25 | 4 | 7.25 | 47.12 | 46 | 51 | 53.75 | 40 | 1.625 | 1.5 | 12.25 | 1454 | 101.6 | 184 | 1197 | 1168.4 | 1295 | 1365.2 | 40 | 41.275 | 38.1 | 310
16.47 Series A | 150 | 48 | 59.5 | 4.19 | 7.5 | 49.12 | 48 | 52.5 | 56 | 44 | 1.625 | 1.5 | 12.5 | 1511 | 106.4 | 191 | 1248 | 1219.2 | 1359 | 1422.4 | 44 | 41.275 | 38.1 | 320
16.47 Series A | 150 | 50 | 67.75 | 4.32 | 7.94 | 51.25 | 50 | 55.5 | 58.25 | 44 | 1.875 | 1.75 | 13.5 | 1568 | 109.7 | 202 | 1302 | 1270 | 1410 | 1479.6 | 44 | 47.625 | 44.45 | 340
16.47 Series A | 150 | 52 | 64 | 4.5 | 8.19 | 53.25 | 52 | 57.5 | 60.5 | 44 | 1.875 | 1.75 | 13.75 | 1626 | 114.3 | 208 | 1353 | 1320.8 | 1431 | 1536.7 | 44 | 47.625 | 44.45 | 350
16.47 Series A | 150 | 54 | 66.25 | 4.69 | 8.44 | 55.25 | 54 | 59.5 | 62.75 | 44 | 1.875 | 1.75 | 14 | 1683 | 119.1 | 214 | 1403 | 1371.6 | 15111 | 1593.8 | 44 | 47.625 | 44.45 | 360
16.47 Series A | 150 | 56 | 68.75 | 4.82 | 8.94 | 57.38 | 56 | 62 | 65 | 48 | 1.875 | 1.75 | 14.5 | 1746 | 122.4 | 227 | 1457 | 1422.4 | 1575 | 1651 | 48 | 47.625 | 44.45 | 365
16.47 Series A | 150 | 58 | 71 | 5 | 9.19 | 59.38 | 58 | 64 | 67.25 | 48 | 1.875 | 1.75 | 14.75 | 1803 | 127 | 233 | 1508 | 1473.2 | 1626 | 1708.2 | 48 | 47.625 | 44.45 | 380
16.47 Series A | 150 | 60 | 73 | 5.13 | 9.38 | 61.38 | 60 | 66 | 69.25 | 52 | 1.875 | 1.75 | 15 | 1854 | 130.3 | 238 | 1559 | 1524 | 1676 | 1759 | 52 | 47.625 | 44.45 | 380

## 16.47 Series A 400 - 900
[5 empty] | Dimensions: Steel Pipe Flanges per ASME B16.47 Series A Class 400 - 900 | [7 empty] | US Units, Inches | Metric Units, milimeters
US & Metric Units Separated by yellow column
Note: Refer to ANSI/ASME B16.47 for notes, pressures, and minimum design requirements.
Note: Any column with "-" is relateto a note in the reference standard or may not be covered in the standard.
Note: Data columns from the reference standard may have been omitted
Note: US units are inches, Metric Units are milimeters
Note: Studs are measured parallel to the axis (L) from the first to the thread without the chamfers (points).
Note: Hex bolts are measured from under the head to the top of the bolt
ASME | Flange Class | Nominal Pipe Size (NPS) | Outside Diameter Flange (O) | Min Thickness Flange (T) | Length Through Hub (Y) | Diameter of Hub (X) | Hub Diameter Top (A) | Raised Face Diameter (R) | Drilling-Daimeter Bolt Circle | Drilling- # Bolt Holes | Drilling- Diameter Bolt Hole | Diameter of Bolt | Length of Bolts- Stud Bolt Raised Face (.25 in) | Outside Diameter Flange (O) | Min Thickness Flange (T) | Length Through Hub (Y) | Diameter of Hub (X) | Hub Diameter Top (A) | Raised Face Diameter (R) | Drilling-Daimeter Bolt Circle | Drilling- # Bolt Holes | Drilling- Diameter Bolt Hole | Diameter of Bolt | Length of Bolts- Stud Bolt Raised Face (6.44mm)
16.47 Series A | 400 | 26 | 38.25 | 3.5 | 7.62 | 28.62 | 26 | 29.5 | 34.5 | 28 | 1.875 | 1.75 | 12 | 972 | 88.9 | 194 | 727 | 660.4 | 749 | 876.3 | 28 | 47.625 | 44.45 | 310
16.47 Series A | 400 | 28 | 40.75 | 3.75 | 8.12 | 30.81 | 28 | 31.5 | 37 | 28 | 2 | 1.875 | 13 | 1035 | 95.2 | 206 | 783 | 711.2 | 800 | 939.8 | 28 | 50.8 | 47.625 | 330
16.47 Series A | 400 | 30 | 43 | 4 | 8.62 | 32.94 | 30 | 33.75 | 39.25 | 28 | 2.125 | 2 | 13.5 | 1092 | 101.6 | 219 | 837 | 762 | 857 | 997 | 28 | 53.975 | 50.8 | 345
16.47 Series A | 400 | 32 | 45.25 | 4.25 | 9.12 | 35 | 32 | 36 | 41.5 | 28 | 2.125 | 2 | 14 | 1149 | 108 | 232 | 339 | 812.8 | 914 | 1054.1 | 28 | 53.975 | 50.8 | 360
16.47 Series A | 400 | 34 | 47.5 | 4.38 | 9.5 | 37.19 | 34 | 38 | 43.5 | 28 | 2.125 | 2 | 14.5 | 1206 | 111.3 | 241 | 945 | 863.6 | 965 | 1104.9 | 28 | 53.975 | 50.8 | 365
16.47 Series A | 400 | 36 | 50 | 4.5 | 9.88 | 39.38 | 36 | 40.25 | 46 | 32 | 2.125 | 2 | 14.5 | 1270 | 114.3 | 251 | 1000 | 914.4 | 1022 | 1168.4 | 32 | 53.975 | 50.8 | 375
16.47 Series A | 400 | 38 | 47.5 | 4.88 | 8.12 | 39.5 | 38 | 40.75 | 44 | 32 | 1.875 | 1.75 | 15 | 1206 | 124 | 206 | 1003 | 965.2 | 1035 | 1117.6 | 32 | 47.625 | 44.45 | 380
16.47 Series A | 400 | 40 | 50 | 5.12 | 8.5 | 41.5 | 40 | 43 | 46.25 | 32 | 2 | 1.875 | 15.5 | 1270 | 130 | 216 | 1054 | 1016 | 1092 | 1174.8 | 32 | 50.8 | 47.625 | 405
16.47 Series A | 400 | 42 | 52 | 5.25 | 8.81 | 43.62 | 42 | 45 | 48.25 | 32 | 2 | 1.875 | 16 | 1321 | 133.4 | 224 | 1108 | 1066.8 | 1143 | 1225.6 | 32 | 50.8 | 47.625 | 405
16.47 Series A | 400 | 44 | 54.5 | 5.5 | 9.18 | 45.62 | 44 | 47.25 | 50.5 | 32 | 2.125 | 2 | 16.5 | 1384 | 139.7 | 233 | 1159 | 1117.6 | 1200 | 1282.7 | 32 | 53.975 | 50.8 | 425
16.47 Series A | 400 | 46 | 56.75 | 5.75 | 9.62 | 47.75 | 46 | 49.5 | 52.75 | 36 | 2.125 | 2 | 17 | 1441 | 146 | 244 | 1213 | 1168.4 | 1257 | 1339.8 | 36 | 53.975 | 50.8 | 435
16.47 Series A | 400 | 48 | 59.5 | 6 | 10.12 | 49.88 | 48 | 51.5 | 55.25 | 28 | 2.375 | 2.25 | 18 | 1511 | 152.4 | 257 | 1267 | 1219.2 | 1308 | 1403.4 | 28 | 60.325 | 57.15 | 460
16.47 Series A | 400 | 50 | 61.75 | 6.19 | 10.56 | 52 | 50 | 53.62 | 57.5 | 32 | 2.375 | 2.25 | 18.5 | 1568 | 157.2 | 268 | 1321 | 1270 | 1362 | 1460.5 | 32 | 60.325 | 57.15 | 470
16.47 Series A | 400 | 52 | 63.75 | 6.38 | 10.88 | 54 | 52 | 55.62 | 59.5 | 32 | 2.375 | 2.25 | 19 | 1619 | 162.1 | 276 | 1372 | 1320.8 | 1413 | 1511.3 | 32 | 60.325 | 57.15 | 480
16.47 Series A | 400 | 54 | 67 | 6.69 | 11.38 | 56.12 | 54 | 57.88 | 62.25 | 28 | 2.625 | 2.5 | 20 | 1702 | 169.9 | 289 | 1425 | 1371.6 | 1470 | 1581.2 | 28 | 66.675 | 63.5 | 510
16.47 Series A | 400 | 56 | 69 | 6.88 | 11.75 | 58.25 | 56 | 60.12 | 64.25 | 32 | 2.625 | 2.5 | 20.5 | 1753 | 174.8 | 298 | 1480 | 1422.4 | 1527 | 1632 | 32 | 66.675 | 63.5 | 520
16.47 Series A | 400 | 58 | 71 | 7 | 12.06 | 60.25 | 58 | 62.12 | 66.25 | 32 | 2.625 | 2.5 | 20.75 | 1803 | 177.8 | 306 | 1530 | 1473.2 | 1578 | 1682.8 | 32 | 66.675 | 63.5 | 530
16.47 Series A | 400 | 60 | 74.25 | 7.31 | 12.56 | 62.38 | 60 | 64.38 | 69 | 32 | 2.875 | 2.75 | 21.75 | 1886 | 185.7 | 319 | 1584 | 1524 | 1635 | 1752.6 | 32 | 73.025 | 69.85 | 560
16.47 Series A | 600 | 26 | 40 | 4.25 | 8.75 | 29.44 | 26 | 29.5 | 36 | 28 | 2 | 1.875 | 14 | 1016 | 108 | 222 | 748 | 660.4 | 749 | 914.4 | 28 | 50.8 | 47.625 | 355
16.47 Series A | 600 | 28 | 42.25 | 4.38 | 9.25 | 31.62 | 28 | 31.5 | 38 | 28 | 2.125 | 2 | 14.5 | 1073 | 111.3 | 235 | 803 | 711.2 | 800 | 965.2 | 28 | 53.975 | 50.8 | 365
16.47 Series A | 600 | 30 | 44.5 | 4.5 | 9.75 | 33.94 | 30 | 33.75 | 40.25 | 28 | 2.375 | 2 | 14.5 | 1130 | 114.3 | 248 | 862 | 762 | 857 | 1022.4 | 28 | 60.325 | 50.8 | 375
16.47 Series A | 600 | 32 | 47 | 4.62 | 10.25 | 36.12 | 32 | 36 | 42.5 | 28 | 2.375 | 2.25 | 15.25 | 1194 | 117.3 | 260 | 917 | 812.8 | 914 | 1079.5 | 28 | 60.325 | 57.15 | 390
16.47 Series A | 600 | 34 | 49 | 4.75 | 10.62 | 38.31 | 34 | 38 | 44.5 | 28 | 2.625 | 2.25 | 15.5 | 1245 | 120.6 | 270 | 973 | 863.6 | 965 | 1130.3 | 28 | 66.675 | 57.15 | 400
16.47 Series A | 600 | 36 | 51.75 | 4.88 | 11.12 | 40.62 | 36 | 40.25 | 47 | 28 | 2.375 | 2.5 | 16.5 | 1314 | 124 | 282 | 1032 | 914.4 | 1022 | 1193.8 | 28 | 60.325 | 63.5 | 415
16.47 Series A | 600 | 38 | 50 | 6 | 10 | 40.25 | 38 | 41.5 | 45.75 | 28 | 2.375 | 2.25 | 18.25 | 1270 | 152.4 | 254 | 1022 | 965.2 | 1054 | 1162 | 28 | 60.325 | 57.15 | 465
16.47 Series A | 600 | 40 | 52 | 6.25 | 10.38 | 42.25 | 40 | 43.75 | 47.75 | 32 | 2.625 | 2.25 | 18.75 | 1321 | 158.8 | 264 | 1073 | 1016 | 1111 | 1212.8 | 32 | 66.675 | 57.15 | 480
16.47 Series A | 600 | 42 | 55.25 | 6.62 | 11 | 44.38 | 42 | 46 | 50.5 | 28 | 2.625 | 2.5 | 20 | 1403 | 168.1 | 279 | 1127 | 1066.8 | 1168 | 1282.7 | 28 | 66.675 | 63.5 | 510
16.47 Series A | 600 | 44 | 57.25 | 6.81 | 11.38 | 46.5 | 44 | 48.25 | 52.5 | 32 | 2.625 | 2.5 | 20.25 | 1454 | 173 | 289 | 1181 | 1117.6 | 1226 | 1333.5 | 32 | 66.675 | 63.5 | 520
16.47 Series A | 600 | 46 | 59.5 | 7.06 | 11.81 | 48.62 | 46 | 50.25 | 54.75 | 32 | 2.875 | 2.5 | 20.75 | 1511 | 179.3 | 300 | 1235 | 1168.4 | 1276 | 1390.6 | 32 | 73.025 | 63.5 | 530
16.47 Series A | 600 | 48 | 62.75 | 7.44 | 12.44 | 50.75 | 48 | 52.5 | 57.5 | 32 | 3.125 | 2.75 | 22 | 15.94 | 189 | 316 | 1289 | 1219.2 | 1334 | 1460.5 | 32 | 79.375 | 69.85 | 565
16.47 Series A | 600 | 50 | 65.75 | 7.75 | 12.94 | 52.88 | 50 | 54.5 | 60 | 28 | 3.125 | 3 | 23.25 | 1670 | 196.8 | 329 | 1343 | 1270 | 1384 | 1524 | 28 | 79.375 | 76.2 | 595
16.47 Series A | 600 | 52 | 67.75 | 8 | 13.25 | 54.88 | 52 | 56.5 | 62 | 32 | 3.125 | 3 | 23.75 | 1721 | 203.2 | 337 | 1394 | 1320.8 | 1435 | 1574.8 | 32 | 79.375 | 76.2 | 605
16.47 Series A | 600 | 54 | 70 | 8.25 | 13.75 | 57 | 54 | 58.75 | 64.25 | 32 | 3.125 | 3 | 2425 | 1778 | 209.6 | 349 | 1448 | 1371.6 | 1492 | 1632 | 32 | 79.375 | 76.2 | 620
16.47 Series A | 600 | 56 | 73 | 8.56 | 14.25 | 59.12 | 56 | 60.75 | 66.75 | 32 | 3.375 | 3.25 | 25.5 | 1854 | 217.4 | 362 | 1502 | 1422.4 | 1543 | 1695.4 | 32 | 85.725 | 82.55 | 645
16.47 Series A | 600 | 58 | 75 | 8.75 | 14.53 | 61.12 | 58 | 63 | 68.75 | 32 | 3.375 | 3.25 | 25.75 | 1905 | 222.2 | 370 | 1553 | 1473.2 | 1600 | 1746.2 | 32 | 85.725 | 82.55 | 655
16.47 Series A | 600 | 60 | 78.5 | 9.19 | 15.31 | 63.38 | 60 | 65.25 | 71.75 | 28 | 3.625 | 3.5 | 27.25 | 1994 | 233.4 | 389 | 1610 | 1524 | 1657 | 1822.4 | 28 | 92.075 | 88.9 | 690
16.47 Series A | 900 | 26 | 42.75 | 5.5 | 11.25 | 30.5 | 26 | 29.5 | 37.5 | 20 | 2.875 | 2.75 | 18.25 | 1086 | 139.7 | 286 | 775 | 660.4 | 749 | 952.5 | 20 | 73.025 | 69.85 | 465
16.47 Series A | 900 | 28 | 46 | 5.62 | 11.75 | 32.75 | 28 | 31.5 | 40.25 | 20 | 3.125 | 3 | 19 | 1168 | 142.7 | 298 | 832 | 711.2 | 800 | 1022.4 | 20 | 79.375 | 76.2 | 485
16.47 Series A | 900 | 30 | 48.5 | 5.88 | 12.25 | 35 | 30 | 33.75 | 42.75 | 20 | 3.125 | 3 | 19.5 | 1232 | 129.4 | 311 | 889 | 762 | 857 | 1085.8 | 20 | 79.375 | 76.2 | 495
16.47 Series A | 900 | 32 | 51.75 | 6.25 | 13 | 37.25 | 32 | 36 | 45.5 | 20 | 3.375 | 3.25 | 20.75 | 1314 | 158.8 | 330 | 946 | 812.8 | 914 | 1155.7 | 20 | 85.725 | 82.55 | 530
16.47 Series A | 900 | 34 | 55 | 6.5 | 13.75 | 39.62 | 34 | 38 | 48.25 | 20 | 3.625 | 3.5 | 21.75 | 1397 | 165.1 | 349 | 1006 | 863.6 | 965 | 1225.6 | 20 | 92.075 | 88.9 | 555
16.47 Series A | 900 | 36 | 57.5 | 6.75 | 14.25 | 41.88 | 36 | 40.25 | 50.75 | 20 | 3.625 | 3.5 | 22.25 | 1460 | 171.4 | 362 | 1064 | 914.4 | 1022 | 1289 | 20 | 92.075 | 88.9 | 565
16.47 Series A | 900 | 38 | 57.5 | 7.5 | 13.88 | 42.25 | 38 | 43.25 | 50.75 | 20 | 3.625 | 3.5 | 23.75 | 1460 | 190.5 | 353 | 1073 | 965.2 | 1099 | 1289 | 20 | 92.075 | 88.9 | 605
16.47 Series A | 900 | 40 | 59.5 | 7.75 | 14.31 | 44.38 | 40 | 45.75 | 52.75 | 24 | 3.625 | 3.5 | 24.5 | 1511 | 196.8 | 363 | 1127 | 1016 | 1162 | 1339.8 | 24 | 92.075 | 88.9 | 620
16.47 Series A | 900 | 42 | 61.5 | 8.12 | 14.62 | 46.31 | 42 | 47.75 | 54.75 | 24 | 3.625 | 3.5 | 25 | 1562 | 206.2 | 371 | 1176 | 1066.8 | 1213 | 1390.6 | 24 | 92.075 | 88.9 | 635
16.47 Series A | 900 | 44 | 64.88 | 8.44 | 15.38 | 48.62 | 44 | 50 | 57.75 | 24 | 3.875 | 3.75 | 26 | 1648 | 214.4 | 391 | 1235 | 1117.6 | 1270 | 1463.5 | 24 | 98.425 | 95.25 | 665
16.47 Series A | 900 | 46 | 68.25 | 8.88 | 16.18 | 50.88 | 46 | 52.5 | 60.5 | 24 | 4.125 | 4 | 27.5 | 1734 | 225.6 | 411 | 1292 | 1168.4 | 1334 | 1536.7 | 24 | 104.775 | 101.6 | 7000
16.47 Series A | 900 | 48 | 70.25 | 9.19 | 16.5 | 52.88 | 48 | 54.5 | 62.5 | 24 | 4.125 | 4 | 28 | 1784 | 233.4 | 419 | 1343 | 1219.2 | 1384 | 1587.5 | 24 | 104.775 | 101.6 | 715
16.47 Series A | 900 | 50 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series A | 900 | 52 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series A | 900 | 54 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series A | 900 | 56 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series A | 900 | 58 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series A | 900 | 60 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …

## 16.47 Series B 75 - 300
[7 empty] | Dimensions: Steel Pipe Flanges per ASME B16.47 Series B Class 75 - 300 | [5 empty] | (US Unites, Inches) | Metric Units, milimeters)
US & Metric Units Separated by yellow column
Note: Refer to ANSI/ASME B16.47 for notes, pressures, and minimum design requirements.
Note: Any column with "-" is relateto a note in the reference standard or may not be covered in the standard.
Note: Data columns from the reference standard may have been omitted
Note: US units are inches, Metric Units are milimeters
Note: Studs are measured parallel to the axis (L) from the first to the thread without the chamfers (points).
Note: Hex bolts are measured from under the head to the top of the bolt
ASME | Flange Class | Nominal Pipe Size (NPS) | Outside Diameter Flange (O) | Min Thickness Flange (T) | Length Through Hub (Y) | Diameter of Hub (X) | Hub Diameter Top (A or H) | Raised Face Diameter (R) | Drilling-Daimeter Bolt Circle | Drilling- # Bolt Holes | Drilling- Diameter Bolt Hole | Diameter of Bolt | Length of Bolts- Stud Bolt Raised Face (.06 in) | Outside Diameter Flange (O) | Min Thickness Flange (T) | Length Through Hub (Y) | Diameter of Hub (X) | Hub Diameter Top (A) | Raised Face Diameter (R) | Drilling-Daimeter Bolt Circle | Drilling- # Bolt Holes | Drilling- Diameter Bolt Hole | Diameter of Bolt | Length of Bolts- Stud Bolt Raised Face (1.6 mm)
16.47 Series B | 75 | 26 | 30 | 1.25 | 2.25 | 26.62 | 26.06 | 27.75 | 28.5 | 36 | 0.75 | 0.625 | 4.5 | 760 | 31.8 | 57 | 676 | 661.9 | 705 | 723.9 | 36 | 15.875 | 114.3 | 115
16.47 Series B | 75 | 28 | 32 | 1.25 | 2.38 | 28.62 | 28.06 | 29.75 | 30.5 | 40 | 0.75 | 0.625 | 4.5 | 813 | 31.8 | 60 | 727 | 712.7 | 756 | 774.7 | 40 | 15.875 | 114.3 | 115
16.47 Series B | 75 | 30 | 34 | 1.25 | 2.5 | 30.62 | 30.06 | 31.75 | 32.5 | 44 | 0.75 | 0.625 | 4.75 | 864 | 31.8 | 64 | 778 | 763.5 | 806 | 825.5 | 44 | 15.875 | 120.65 | 115
16.47 Series B | 75 | 32 | 36 | 1.32 | 2.69 | 32.62 | 32.06 | 33.75 | 34.5 | 48 | 0.75 | 0.625 | 4.75 | 914 | 33.5 | 68 | 829 | 814.3 | 857 | 876.3 | 48 | 15.875 | 120.65 | 120
16.47 Series B | 75 | 34 | 38 | 1.32 | 2.82 | 34.62 | 34.06 | 35.75 | 36.5 | 52 | 0.75 | 0.625 | 4.75 | 965 | 33.5 | 72 | 879 | 865.1 | 908 | 927.1 | 52 | 15.875 | 120.65 | 120
16.47 Series B | 75 | 36 | 40.69 | 1.38 | 3.32 | 36.81 | 36.06 | 38 | 39.06 | 40 | 0.875 | 0.75 | 5 | 1034 | 35.1 | 84 | 935 | 915.9 | 965 | 992.1 | 40 | 19.05 | 127 | 130
16.47 Series B | 75 | 38 | 42.69 | 1.44 | 3.44 | 38.81 | 38.06 | 40 | 41.06 | 40 | 0.875 | 0.75 | 5.25 | 1084 | 36.6 | 87 | 986 | 966.7 | 1016 | 1042.9 | 40 | 19.05 | 133.35 | 130
16.47 Series B | 75 | 40 | 44.69 | 1.44 | 3.57 | 40.81 | 40.06 | 42 | 43.06 | 44 | 0.875 | 0.75 | 5.25 | 1135 | 36.6 | 91 | 1037 | 1017.5 | 1067 | 1093.7 | 44 | 19.05 | 133.35 | 130
16.47 Series B | 75 | 42 | 46.69 | 1.5 | 3.69 | 42.81 | 42.06 | 44 | 45.06 | 48 | 0.875 | 0.75 | 5.25 | 1186 | 38.1 | 94 | 1087 | 1068.3 | 1118 | 1144.5 | 48 | 19.05 | 133.35 | 135
16.47 Series B | 75 | 44 | 49.25 | 1.63 | 4.07 | 44.88 | 44.06 | 46.25 | 47.38 | 36 | 1 | 0.875 | 5.75 | 1251 | 41.4 | 103 | 1140 | 1119.1 | 1175 | 1203.5 | 36 | 22.225 | 146.05 | 150
16.47 Series B | 75 | 46 | 51.25 | 1.69 | 4.19 | 46.88 | 46.06 | 48.25 | 49.38 | 40 | 1 | 0.875 | 6 | 1302 | 42.9 | 106 | 1191 | 1169.9 | 1226 | 1254.3 | 40 | 22.225 | 152.4 | 150
16.47 Series B | 75 | 48 | 53.25 | 1.75 | 4.32 | 48.88 | 48.06 | 50.25 | 51.38 | 44 | 1 | 0.875 | 6 | 1353 | 44.6 | 110 | 1242 | 1220.7 | 1276 | 1305.1 | 44 | 22.225 | 152.4 | 160
16.47 Series B | 75 | 50 | 55.25 | 1.82 | 4.5 | 50.94 | 50.06 | 52.25 | 53.38 | 44 | 1 | 0.875 | 6.25 | 1403 | 46.2 | 114 | 1294 | 1271.5 | 1327 | 1355.9 | 44 | 22.225 | 158.75 | 160
16.47 Series B | 75 | 52 | 57.38 | 1.82 | 4.69 | 52.94 | 52.06 | 54.25 | 55.5 | 48 | 1 | 0.875 | 6.25 | 1457 | 46.2 | 119 | 1345 | 1322.3 | 1378 | 1409.7 | 48 | 22.225 | 158.75 | 160
16.47 Series B | 75 | 54 | 59.38 | 1.88 | 4.88 | 55 | 54.06 | 56.25 | 57.5 | 48 | 1 | 0.875 | 6.25 | 1508 | 47.8 | 124 | 1397 | 1373.1 | 1429 | 1460.5 | 48 | 22.225 | 158.75 | 160
16.47 Series B | 75 | 56 | 62 | 1.94 | 5.25 | 57.12 | 56.06 | 58.5 | 59.88 | 40 | 1.125 | 1 | 6.75 | 1575 | 49.3 | 133 | 1451 | 1423.9 | 1486 | 1521 | 40 | 25.4 | 171.45 | 170
16.47 Series B | 75 | 58 | 64 | 2 | 5.38 | 59.12 | 58.06 | 60.5 | 61.88 | 44 | 1.125 | 1 | 7 | 1626 | 50.8 | 137 | 1502 | 1474.7 | 1537 | 1571.8 | 44 | 25.4 | 177.8 | 180
16.47 Series B | 75 | 60 | 66 | 2.13 | 5.63 | 61.12 | 60.06 | 62.5 | 63.88 | 44 | 1.125 | 1 | 7.25 | 1676 | 54.1 | 143 | 1553 | 1525.5 | 1588 | 1622.6 | 44 | 25.4 | 184.15 | 185
16.47 Series B | 150 | 26 | 30.94 | 1.57 | 3.44 | 26.94 | 26.06 | 28 | 29.31 | 36 | 0.875 | 0.75 | 5.5 | 786 | 39.9 | 87 | 683 | 661.9 | 711 | 744.5 | 36 | 19.05 | 139.7 | 140
16.47 Series B | 150 | 28 | 32.94 | 1.69 | 3.69 | 28.94 | 28.06 | 30 | 31.31 | 40 | 0.875 | 0.75 | 5.75 | 837 | 42.9 | 94 | 735 | 712.7 | 762 | 795.3 | 40 | 19.05 | 146.05 | 145
16.47 Series B | 150 | 30 | 34.94 | 1.69 | 3.88 | 31 | 30.06 | 32 | 33.31 | 44 | 0.875 | 0.75 | 5.75 | 887 | 42.9 | 98 | 787 | 763.5 | 813 | 846.1 | 44 | 19.05 | 146.05 | 145
16.47 Series B | 150 | 32 | 37.06 | 1.75 | 4.19 | 33.06 | 32.06 | 34 | 35.44 | 48 | 0.875 | 0.75 | 5.75 | 941 | 44.4 | 106 | 840 | 814.3 | 864 | 900.2 | 48 | 19.05 | 146.05 | 150
16.47 Series B | 150 | 34 | 39.56 | 1.88 | 4.28 | 35.12 | 34.06 | 36.25 | 37.69 | 40 | 1 | 0.875 | 6.25 | 1005 | 47.8 | 109 | 892 | 865.1 | 921 | 957.3 | 40 | 22.225 | 158.75 | 165
16.47 Series B | 150 | 36 | 41.62 | 2 | 4.57 | 37.19 | 36.06 | 38.25 | 39.75 | 44 | 1 | 0.875 | 6.5 | 1057 | 50.8 | 116 | 945 | 915.9 | 972 | 1009.6 | 44 | 22.225 | 165.1 | 165
16.47 Series B | 150 | 38 | 44.25 | 2.07 | 4.82 | 39.25 | 38.12 | 40.25 | 42.12 | 40 | 1.125 | 1 | 7.25 | 1124 | 52.6 | 122 | 997 | 968.2 | 1022 | 1069.8 | 40 | 25.4 | 184.15 | 185
16.47 Series B | 150 | 40 | 46.25 | 2.13 | 5 | 41.31 | 40.12 | 42.5 | 44.12 | 44 | 1.125 | 1 | 7.25 | 1175 | 54.1 | 127 | 1049 | 1019 | 1080 | 1120.6 | 44 | 25.4 | 184.15 | 185
16.47 Series B | 150 | 42 | 48.25 | 2.25 | 5.19 | 43.38 | 42.12 | 44.5 | 46.12 | 48 | 1.125 | 1 | 7.5 | 1226 | 57.2 | 132 | 1102 | 1069.8 | 1130 | 1171.4 | 48 | 25.4 | 190.5 | 190
16.47 Series B | 150 | 44 | 50.25 | 2.32 | 5.32 | 445.38 | 44.12 | 46.5 | 48.12 | 52 | 1.125 | 1 | 7.75 | 1276 | 58.9 | 135 | 1153 | 1120.6 | 1181 | 1222.2 | 52 | 25.4 | 196.85 | 195
16.47 Series B | 150 | 46 | 52.81 | 2.38 | 5.63 | 47.44 | 46.12 | 48.62 | 50.56 | 40 | 1.25 | 1.125 | 8 | 1341 | 60.5 | 143 | 1205 | 1171.4 | 1235 | 1284.2 | 40 | 28.575 | 203.2 | 205
16.47 Series B | 150 | 48 | 54.81 | 2.5 | 5.82 | 49.5 | 48.12 | 50.75 | 52.56 | 44 | 1.25 | 1.125 | 8.25 | 1392 | 63.5 | 148 | 1257 | 1222.2 | 1289 | 1335 | 44 | 28.575 | 209.55 | 210
16.47 Series B | 150 | 50 | 56.81 | 2.63 | 6 | 51.5 | 50.12 | 52.75 | 54.56 | 48 | 1.25 | 1.125 | 8.5 | 1443 | 66.8 | 152 | 1308 | 1273 | 1340 | 1385.8 | 48 | 28.575 | 215.9 | 215
16.47 Series B | 150 | 52 | 58.81 | 2.69 | 6.13 | 53.56 | 52.12 | 54.75 | 56.56 | 52 | 1.25 | 1.125 | 8.75 | 1494 | 68.3 | 156 | 1360 | 1323.8 | 1391 | 1436.6 | 52 | 28.575 | 222.25 | 220
16.47 Series B | 150 | 54 | 61 | 2.75 | 6.32 | 55.62 | 54.12 | 56.75 | 58.75 | 56 | 1.25 | 1.125 | 8.75 | 1549 | 69.8 | 161 | 1413 | 1374.6 | 1441 | 1492.2 | 56 | 28.575 | 222.25 | 225
16.47 Series B | 150 | 56 | 63 | 2.82 | 6.5 | 57.62 | 56.12 | 58.75 | 60.75 | 60 | 1.25 | 1.125 | 9 | 1600 | 71.6 | 165 | 1465 | 1425.4 | 1492 | 1543 | 60 | 28.575 | 228.6 | 225
16.47 Series B | 150 | 58 | 65.94 | 2.88 | 6.82 | 59.69 | 58.12 | 60.75 | 63.44 | 48 | 1.375 | 1.25 | 9.25 | 1675 | 73.2 | 173 | 1516 | 1476.2 | 1543 | 1611.4 | 48 | 31.75 | 234.95 | 235
16.47 Series B | 150 | 60 | 67.94 | 2.94 | 7 | 61.81 | 60.12 | 63 | 65.44 | 52 | 1.375 | 1.25 | 9.5 | 1726 | 74.7 | 178 | 1570 | 1527 | 1600 | 1662.2 | 52 | 31.75 | 241.3 | 240
16.47 Series B | 300 | 26 | 34.12 | 3.44 | 5.63 | 27.62 | 26.19 | 29 | 31.62 | 32 | 1.375 | 1.25 | 10.5 | 867 | 87.4 | 143 | 702 | 665.2 | 737 | 803.1 | 32 | 31.75 | 266.7 | 270
16.47 Series B | 300 | 28 | 36.25 | 3.44 | 5.81 | 29.75 | 28.19 | 31 | 33.75 | 36 | 1.375 | 1.25 | 10.5 | 921 | 87.4 | 148 | 756 | 716 | 787 | 857.2 | 36 | 31.75 | 266.7 | 270
16.47 Series B | 300 | 30 | 39 | 3.63 | 6.16 | 32 | 30.25 | 33.25 | 36.25 | 36 | 1.5 | 1.375 | 11.25 | 991 | 92.2 | 156 | 813 | 768.4 | 845 | 920.8 | 36 | 34.925 | 285.75 | 285
16.47 Series B | 300 | 32 | 41.5 | 4 | 6.56 | 34 | 32.25 | 35.5 | 38.5 | 32 | 1.625 | 1.5 | 12.25 | 1054 | 101.6 | 167 | 864 | 819.2 | 902 | 977.9 | 32 | 38.1 | 311.15 | 310
16.47 Series B | 300 | 34 | 43.62 | 4 | 6.75 | 36.12 | 34.25 | 37.5 | 40.62 | 36 | 1.625 | 1.5 | 12.25 | 1108 | 101.6 | 171 | 917 | 870 | 952 | 1031.7 | 36 | 38.1 | 311.15 | 310
16.47 Series B | 300 | 36 | 46.12 | 4 | 7.06 | 38 | 36.25 | 39.75 | 42.88 | 32 | 1.75 | 1.625 | 12.5 | 1171 | 101.6 | 179 | 965 | 920.8 | 1010 | 1089.2 | 32 | 41.275 | 317.5 | 320
16.47 Series B | 300 | 38 | 48.12 | 4.31 | 7.5 | 40 | 38.25 | 41.75 | 44.88 | 36 | 1.75 | 1.625 | 13 | 1222 | 109.5 | 190 | 1016 | 971.6 | 1060 | 1140 | 36 | 41.275 | 330.2 | 335
16.47 Series B | 300 | 40 | 50.12 | 4.5 | 7.75 | 42 | 40.25 | 43.88 | 46.88 | 40 | 1.75 | 1.625 | 13.5 | 1273 | 114.3 | 197 | 1067 | 1022.4 | 1115 | 1190.8 | 40 | 41.275 | 342.9 | 345
16.47 Series B | 300 | 42 | 52.5 | 4.63 | 8 | 44 | 42.31 | 46 | 49 | 36 | 1.875 | 1.75 | 14 | 1334 | 117.6 | 203 | 1118 | 1074.7 | 1168 | 1244.6 | 36 | 44.45 | 355.6 | 355
16.47 Series B | 300 | 44 | 54.5 | 4.94 | 8.38 | 46.19 | 44.31 | 48 | 51 | 40 | 1.875 | 1.75 | 14.5 | 1384 | 125.5 | 213 | 1173 | 1125.5 | 1219 | 1295.4 | 40 | 44.45 | 368.3 | 370
16.47 Series B | 300 | 46 | 57.5 | 5 | 8.69 | 48.38 | 46.31 | 50 | 53.75 | 36 | 2 | 1.875 | 15 | 1460 | 127 | 221 | 1229 | 1176.3 | 1270 | 1365.2 | 36 | 47.625 | 381 | 380
16.47 Series B | 300 | 48 | 59.5 | 5 | 8.75 | 50.31 | 48.31 | 52.25 | 55.75 | 40 | 2 | 1.875 | 15 | 1511 | 127 | 222 | 1278 | 1227.1 | 1327 | 1416 | 40 | 47.625 | 381 | 380
16.47 Series B | 300 | 50 | 61.5 | 5.38 | 9.19 | 52.38 | 50.31 | 54.25 | 57.75 | 44 | 2 | 1.875 | 15.75 | 1562 | 136.7 | 233 | 1330 | 1277.9 | 1378 | 1466.8 | 44 | 47.625 | 400.05 | 400
16.47 Series B | 300 | 52 | 63.5 | 5.56 | 9.5 | 54.44 | 52.31 | 56.25 | 59.75 | 48 | 2 | 1.875 | 16 | 1613 | 141.2 | 241 | 1383 | 1328.7 | 1429 | 1517.6 | 48 | 47.625 | 406.4 | 410
16.47 Series B | 300 | 54 | 65.88 | 5.32 | 9.38 | 56.5 | 54.31 | 58.25 | 62.12 | 48 | 2 | 1.875 | 15.75 | 1673 | 135.1 | 238 | 1435 | 1379.5 | 1480 | 1577.8 | 48 | 47.625 | 400.05 | 400
16.47 Series B | 300 | 56 | 69.5 | 6 | 10.5 | 58.81 | 56.31 | 60.5 | 65 | 36 | 2.375 | 2.25 | 17.75 | 1765 | 152.4 | 267 | 1494 | 14300.3 | 1537 | 1651 | 36 | 57.15 | 450.85 | 450
16.47 Series B | 300 | 58 | 71.94 | 6 | 10.75 | 60.94 | 58.31 | 62.75 | 67.44 | 40 | 2.375 | 2.25 | 17.75 | 1827 | 152.4 | 273 | 1548 | 1481.1 | 1594 | 1713 | 40 | 57.15 | 450.85 | 450
16.47 Series B | 300 | 60 | 73.94 | 5.88 | 10.63 | 62.94 | 60.31 | 65 | 69.44 | 40 | 2.375 | 2.25 | 17.5 | 1878 | 149.4 | 270 | 1599 | 1531.9 | 1651 | 1763.8 | 40 | 57.15 | 444.5 | 450

## 16.47 Series B 400 - 900
[7 empty] | Dimensions: Steel Pipe Flanges per ASME B16.47 Series B Class 400 - 900 | [5 empty] | (US Unites, Inches) | Metric Units, milimeters)
US & Metric Units Separated by yellow column
Note: Refer to ANSI/ASME B16.47 for notes, pressures, and minimum design requirements.
Note: Any column with "-" is relateto a note in the reference standard or may not be covered in the standard.
Note: Data columns from the reference standard may have been omitted
Note: US units are inches, Metric Units are milimeters
Note: Studs are measured parallel to the axis (L) from the first to the thread without the chamfers (points).
Note: Hex bolts are measured from under the head to the top of the bolt
ASME | Flange Class | Nominal Pipe Size (NPS) | Outside Diameter Flange (O) | Min Thickness Flange (T) | Length Through Hub (Y) | Diameter of Hub (X) | Hub Diameter Top (A or H) | Raised Face Diameter (R) | Drilling-Daimeter Bolt Circle | Drilling- # Bolt Holes | Drilling- Diameter Bolt Hole | Diameter of Bolt | Length of Bolts- Stud Bolt Raised Face (.25 in) | Outside Diameter Flange (O) | Min Thickness Flange (T) | Length Through Hub (Y) | Diameter of Hub (X) | Hub Diameter Top (A) | Raised Face Diameter (R) | Drilling-Daimeter Bolt Circle | Drilling- # Bolt Holes | Drilling- Diameter Bolt Hole | Diameter of Bolt | Length of Bolts- Stud Bolt Raised Face (6.44 mm)
16.47 Series B | 400 | 26 | 33.5 | 3.5 | 5.88 | 27.12 | 26 | 28 | 30.75 | 28 | 1.5 | 1.375 | 14.25 | 851 | 88.9 | 149 | 689 | 660.4 | 711 | 781 | 28 | 38.1 | 34.925 | 290
16.47 Series B | 400 | 28 | 36 | 3.75 | 6.25 | 29.12 | 28 | 30 | 33 | 24 | 1.625 | 1.5 | 14.75 | 914 | 95.2 | 159 | 740 | 711.2 | 762 | 838.2 | 24 | 41.275 | 38.1 | 310
16.47 Series B | 400 | 30 | 38.25 | 4 | 6.69 | 31.25 | 30 | 32.25 | 35.25 | 28 | 1.625 | 1.5 | 15.5 | 972 | 101.6 | 170 | 794 | 768 | 819 | 895.4 | 28 | 41.275 | 38.1 | 320
16.47 Series B | 400 | 32 | 40.75 | 4.25 | 7.06 | 33.25 | 32 | 34.38 | 37.25 | 28 | 1.75 | 1.625 | 16.25 | 1035 | 108 | 179 | 845 | 812.8 | 873 | 952.5 | 28 | 44.45 | 41.275 | 345
16.47 Series B | 400 | 34 | 42.75 | 4.38 | 7.38 | 35.38 | 34 | 36.5 | 39.5 | 32 | 1.75 | 1.625 | 17.25 | 1086 | 111.3 | 187 | 899 | 863.6 | 927 | 1003.3 | 32 | 44.45 | 41.275 | 345
16.47 Series B | 400 | 36 | 45.5 | 4.69 | 7.88 | 37.5 | 36 | 38.62 | 42 | 28 | 1.875 | 1.75 | 18 | 1156 | 119.1 | 200 | 952 | 914.4 | 981 | 1066.8 | 28 | 47.625 | 44.45 | 370
16.47 Series B | 400 | 38 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 400 | 40 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 400 | 42 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 400 | 44 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 400 | 46 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 400 | 48 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 400 | 50 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 400 | 52 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 400 | 54 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 400 | 56 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 400 | 58 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 400 | 60 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 600 | 26 | 35 | 4.38 | 7.12 | 27.5 | 26 | 28.62 | 31.75 | 28 | 1.75 | 1.625 | 14.25 | 889 | 111.3 | 181 | 698 | 660.4 | 727 | 806.4 | 28 | 44.45 | 41.275 | 360
16.47 Series B | 600 | 28 | 37.5 | 4.56 | 7.5 | 29.62 | 28 | 30.88 | 34 | 28 | 1.875 | 1.75 | 14.75 | 952 | 115.8 | 190 | 752 | 711.2 | 784 | 863.6 | 28 | 47.625 | 44.45 | 375
16.47 Series B | 600 | 30 | 40.25 | 4.94 | 8.06 | 31.75 | 30 | 33.12 | 36.5 | 28 | 2 | 1.875 | 15.5 | 1022 | 125.5 | 205 | 806 | 762 | 841 | 927.1 | 28 | 50.8 | 47.625 | 395
16.47 Series B | 600 | 32 | 42.75 | 5.12 | 8.5 | 33.88 | 32 | 35.25 | 38.75 | 28 | 2.125 | 2 | 16.25 | 1086 | 130 | 216 | 861 | 812.8 | 895 | 984.2 | 28 | 53.975 | 50.8 | 415
16.47 Series B | 600 | 34 | 45.75 | 5.56 | 9.19 | 36 | 34 | 37.5 | 41.5 | 24 | 2.375 | 2.25 | 17.25 | 1162 | 141.2 | 233 | 914 | 863.6 | 952 | 1054.1 | 24 | 60.325 | 57.15 | 440
16.47 Series B | 600 | 36 | 47.75 | 5.75 | 9.56 | 38.12 | 36 | 39.75 | 43.5 | 28 | 2.375 | 2.25 | 18 | 1213 | 146 | 243 | 968 | 914.4 | 1010 | 1104.9 | 28 | 60.325 | 57.15 | 460
16.47 Series B | 600 | 38 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 600 | 40 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 600 | 42 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 600 | 44 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 600 | 46 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 600 | 48 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 600 | 50 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 600 | 52 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 600 | 54 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 600 | 56 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 600 | 58 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 600 | 60 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 900 | 26 | 40.25 | 5.31 | 10.19 | 29.25 | 26 | 30 | 35.5 | 20 | 2.625 | 2.5 | 17.75 | 1022 | 134.9 | 259 | 743 | 660.4 | 762 | 901.7 | 20 | 66.675 | 63.5 | 450
16.47 Series B | 900 | 28 | 43.5 | 5.81 | 10.88 | 31.38 | 28 | 32.25 | 38.25 | 20 | 2.875 | 2.75 | 19.25 | 1105 | 147.6 | 276 | 797 | 711.2 | 819 | 971.6 | 20 | 73.025 | 69.85 | 495
16.47 Series B | 900 | 30 | 46.5 | 6.12 | 11.38 | 33.5 | 30 | 34.5 | 40.75 | 20 | 3.125 | 3 | 20 | 1181 | 155.4 | 289 | 851 | 762 | 876 | 1035 | 20 | 79.375 | 76.2 | 510
16.47 Series B | 900 | 32 | 48.75 | 6.31 | 11.94 | 35.75 | 32 | 36.5 | 43 | 20 | 3.125 | 3 | 20.75 | 1238 | 160.3 | 303 | 908 | 812.8 | 927 | 1092.2 | 20 | 79.375 | 76.2 | 530
16.47 Series B | 900 | 34 | 51.75 | 6.75 | 12.56 | 37.88 | 34 | 39 | 45.5 | 20 | 3.375 | 3.25 | 22.25 | 1314 | 171.4 | 319 | 962 | 863.6 | 991 | 1155.7 | 20 | 85.725 | 82.55 | 565
16.47 Series B | 900 | 36 | 53 | 6.81 | 12.81 | 40 | 36 | 40.5 | 47.25 | 24 | 3.125 | 3 | 22.5 | 1346 | 173 | 325 | 1016 | 914.4 | 1029 | 1200.2 | 24 | 79.375 | 76.2 | 570
16.47 Series B | 900 | 38 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 900 | 40 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 900 | 42 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 900 | 44 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 900 | 46 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 900 | 48 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 900 | 50 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 900 | 52 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 900 | 54 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 900 | 56 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 900 | 58 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 900 | 60 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …

## All (hidden)
ASME | Flange Class | Nominal Pipe Size (NPS) | Outside Diameter Flange (O) | Diameter Bolt Circle (W) | Diameter Bolt Holes | # of Bolts | Bolt Diameter | Stud Bolts-Raised Face (0.06 in) | Stud Bolts-Ring Joint | Machine Bolts-Raised Face (0.06in) | Outside Diameter Flange (O) mm | Diameter Bolt Circle (W) mm | Stud Bolts- 1.5 mm Raised Face | Stud Bolts-Ring Joint | Machine Bolts- 1.5mm Raised Face | Min Thickness Flange (in) | Min Thickness Lap Joint (in) | Diameter of Hub (in) | Diameter Beginning Chamfer Welding Neck (in) | Length Through Hub-Threaded slip on socket Welding (in) | Length Through Hub- Lapped (in) | Length Through Hub Bore Welding Neck (in) | Min Thread Length Threaded (in) | Bore- Min Slip On Socket Weld (in) | Bore- Min Lapped (in) | Bore- Weld Neck/Socket Weld (in) | Corner Bore Radius of Lapped Flange and Pipe (in) | Depth of socket (in) | Min Thickness Flange (mm) | Min Thickness Lap Joint (m) | Diameter of Hub (mm) | Diameter Beginning Chamfer Welding Neck (mm) | Length through Hub-Threaded/Slip-on/Socket Weld(mm) | Length Through Hub- Lapped (mm) | Lemgth Through Bore- Welding Neck(mm) | Min Thread Length Threaded(mm) | Bore- Min Slip On Socket Weld (mm) | Bore- Min Lapped (mm) | Bore- Weld Neck/Socket Weld (mm) | Corner Bore Radius of Lapped Flange and Pipe (mm) | Depth of socket (mm) | Min Counterbore Threaded Flange (in) | Min Counterbore Threaded Flange (mm)
16.5 | 150 | 0.5 | 3.5 | 2.38 | 0.625 | 4 | 0.5 | 2.25 | … | 2 | 89 | 60.5 | 55 | … | 50 | 0.38 | 0.44 | 1.19 | 0.84 | 0.56 | 0.62 | 1.81 | 0.62 | 0.88 | 0.9 | 0.62 | 0.12 | 0.38 | 9.7 | 11.2 | 30 | 21.3 | 14 | 16 | 46 | 16 | 22.4 | 22.9 | 1.7 | 3 | 10 | N/A | N/A
16.5 | 150 | 0.75 | 3.88 | 2.75 | 0.625 | 4 | 0.5 | 2.5 | … | 2 | 99 | 69.8 | 65 | … | 50 | 0.44 | 0.5 | 1.5 | 1.05 | 0.56 | 0.62 | 2 | 0.62 | 1.09 | 1.11 | 0.82 | 0.12 | 0.44 | 11.2 | 12.7 | 38 | 26.7 | 14 | 16 | 51 | 16 | 27.7 | 28.2 | 20.8 | 3 | 11 | N/A | N/A
16.5 | 150 | 1 | 4.25 | 3.12 | 0.625 | 4 | 0.5 | 2.5 | 3 | 2.25 | 108 | 79.2 | 65 | 75 | 55 | 0.5 | 0.56 | 1.94 | 1.32 | 0.62 | 0.69 | 2.12 | 0.69 | 1.36 | 1.38 | 1.05 | 0.12 | 0.5 | 12.7 | 14.2 | 49 | 33.5 | 16 | 18 | 54 | 18 | 34.5 | 35.1 | 26.7 | 3 | 13 | N/A | N/A
16.5 | 150 | 1.25 | 4.62 | 3.5 | 0.625 | 4 | 0.5 | 2.75 | 3.25 | 2.25 | 117 | 88.9 | 70 | 85 | 55 | 0.56 | 0.62 | 2.31 | 1.66 | 0.75 | 0.81 | 2.19 | 0.81 | 1.7 | 1.72 | 1.38 | 0.19 | 0.56 | 14.2 | 15.7 | 59 | 42.2 | 19 | 21 | 56 | 21 | 43.2 | 43.7 | 35.1 | 5 | 14 | N/A | N/A
16.5 | 150 | 1.5 | 5 | 3.88 | 0.625 | 4 | 0.5 | 2.75 | 3.25 | 2.5 | 127 | 98.6 | 70 | 85 | 65 | 0.62 | 0.69 | 2.56 | 1.9 | 0.81 | 0.88 | 2.83 | 0.88 | 1.95 | 1.97 | 1.61 | 0.25 | 0.62 | 15.9 | 17.5 | 65 | 48.3 | 21 | 22 | 60 | 22 | 49.5 | 50 | 40.9 | 6 | 16 | N/A | N/A
16.5 | 150 | 2 | 6 | 4.75 | 0.75 | 4 | 0.625 | 3.25 | 3.75 | 2.75 | 152 | 120.6 | 85 | 95 | 70 | 0.69 | 0.75 | 3.06 | 2.38 | 0.94 | 1 | 2.44 | 1 | 2.44 | 2.46 | 2.07 | 0.31 | 0.69 | 17.5 | 19 | 78 | 60.5 | 24 | 25 | 62 | 25 | 61.9 | 62.5 | 52.6 | 8 | 18 | N/A | N/A
16.5 | 150 | 2.5 | 7 | 5.5 | 0.75 | 4 | 0.625 | 3.5 | 4 | 3 | 178 | 139.7 | 90 | 100 | 75 | 0.81 | 0.88 | 3.56 | 2.88 | 1.06 | 1.12 | 2.69 | 1.12 | 2.94 | 2.97 | 2.47 | 0.31 | 0.75 | 20.6 | 22.4 | 90 | 73.2 | 27 | 28 | 68 | 28 | 74.7 | 75.4 | 62.7 | 8 | 19 | N/A | N/A
16.5 | 150 | 3 | 7.5 | 6 | 0.75 | 4 | 0.625 | 3.5 | 4 | 3 | 190 | 152.4 | 90 | 100 | 75 | 0.88 | 0.94 | 4.25 | 3.5 | 1.12 | 1.19 | 2.69 | 1.19 | 3.57 | 3.6 | 3.07 | 0.38 | 0.81 | 22.4 | 23.9 | 108 | 88.9 | 28 | 30 | 68 | 30 | 90.7 | 91.4 | 78 | 10 | 21 | N/A | N/A
16.5 | 150 | 3.5 | 8.5 | 7 | 0.75 | 8 | 0.625 | 3.5 | 4 | 3 | 216 | 177.8 | 90 | 100 | 75 | 0.88 | 0.94 | 4.81 | 4 | 1.19 | 1.25 | 2.75 | 1.25 | 4.07 | 4.1 | 3.55 | 0.38 | … | 22.4 | 23.9 | 122 | 101.6 | 30 | 32 | 70 | 32 | 103.4 | 104.1 | 90.2 | 10 | … | N/A | N/A
16.5 | 150 | 4 | 9 | 7.5 | 0.75 | 8 | 0.625 | 3.5 | 4 | 3 | 229 | 190.5 | 90 | 100 | 75 | 0.88 | 0.94 | 5.31 | 4.5 | 1.25 | 1.31 | 2.94 | 1.31 | 4.57 | 4.6 | 4.03 | 0.44 | … | 22.4 | 23.9 | 135 | 114.3 | 32 | 33 | 75 | 33 | 116.1 | 116.8 | 102.4 | 11 | … | N/A | N/A
16.5 | 150 | 5 | 10 | 8.5 | 0.875 | 8 | 0.75 | 3.75 | 4.25 | 3.25 | 254 | 215.9 | 95 | 110 | 85 | 0.88 | 0.94 | 6.44 | 5.56 | 1.38 | 1.44 | 3.44 | 1.44 | 5.66 | 5.69 | 5.05 | 0.44 | … | 22.4 | 23.9 | 164 | 141.2 | 35 | 37 | 87 | 37 | 143.8 | 144.5 | 128.3 | 11 | … | N/A | N/A
16.5 | 150 | 6 | 11 | 9.5 | 0.875 | 8 | 0.75 | 4 | 4.5 | 3.25 | 279 | 241.3 | 100 | 115 | 85 | 0.94 | 1 | 7.56 | 6.63 | 1.5 | 1.56 | 3.44 | 1.56 | 6.72 | 6.75 | 6.07 | 0.5 | … | 23.9 | 25.4 | 192 | 168.4 | 38 | 40 | 87 | 40 | 170.7 | 171.4 | 154.2 | 13 | … | N/A | N/A
16.5 | 150 | 8 | 13.5 | 11.75 | 0.875 | 8 | 0.75 | 4.25 | 4.75 | 3.5 | 343 | 298.4 | 110 | 120 | 90 | 1.06 | 1.12 | 9.69 | 8.63 | 1.69 | 1.75 | 3.94 | 1.75 | 8.72 | 8.75 | 7.98 | 0.5 | … | 26.9 | 28.4 | 246 | 219.2 | 43 | 44 | 100 | 44 | 221.5 | 222.2 | 202.7 | 13 | … | N/A | N/A
16.5 | 150 | 10 | 16 | 14.25 | 1 | 12 | 0.875 | 4.5 | 5 | 4 | 406 | 362 | 115 | 125 | 100 | 1.12 | 1.19 | 12 | 10.75 | 1.88 | 1.94 | 3.94 | 1.94 | 10.88 | 10.92 | 10.02 | 0.5 | … | 28.4 | 30.2 | 305 | 273 | 48 | 49 | 100 | 49 | 276.4 | 277.4 | 254.5 | 13 | … | N/A | N/A
16.5 | 150 | 12 | 19 | 17 | 1 | 12 | 0.875 | 4.75 | 5.25 | 4 | 483 | 431.8 | 120 | 135 | 100 | 1.19 | 1.25 | 14.38 | 12.75 | 2.12 | 2.19 | 4.44 | 2.19 | 12.88 | 12.92 | 12 | 0.5 | … | 30.2 | 31.8 | 365 | 323.8 | 54 | 56 | 113 | 56 | 327.2 | 328.2 | 304.8 | 13 | … | N/A | N/A
16.5 | 150 | 14 | 21 | 18.75 | 1.125 | 12 | 1 | 5.25 | 5.75 | 4.5 | 533 | 476.2 | 135 | 145 | 115 | 1.31 | 1.38 | 15.75 | 14 | 2.19 | 3.12 | 4.94 | 2.25 | 14.14 | 14.18 | (8) | 0.5 | … | 33.3 | 35.1 | 400 | 355.6 | 56 | 79 | 125 | 57 | 359.2 | 360.2 | (8) | 13 | … | N/A | N/A
16.5 | 150 | 16 | 23.5 | 21.25 | 1.125 | 16 | 1 | 5.25 | 5.75 | 4.5 | 597 | 539.8 | 135 | 145 | 115 | 1.38 | 1.44 | 18 | 16 | 2.44 | 3.44 | 4.94 | 2.5 | 16.16 | 16.19 | (8) | 0.5 | … | 35.1 | 36.6 | 457 | 406.4 | 62 | 87 | 125 | 64 | 410.5 | 411.2 | (8) | 13 | … | N/A | N/A
16.5 | 150 | 18 | 25 | 22.75 | 1.25 | 16 | 1.125 | 5.75 | 6.25 | 5 | 635 | 577.8 | 145 | 160 | 125 | 1.5 | 1.56 | 19.88 | 18 | 2.62 | 3.81 | 5.44 | 2.69 | 18.18 | 18.2 | (8) | 0.5 | … | 38.1 | 39.6 | 505 | 457.2 | 67 | 97 | 138 | 68 | 461.8 | 462.3 | (8) | 13 | … | N/A | N/A
16.5 | 150 | 20 | 27.5 | 25 | 1.25 | 20 | 1.125 | 6.25 | 6.75 | 5.5 | 693 | 635 | 160 | 170 | 140 | 1.62 | 1.69 | 22 | 20 | 2.81 | 4.06 | 5.62 | 2.88 | 20.2 | 20.25 | (8) | 0.5 | … | 41.1 | 42.9 | 559 | 508 | 71 | 103 | 143 | 73 | 513.1 | 514.4 | (8) | 13 | … | N/A | N/A
16.5 | 150 | 22 | 29.5 | 27.25 | 1.375 | 20 | 1.25 | 6.75 | 7.25 | 6 | 749 | 692.2 | 170 | 185 | 150 | 1.75 | 1.81 | 24 | 22 | 3.06 | 4.25 | 5.82 | … | 22.22 | 22.25 | (8) | 0.5 | … | 44.4 | 46 | 610 | 558.8 | 78 | 108 | 148 | … | 564.4 | 565.2 | (8) | 13 | … | N/A | N/A
16.5 | 150 | 24 | 32 | 29.5 | 1.375 | 20 | 1.25 | 6.75 | 7.25 | 6 | 813 | 749.3 | 170 | 185 | 150 | 1.81 | 1.88 | 26.12 | 24 | 3.19 | 4.38 | 5.94 | 3.25 | 24.25 | 24.25 | (8) | 0.5 | … | 46 | 47.8 | 663 | 609.6 | 81 | 111 | 151 | 83 | 616 | 616 | (8) | 13 | … | N/A | N/A
16.5 | 300 | 0.5 | 3.75 | 2.62 | 0.625 | 4 | 0.5 | 2.5 | 3 | 2.25 | 95 | 66.5 | 65 | 75 | 55 | 0.5 | 0.56 | 1.5 | 0.84 | 0.81 | 0.88 | 2 | 0.62 | 0.88 | 0.9 | 0.62 | 0.12 | 0.38 | 12.7 | 14.2 | 38 | 21.3 | 21 | 22 | 51 | 16 | 22.4 | 22.9 | 15.7 | 3 | 10 | 0.93 | 23.6
16.5 | 300 | 0.75 | 4.62 | 3.25 | 0.75 | 4 | 0.625 | 3 | 3.5 | 2.5 | 117 | 82.6 | 75 | 90 | 65 | 0.56 | 0.62 | 1.88 | 1.05 | 0.94 | 1 | 2.19 | 0.62 | 1.09 | 1.11 | 0.82 | 0.12 | 0.44 | 14.2 | 15.7 | 48 | 26.7 | 24 | 25 | 56 | 16 | 27.7 | 28.2 | 20.8 | 3 | 11 | 1.14 | 29
16.5 | 300 | 1 | 4.88 | 3.5 | 0.75 | 4 | 0.625 | 3 | 3.5 | 2.5 | 124 | 88.9 | 75 | 90 | 65 | 0.62 | 0.69 | 2.12 | 1.32 | 1 | 1.06 | 2.38 | 0.69 | 1.36 | 1.38 | 1.05 | 0.12 | 0.5 | 15.7 | 17.5 | 54 | 33.5 | 25 | 27 | 60 | 18 | 34.5 | 35.1 | 26.7 | 3 | 13 | 1.41 | 35.8
16.5 | 300 | 1.25 | 5.25 | 3.88 | 0.75 | 4 | 0.625 | 3.25 | 3.75 | 2.75 | 133 | 98.6 | 85 | 95 | 70 | 0.69 | 0.75 | 2.5 | 1.66 | 1 | 1.06 | 2.5 | 0.81 | 1.7 | 1.72 | 1.38 | 0.19 | 0.56 | 17.5 | 19 | 64 | 42.2 | 25 | 27 | 64 | 21 | 43.2 | 43.7 | 35.1 | 5 | 14 | 1.75 | 44.4
16.5 | 300 | 1.5 | 6.12 | 4.5 | 0.875 | 4 | 0.75 | 3.5 | 4 | 3 | 155 | 114.3 | 90 | 100 | 75 | 0.75 | 0.81 | 2.75 | 1.9 | 1.13 | 1.16 | 2.63 | 0.88 | 1.95 | 1.97 | 1.61 | 0.25 | 0.62 | 19 | 20.6 | 70 | 48.3 | 29 | 30 | 67 | 22 | 49.5 | 50 | 40.9 | 6 | 16 | 1.98 | 50.3
16.5 | 300 | 2 | 6.5 | 5 | 0.75 | 8 | 0.625 | 3.5 | 4 | 3 | 165 | 127 | 90 | 100 | 75 | 0.81 | 0.88 | 3.31 | 2.38 | 1.25 | 1.31 | 2.69 | 1.12 | 2.44 | 2.46 | 2.07 | 0.31 | 0.69 | 20.6 | 22.4 | 84 | 60.5 | 32 | 33 | 68 | 28 | 62 | 62.5 | 52.6 | 8 | 17 | 2.5 | 63.5
16.5 | 300 | 2.5 | 7.5 | 5.88 | 0.875 | 8 | 0.75 | 4 | 4.5 | 3.25 | 190 | 149.4 | 100 | 115 | 85 | 0.94 | 1 | 3.94 | 2.88 | 1.44 | 1.5 | 2.94 | 1.25 | 2.94 | 2.97 | 2.47 | 0.31 | 0.75 | 23.9 | 25.4 | 100 | 73.2 | 37 | 38 | 75 | 32 | 74.7 | 75.4 | 62.7 | 8 | 19 | 3 | 76.2
16.5 | 300 | 3 | 8.25 | 6.62 | 0.875 | 8 | 0.75 | 4.25 | 4.75 | 3.5 | 210 | 168.1 | 110 | 120 | 90 | 1.06 | 1.12 | 4.62 | 3.5 | 1.63 | 1.69 | 3.06 | 1.25 | 3.57 | 3.6 | 3.07 | 0.38 | 0.81 | 26.9 | 28.4 | 117 | 88.9 | 41 | 43 | 78 | 32 | 90.7 | 91.4 | 78 | 10 | 21 | 3.63 | 92.2
16.5 | 300 | 3.5 | 9 | 7.25 | 0.875 | 8 | 0.75 | 4.25 | 5 | 3.75 | 229 | 184.2 | 110 | 125 | 95 | 1.12 | 1.19 | 5.25 | 4 | 1.69 | 1.75 | 3.13 | 1.44 | 4.07 | 4.1 | 3.55 | 0.38 | … | 28.4 | 30.2 | 133 | 101.6 | 43 | 44 | 80 | 37 | 103.4 | 104.1 | 90.2 | 10 | … | 4.13 | 104.9
16.5 | 300 | 4 | 10 | 7.88 | 0.875 | 8 | 0.75 | 4.5 | 5 | 3.75 | 254 | 200.2 | 115 | 125 | 95 | 1.19 | 1.25 | 5.75 | 4.5 | 1.82 | 1.88 | 3.32 | 1.44 | 4.57 | 4.6 | 4.03 | 0.44 | … | 30.2 | 31.8 | 146 | 114.3 | 46 | 48 | 84 | 37 | 116.1 | 116.8 | 102.4 | 11 | … | 4.63 | 117.6
16.5 | 300 | 5 | 11 | 9.25 | 0.875 | 8 | 0.75 | 4.75 | 5.25 | 4.25 | 279 | 235 | 120 | 135 | 110 | 1.31 | 1.38 | 7 | 5.56 | 1.94 | 2 | 3.82 | 1.69 | 5.66 | 5.69 | 5.05 | 0.44 | … | 33.3 | 35.1 | 178 | 141.2 | 49 | 51 | 97 | 43 | 143.8 | 144.5 | 128.3 | 11 | … | 5.69 | 144.5
16.5 | 300 | 6 | 12.5 | 10.62 | 0.875 | 12 | 0.75 | 4.75 | 5.5 | 4.25 | 318 | 269.7 | 120 | 140 | 110 | 1.38 | 1.44 | 8.12 | 6.63 | 2 | 2.06 | 3.82 | 1.81 | 6.72 | 6.75 | 6.07 | 0.5 | … | 35.1 | 36.6 | 206 | 168.4 | 51 | 52 | 97 | 46 | 170.7 | 171.4 | 154.2 | 13 | … | 6.75 | 171.4
16.5 | 300 | 8 | 15 | 13 | 1 | 12 | 0.875 | 5.5 | 6 | 4.75 | 381 | 330.2 | 140 | 150 | 120 | 1.56 | 1.62 | 10.25 | 8.63 | 2.38 | 2.44 | 4.32 | 2 | 8.72 | 8.75 | 7.98 | 0.5 | … | 39.6 | 41.1 | 260 | 219.2 | 60 | 62 | 110 | 51 | 221.5 | 222.2 | 202.7 | 13 | … | 8.75 | 222.2
16.5 | 300 | 10 | 17.5 | 15.25 | 1.125 | 16 | 1 | 6.25 | 6.75 | 5.5 | 444 | 387.4 | 160 | 170 | 140 | 1.81 | 1.88 | 12.62 | 10.75 | 2.56 | 3.75 | 4.56 | 2.19 | 10.88 | 10.92 | 10.02 | 0.5 | … | 46 | 47.8 | 321 | 273 | 65 | 95 | 116 | 56 | 276.4 | 277.4 | 254.5 | 13 | … | 10.88 | 276.4
16.5 | 300 | 12 | 20.5 | 17.75 | 1.25 | 16 | 1.125 | 6.75 | 7.25 | 5.75 | 521 | 450.8 | 170 | 185 | 145 | 1.94 | 2 | 14.75 | 12.75 | 2.82 | 4 | 5.06 | 2.38 | 12.88 | 12.92 | 12 | 0.5 | … | 49.3 | 50.8 | 375 | 323.8 | 72 | 102 | 129 | 60 | 327.2 | 328.2 | 304.8 | 13 | … | 12.94 | 328.7
16.5 | 300 | 14 | 23 | 20.25 | 1.25 | 20 | 1.125 | 7 | 7.5 | 6.25 | 584 | 514.4 | 180 | 190 | 160 | 2.06 | 2.12 | 16.75 | 14 | 2.94 | 4.38 | 5.56 | 2.5 | 14.14 | 14.18 | (7) | 0.5 | … | 52.3 | 53.8 | 425 | 355.6 | 75 | 111 | 141 | 64 | 359.2 | 360.2 | (7) | 13 | … | 14.19 | 360.4
16.5 | 300 | 16 | 25.5 | 22.5 | 1.375 | 20 | 1.25 | 7.5 | 8 | 6.5 | 648 | 571.5 | 190 | 205 | 165 | 2.19 | 2.25 | 19 | 16 | 3.19 | 4.75 | 5.69 | 2.69 | 16.16 | 16.19 | (7) | 0.5 | … | 55.6 | 57.2 | 483 | 406.4 | 81 | 121 | 145 | 68 | 410.5 | 411.2 | (7) | 13 | … | 16.19 | 411.2
16.5 | 300 | 18 | 28 | 24.75 | 1.375 | 24 | 1.25 | 7.75 | 8.25 | 6.75 | 711 | 628.6 | 195 | 210 | 170 | 2.31 | 2.38 | 21 | 18 | 3.44 | 5.12 | 6.19 | 2.75 | 18.18 | 18.2 | (7) | 0.5 | … | 58.7 | 60.5 | 533 | 457.2 | 87 | 130 | 157 | 70 | 461.8 | 462.3 | (7) | 13 | … | 18.19 | 462
16.5 | 300 | 20 | 30.5 | 27 | 1.375 | 24 | 1.25 | 8 | 8.75 | 7.25 | 775 | 685.8 | 205 | 220 | 185 | 2.44 | 2.5 | 23.12 | 20 | 3.69 | 5.5 | 6.32 | 2.88 | 20.2 | 20.25 | (7) | 0.5 | … | 62 | 63.5 | 587 | 508 | 94 | 140 | 161 | 73 | 513.1 | 514.4 | (7) | 13 | … | 20.19 | 512.8
16.5 | 300 | 22 | 33 | 29.25 | 1.625 | 24 | 1.5 | 9 | 10 | 8 | 838 | 743 | 230 | 255 | 205 | 2.56 | 2.62 | 25.25 | 22 | 3.94 | 5.69 | 6.44 | … | 22.22 | 22.25 | (7) | 0.5 | … | 65 | 66.5 | 641 | 558.8 | 100 | 145 | 164 | … | 564.4 | 565.2 | (7) | 13 | … | … | …
16.5 | 300 | 24 | 36 | 32 | 1.625 | 24 | 1.5 | 9 | 10 | 8 | 914 | 812.8 | 230 | 255 | 205 | 2.69 | 2.75 | 27.62 | 24 | 4.13 | 6 | 6.56 | 3.25 | 24.25 | 24.25 | (7) | 0.5 | … | 68.3 | 68.8 | 702 | 609.6 | 105 | 152 | 167 | 83 | 616 | 616 | (7) | 13 | … | 24.19 | 614.4
[8 empty] | Length Bolts-Raised Face (0.25 in) | Length Bolts-Ring Joint | Length Bolts-Male and Female |  |  | Length Bolts-6.4 mm Raised Face | Length Bolts-Ring Joint | Length Bolts-Male and Female
16.5 | 400 | 0.5 | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4)
16.5 | 400 | 0.75 | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4)
16.5 | 400 | 1 | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4)
16.5 | 400 | 1.25 | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4)
16.5 | 400 | 1.5 | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4)
16.5 | 400 | 2 | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4)
16.5 | 400 | 2.5 | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4)
16.5 | 400 | 3 | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4)
16.5 | 400 | 3.5 | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4)
16.5 | 400 | 4 | 10 | 7.88 | 1 | 8 | 0.875 | 5.5 | 5.5 | 5.25 | 254 | 200.2 | 140 | 140 | 135 | 1.38 | N/A | 5.75 | 4.5 | 2 | 2 | 3.5 | 1.44 | 4.57 | 4.6 | (5) | 0.44 | N/A | 35.1 | N/A | 146 | 114.3 | 51 | 51 | 89 | 37 | 116.1 | 116.8 | (5) | 11 | N/A | 4.63 | 117.6
16.5 | 400 | 5 | 11 | 9.25 | 1 | 8 | 0.875 | 5.75 | 5.75 | 5.25 | 279 | 235 | 145 | 145 | 135 | 1.5 | N/A | 7 | 5.56 | 2.12 | 2.12 | 4 | 1.69 | 5.66 | 5.69 | (5) | 0.44 | N/A | 38.1 | N/A | 178 | 141.2 | 54 | 54 | 102 | 43 | 143.8 | 144.5 | (5) | 11 | N/A | 5.69 | 144.5
16.5 | 400 | 6 | 12.5 | 10.62 | 1 | 12 | 0.875 | 6 | 6 | 5.75 | 318 | 269.7 | 150 | 150 | 145 | 1.62 | N/A | 8.12 | 6.63 | 2.25 | 2.25 | 4.06 | 1.81 | 6.72 | 6.75 | (5) | 0.5 | N/A | 41.1 | N/A | 206 | 168.4 | 57 | 57 | 103 | 46 | 170.7 | 171.4 | (5) | 13 | N/A | 6.75 | 171.4
16.5 | 400 | 8 | 15 | 13 | 1.125 | 12 | 1 | 6.75 | 6.75 | 6.5 | 381 | 330.2 | 170 | 170 | 165 | 1.88 | N/A | 10.25 | 8.63 | 2.69 | 2.69 | 4.62 | 2 | 8.72 | 8.75 | (5) | 0.5 | N/A | 47.8 | N/A | 260 | 219.2 | 68 | 68 | 117 | 51 | 221.5 | 222.2 | (5) | 13 | N/A | 8.75 | 222.2
16.5 | 400 | 10 | 17.5 | 15.25 | 1.25 | 16 | 1.125 | 7.5 | 7.5 | 7.25 | 444 | 387.4 | 190 | 190 | 185 | 2.12 | N/A | 12.62 | 10.75 | 2.88 | 4 | 4.88 | 2.19 | 10.88 | 10.92 | (5) | 0.5 | N/A | 53.8 | N/A | 321 | 273 | 73 | 102 | 124 | 56 | 276.4 | 277.4 | (5) | 13 | N/A | 10.88 | 276.4
16.5 | 400 | 12 | 20.5 | 17.75 | 1.375 | 16 | 1.25 | 8 | 8 | 7.75 | 521 | 450.8 | 205 | 205 | 195 | 2.25 | N/A | 14.75 | 12.75 | 3.12 | 4.25 | 5.38 | 2.38 | 12.88 | 12.92 | (5) | 0.5 | N/A | 57.2 | N/A | 375 | 323.8 | 79 | 108 | 137 | 60 | 327.2 | 328.2 | (5) | 13 | N/A | 12.94 | 328.7
16.5 | 400 | 14 | 23 | 20.25 | 1.375 | 20 | 1.25 | 8.25 | 8.25 | 8 | 584 | 514.4 | 210 | 210 | 205 | 2.38 | N/A | 16.75 | 14 | 3.31 | 4.62 | 5.88 | 2.5 | 14.14 | 14.18 | (5) | 0.5 | N/A | 60.5 | N/A | 425 | 355.6 | 84 | 117 | 149 | 64 | 359.2 | 360.2 | (5) | 13 | N/A | 14.19 | 360.4
16.5 | 400 | 16 | 25.5 | 23 | 1.5 | 20 | 1.375 | 8.75 | 8.75 | 8.5 | 648 | 571.5 | 220 | 220 | 215 | 2.5 | N/A | 19 | 16 | 3.69 | 5 | 6 | 2.69 | 16.16 | 16.19 | (5) | 0.5 | N/A | 63.5 | N/A | 483 | 406.4 | 94 | 127 | 152 | 68 | 410.5 | 411.2 | (5) | 13 | N/A | 16.19 | 411.2
16.5 | 400 | 18 | 28 | 24.75 | 1.5 | 24 | 1.375 | 9 | 9 | 8.75 | 711 | 628.6 | 230 | 230 | 220 | 2.62 | N/A | 21 | 18 | 3.88 | 5.38 | 6.5 | 2.75 | 18.18 | 18.2 | (5) | 0.5 | N/A | 66.5 | N/A | 533 | 457.2 | 99 | 137 | 165 | 70 | 461.8 | 462.3 | (5) | 13 | N/A | 18.19 | 462
16.5 | 400 | 20 | 30.5 | 27 | 1.625 | 24 | 1.5 | 9.5 | 9.75 | 9.25 | 775 | 685.8 | 240 | 250 | 235 | 2.75 | N/A | 23.12 | 20 | 4 | 5.75 | 6.62 | 2.88 | 20.2 | 20.25 | (5) | 0.5 | N/A | 69.8 | N/A | 587 | 508 | 102 | 146 | 168 | 73 | 513.1 | 514.4 | (5) | 13 | N/A | 20.19 | 512.8
16.5 | 400 | 22 | 33 | 29.25 | 1.75 | 24 | 1.625 | 10 | 10.25 | 9.75 | 838 | 743 | 255 | 260 | 250 | 2.88 | N/A | 25.25 | 22 | 4.25 | 6 | 6.75 | … | 22.22 | 22.25 | (5) | 0.5 | N/A | 73.2 | N/A | 641 | 558.8 | 108 | 152 | 171 | … | 564.4 | 565.2 | (5) | 13 | N/A | … | …
16.5 | 400 | 24 | 36 | 32 | 1.875 | 24 | 1.75 | 10.5 | 11 | 10.25 | 914 | 812.8 | 265 | 280 | 260 | 3 | N/A | 27.62 | 24 | 4.5 | 6.25 | 6.88 | 3.25 | 24.25 | 24.25 | (5) | 0.5 | N/A | 76.2 | N/A | 702 | 609.6 | 114 | 159 | 175 | 83 | 616 | 616 | (5) | 13 | N/A | 24.19 | 614.4
16.5 | 600 | 0.5 | 3.75 | 2 | 0.625 | 4 | 0.5 | 3 | 3 | 2.75 | 95 | 66.5 | 75 | 75 | 70 | 0.56 | N/A | 1.5 | 0.84 | 0.88 | 0.88 | 2.06 | 0.62 | 0.88 | 0.9 | (4) | 0.12 | 0.38 | 14.2 | N/A | 38 | 21.3 | 22 | 22 | 52 | 16 | 22.4 | 22.9 | (4) | 3 | 10 | 0.93 | 23.6
16.5 | 600 | 0.75 | 4.62 | 3.25 | 0.75 | 4 | 0.625 | 3.5 | 3.5 | 3.25 | 117 | 82.6 | 90 | 90 | 85 | 0.62 | N/A | 1.88 | 1.05 | 1 | 1 | 2.25 | 0.62 | 1.09 | 1.11 | (4) | 0.12 | 0.44 | 15.7 | N/A | 48 | 26.7 | 25 | 25 | 57 | 16 | 27.7 | 28.2 | (4) | 3 | 11 | 1.14 | 29
16.5 | 600 | 1 | 4.88 | 3.5 | 0.75 | 4 | 0.625 | 3.5 | 3.5 | 3.25 | 124 | 88.9 | 90 | 90 | 85 | 0.69 | N/A | 2.12 | 1.32 | 1.06 | 1.06 | 2.44 | 0.69 | 1.36 | 1.38 | (4) | 0.12 | 0.5 | 17.5 | N/A | 54 | 33.5 | 27 | 27 | 62 | 18 | 34.5 | 35.1 | (4) | 3 | 13 | 1.41 | 35.8
16.5 | 600 | 1.25 | 5.25 | 3.88 | 0.75 | 4 | 0.625 | 3.75 | 3.75 | 3.5 | 133 | 98.6 | 95 | 95 | 90 | 0.81 | N/A | 2.5 | 1.66 | 1.12 | 1.12 | 2.62 | 0.81 | 1.7 | 1.72 | (4) | 0.19 | 0.56 | 20.3 | N/A | 64 | 42.2 | 28 | 28 | 67 | 21 | 43.2 | 43.7 | (4) | 5 | 14 | 1.75 | 44.4
16.5 | 600 | 1.5 | 6.12 | 4.5 | 0.875 | 4 | 0.75 | 4.25 | 4.25 | 4 | 155 | 114.3 | 110 | 110 | 100 | 0.88 | N/A | 2.75 | 1.9 | 1.25 | 1.25 | 2.75 | 0.88 | 1.95 | 1.97 | (4) | 0.25 | 0.62 | 22.4 | N/A | 70 | 48.3 | 32 | 32 | 70 | 22 | 49.5 | 50 | (4) | 6 | 16 | 1.99 | 50.5
16.5 | 600 | 2 | 6.5 | 5 | 0.75 | 8 | 0.625 | 4.25 | 4.25 | 4 | 165 | 127 | 110 | 110 | 100 | 1 | N/A | 3.31 | 2.38 | 1.44 | 1.44 | 2.88 | 1.12 | 2.44 | 2.46 | (4) | 0.31 | 0.69 | 25.4 | N/A | 84 | 60.5 | 37 | 37 | 73 | 28 | 62 | 62.5 | (4) | 8 | 18 | 0.25 | 63.5
16.5 | 600 | 2.5 | 7.5 | 5.88 | 0.875 | 8 | 0.75 | 4.75 | 4.75 | 4.5 | 190 | 149.4 | 120 | 120 | 115 | 1.12 | N/A | 3.94 | 2.88 | 1.62 | 1.62 | 3.12 | 1.25 | 2.94 | 2.97 | (4) | 0.31 | 0.75 | 28.4 | N/A | 100 | 73.2 | 41 | 41 | 79 | 32 | 74.7 | 75.4 | (4) | 8 | 19 | 3 | 76.2
16.5 | 600 | 3 | 8.25 | 6.62 | 0.875 | 8 | 0.75 | 5 | 5 | 4.75 | 210 | 168.1 | 125 | 125 | 120 | 1.25 | N/A | 4.62 | 3.5 | 1.81 | 1.81 | 3.25 | 1.38 | 3.57 | 3.6 | (4) | 0.38 | 0.81 | 31.8 | N/A | 117 | 88.9 | 46 | 46 | 83 | 35 | 90.7 | 91.4 | (4) | 10 | 21 | 3.63 | 92.2
16.5 | 600 | 3.5 | 9 | 7.25 | 1 | 8 | 0.875 | 5.5 | 5.5 | 5.25 | 229 | 184.2 | 140 | 140 | 135 | 1.38 | N/A | 5.25 | 4 | 1.94 | 1.94 | 3.38 | 1.56 | 4.07 | 4.1 | (4) | 0.38 | … | 35.1 | N/A | 133 | 101.6 | 49 | 49 | 86 | 40 | 103.4 | 104.1 | (4) | 10 | … | 4.13 | 104.9
16.5 | 600 | 4 | 10.75 | 8.5 | 1 | 8 | 0.875 | 5.75 | 5.75 | 5.5 | 273 | 215.9 | 145 | 145 | 140 | 1.5 | N/A | 6 | 4.5 | 2.12 | 2.12 | 4 | 1.62 | 4.57 | 4.6 | (4) | 0.44 | … | 38.1 | N/A | 152 | 114.3 | 54 | 54 | 102 | 41 | 116.1 | 116.8 | (4) | 11 | … | 4.63 | 117.6
16.5 | 600 | 5 | 13 | 10.5 | 1.125 | 8 | 1 | 6.5 | 6.5 | 6.25 | 330 | 266.7 | 165 | 165 | 160 | 1.75 | N/A | 7.44 | 5.56 | 2.38 | 2.38 | 4.5 | 1.88 | 5.66 | 5.69 | (4) | 0.44 | … | 44.4 | N/A | 189 | 141.2 | 60 | 60 | 114 | 48 | 143.8 | 144.5 | (4) | 11 | … | 5.69 | 144.5
16.5 | 600 | 6 | 14 | 11.5 | 1.125 | 12 | 1 | 6.75 | 6.75 | 6.5 | 356 | 292.1 | 170 | 170 | 165 | 1.88 | N/A | 8.75 | 6.63 | 2.62 | 2.62 | 4.62 | 2 | 6.72 | 6.75 | (4) | 0.5 | … | 47.8 | N/A | 222 | 168.4 | 67 | 67 | 117 | 51 | 170.7 | 171.4 | (4) | 13 | … | 6.75 | 171.4
16.5 | 600 | 8 | 16.5 | 13.75 | 1.25 | 12 | 1.125 | 7.5 | 7.75 | 7.25 | 419 | 349.2 | 190 | 195 | 185 | 2.19 | N/A | 10.75 | 8.63 | 3 | 3 | 5.25 | 2.25 | 8.72 | 8.75 | (4) | 0.5 | … | 55.6 | N/A | 273 | 219.2 | 76 | 76 | 133 | 57 | 221.5 | 222.2 | (4) | 13 | … | 8.75 | 222.2
16.5 | 600 | 10 | 20 | 17 | 1.375 | 16 | 1.25 | 8.5 | 8.5 | 8.25 | 508 | 431.8 | 215 | 215 | 210 | 2.5 | N/A | 13.5 | 10.75 | 3.38 | 4.38 | 6 | 2.56 | 10.88 | 10.92 | (4) | 0.5 | … | 63.5 | N/A | 343 | 273 | 86 | 111 | 152 | 65 | 276.2 | 277.4 | (4) | 13 | … | 10.88 | 276.4
16.5 | 600 | 12 | 22 | 19.25 | 1.375 | 20 | 1.25 | 8.75 | 8.75 | 8.5 | 559 | 489 | 220 | 220 | 215 | 2.62 | N/A | 15.75 | 12.75 | 3.62 | 4.62 | 6.12 | 2.75 | 12.88 | 12.92 | (4) | 0.5 | … | 66.5 | N/A | 400 | 323.8 | 92 | 117 | 155 | 70 | 327 | 328.2 | (4) | 13 | … | 12.94 | 328.7
16.5 | 600 | 14 | 23.75 | 20.75 | 1.5 | 20 | 1.375 | 9.25 | 9.25 | 9 | 603 | 527 | 235 | 235 | 230 | 2.75 | N/A | 17 | 14 | 3.69 | 5 | 6.5 | 2.88 | 14.14 | 14.18 | (4) | 0.5 | … | 69.8 | N/A | 432 | 355.6 | 94 | 127 | 165 | 73 | 359.2 | 360.2 | (4) | 13 | … | 14.19 | 360.4
16.5 | 600 | 16 | 27 | 23.75 | 1.625 | 20 | 1.5 | 10 | 10 | 9.75 | 686 | 603.2 | 255 | 255 | 250 | 3 | N/A | 19.5 | 16 | 4.19 | 5.5 | 7 | 3.06 | 16.16 | 16.19 | (4) | 0.5 | … | 76.2 | N/A | 495 | 406.4 | 106 | 140 | 178 | 78 | 410.5 | 411.2 | (4) | 13 | … | 16.19 | 411.2
16.5 | 600 | 18 | 29.25 | 25.75 | 1.75 | 20 | 1.625 | 10.75 | 10.75 | 10.5 | 743 | 654 | 275 | 275 | 265 | 3.25 | N/A | 21.5 | 18 | 4.62 | 6 | 7.25 | 3.12 | 18.18 | 18.2 | (4) | 0.5 | … | 82.6 | N/A | 546 | 457.2 | 117 | 152 | 184 | 79 | 461.8 | 462.3 | (4) | 13 | … | 18.19 | 462
16.5 | 600 | 20 | 32 | 28.5 | 1.75 | 24 | 1.625 | 11.25 | 11.5 | 11 | 813 | 723.9 | 285 | 290 | 280 | 3.5 | N/A | 24 | 20 | 5 | 6.5 | 7.5 | 3.25 | 20.2 | 20.25 | (4) | 0.5 | … | 88.9 | N/A | 610 | 508 | 127 | 165 | 190 | 83 | 513.1 | 514.4 | (4) | 13 | … | 20.19 | 512.8
16.5 | 600 | 22 | 34.25 | 30.62 | 1.875 | 24 | 1.75 | 12 | 12.25 | … | 870 | 777.7 | 305 | 310 | … | 3.75 | N/A | 26.25 | 22 | 5.25 | 6.88 | 7.75 | … | 22.22 | 22.25 | (4) | 0.5 | … | 95.2 | N/A | 663 | 558.8 | 133 | 175 | 197 | … | 564.4 | 565.2 | (4) | 13 | … | … | …
16.5 | 600 | 24 | 37 | 33 | 2 | 24 | 1.875 | 13 | 13.25 | 12.75 | 940 | 838.2 | 330 | 335 | 325 | 4 | N/A | 28.25 | 24 | 5.5 | 7.25 | 8 | 3.62 | 24.25 | 24.25 | (4) | 0.5 | … | 101.6 | N/A | 718 | 609.6 | 140 | 184 | 203 | 92 | 616 | 616 | (4) | 13 | … | 24.19 | 614.4
16.5 | 900 | 0.5 | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4)
16.5 | 900 | 0.75 | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4)
16.5 | 900 | 1 | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4)
16.5 | 900 | 1.25 | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4)
16.5 | 900 | 1.5 | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4)
16.5 | 900 | 2 | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4)
16.5 | 900 | 2.5 | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (5) | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4)
16.5 | 900 | 3 | 9.5 | 7.5 | 1 | 8 | 0.875 | 5.75 | 5.5 | 5.75 | 241 | 190.5 | 145 | 140 | 145 | 1.5 | N/A | 5 | 3.5 | 2.12 | 2.12 | 4 | 1.62 | 3.57 | 3.6 | (5) | 0.38 | N/A | 38.1 | N/A | 127 | 88.9 | 54 | 54 | 102 | 41 | 90.7 | 91.4 | (5) | 10 | N/A | 3.63 | 92.2
16.5 | 900 | 4 | 11.5 | 9.25 | 1.25 | 8 | 1.125 | 6.75 | 6.5 | 6.75 | 292 | 235 | 170 | 165 | 170 | 1.75 | N/A | 6.25 | 4.5 | 2.75 | 2.75 | 4.5 | 1.88 | 4.57 | 4.6 | (5) | 0.44 | N/A | 44.5 | N/A | 159 | 114.3 | 70 | 70 | 114 | 48 | 116.1 | 116.8 | (5) | 11 | N/A | 4.63 | 117.6
16.5 | 900 | 5 | 13.75 | 11 | 1.375 | 8 | 1.25 | 7.5 | 7.25 | 7.5 | 349 | 279.4 | 190 | 185 | 190 | 2 | N/A | 7.5 | 5.56 | 3.12 | 3.12 | 5 | 2.12 | 5.66 | 5.69 | (5) | 0.44 | N/A | 50.8 | N/A | 190 | 141.2 | 79 | 79 | 127 | 54 | 143.8 | 144.5 | (5) | 11 | N/A | 5.69 | 144.5
16.5 | 900 | 6 | 15 | 12.5 | 1.25 | 12 | 1.125 | 7.5 | 7.25 | 7.75 | 381 | 317.5 | 190 | 185 | 195 | 2.19 | N/A | 9.25 | 6.63 | 3.38 | 3.38 | 5.5 | 2.25 | 6.72 | 6.75 | (5) | 0.5 | N/A | 55.6 | N/A | 235 | 168.4 | 86 | 86 | 140 | 57 | 170.7 | 171.4 | (5) | 13 | N/A | 6.75 | 171.4
16.5 | 900 | 8 | 18.5 | 15.5 | 1.5 | 12 | 1.375 | 8.75 | 8.5 | 8.75 | 470 | 393.7 | 220 | 215 | 220 | 2.5 | N/A | 11.75 | 8.63 | 4 | 4.5 | 6.38 | 2.5 | 8.72 | 8.75 | (5) | 0.5 | N/A | 63.5 | N/A | 298 | 219.2 | 102 | 114 | 162 | 64 | 221.5 | 222.2 | (5) | 13 | N/A | 8.75 | 222.2
16.5 | 900 | 10 | 21.5 | 18.5 | 1.5 | 16 | 1.375 | 9.25 | 9 | 9.25 | 546 | 469.9 | 235 | 230 | 235 | 2.75 | N/A | 14.5 | 10.75 | 4.25 | 5 | 7.25 | 2.81 | 10.88 | 10.92 | (5) | 0.5 | N/A | 69.8 | N/A | 368 | 273 | 108 | 127 | 184 | 71 | 276.4 | 277.4 | (5) | 13 | N/A | 10.88 | 276.4
16.5 | 900 | 12 | 24 | 21 | 1.5 | 20 | 1.375 | 10 | 9.75 | 10 | 610 | 533.4 | 255 | 250 | 255 | 3.12 | N/A | 16.5 | 12.75 | 4.62 | 5.62 | 7.88 | 3 | 12.88 | 12.92 | (5) | 0.5 | N/A | 79.2 | N/A | 419 | 323.8 | 117 | 143 | 200 | 76 | 327.2 | 328.2 | (5) | 13 | N/A | 12.94 | 328.7
16.5 | 900 | 14 | 25.25 | 22 | 1.625 | 20 | 1.5 | 10.75 | 10.5 | 11 | 641 | 558.8 | 275 | 265 | 280 | 3.38 | N/A | 17.75 | 14 | 5.12 | 6.12 | 8.38 | 3.25 | 14.14 | 14.18 | (5) | 0.5 | N/A | 85.9 | N/A | 451 | 355.6 | 130 | 155 | 213 | 83 | 359.2 | 360.2 | (5) | 13 | N/A | 14.19 | 360.4
16.5 | 900 | 16 | 27.75 | 24.25 | 1.75 | 20 | 1.625 | 11.25 | 11 | 11.5 | 705 | 616 | 285 | 280 | 290 | 3.5 | N/A | 20 | 16 | 5.25 | 6.5 | 8.5 | 3.38 | 16.16 | 16.19 | (5) | 0.5 | N/A | 88.9 | N/A | 508 | 406.4 | 133 | 165 | 216 | 86 | 410.5 | 411.2 | (5) | 13 | N/A | 16.19 | 411.2
16.5 | 900 | 18 | 31 | 27 | 2 | 20 | 1.875 | 12.75 | 12.5 | 13.25 | 787 | 685.8 | 325 | 320 | 335 | 4 | N/A | 22.25 | 18 | 6 | 7.5 | 9 | 3.5 | 18.18 | 18.2 | (5) | 0.5 | N/A | 101.6 | N/A | 565 | 457.2 | 152 | 190 | 229 | 89 | 461.8 | 462.3 | (5) | 13 | N/A | 18.19 | 462
16.5 | 900 | 20 | 33.75 | 29.5 | 2.125 | 20 | 2 | 13.75 | 13.5 | 14.25 | 857 | 749.3 | 350 | 345 | 360 | 4.25 | N/A | 24.5 | 20 | 6.25 | 8.25 | 9.75 | 3.62 | 20.2 | 20.25 | (5) | 0.5 | N/A | 108 | N/A | 622 | 508 | 159 | 210 | 248 | 92 | 513.1 | 514.4 | (5) | 13 | N/A | 20.19 | 512.8
16.5 | 900 | 24 | 41 | 35.5 | 2.625 | 20 | 2.5 | 17.25 | 17 | 18 | 1041 | 901.7 | 440 | 430 | 455 | 5.5 | N/A | 29.5 | 24 | 8 | 10.5 | 11.5 | 4 | 24.25 | 24.25 | (5) | 0.5 | N/A | 139.7 | N/A | 749 | 609.6 | 203 | 267 | 292 | 102 | 616 | 616 | (5) | 13 | N/A | 24.19 | 614.4
16.5 | 1500 | 0.5 | 4.75 | 3.25 | 0.875 | 4 | 0.75 | 4.25 | 4.25 | 4 | 121 | 82.6 | 110 | 110 | 100 | 0.88 | N/A | 1.5 | 0.84 | 1.25 | 1.25 | 2.28 | 0.88 | 0.88 | 0.9 | (4) | 0.12 | 0.38 | 22.4 | N/A | 38 | 21.3 | 32 | 32 | 60 | 22 | 22.4 | 22.9 | (4) | 3 | 10 | 0.93 | 23.6
16.5 | 1500 | 0.75 | 5.12 | 3.5 | 0.875 | 4 | 0.75 | 4.5 | 4.5 | 4.25 | 130 | 88.9 | 115 | 115 | 110 | 1 | N/A | 1.75 | 1.05 | 1.38 | 1.38 | 2.75 | 1 | 1.09 | 1.11 | (4) | 0.12 | 0.44 | 25.4 | N/A | 44 | 26.7 | 35 | 35 | 70 | 25 | 27.7 | 28.2 | (4) | 3 | 11 | 1.14 | 29
16.5 | 1500 | 1 | 5.88 | 4 | 1 | 4 | 0.875 | 5 | 5 | 4.75 | 149 | 101.6 | 125 | 125 | 120 | 1.12 | N/A | 2.06 | 1.32 | 1.62 | 1.62 | 2.88 | 1.12 | 1.36 | 1.38 | (4) | 0.12 | 0.5 | 28.4 | N/A | 52 | 33.5 | 41 | 41 | 73 | 28 | 34.5 | 35.4 | (4) | 3 | 13 | 1.41 | 35.8
16.5 | 1500 | 1.25 | 6.25 | 4.38 | 1 | 4 | 0.875 | 5 | 5 | 4.75 | 159 | 111.1 | 125 | 125 | 120 | 1.12 | N/A | 2.5 | 1.66 | 1.62 | 1.62 | 2.88 | 1.19 | 1.7 | 1.72 | (4) | 0.19 | 0.56 | 28.4 | N/A | 64 | 42.2 | 41 | 41 | 73 | 30 | 43.2 | 43.7 | (4) | 5 | 14 | 1.75 | 44.4
16.5 | 1500 | 1.5 | 7 | 4.88 | 1.125 | 4 | 1 | 5.5 | 5.5 | 5.25 | 178 | 124 | 140 | 140 | 135 | 1.25 | N/A | 2.75 | 1.9 | 1.75 | 1.75 | 3.25 | 1.25 | 1.95 | 1.97 | (4) | 0.25 | 0.62 | 31.8 | N/A | 70 | 48.3 | 44 | 44 | 83 | 32 | 49.5 | 50 | (4) | 6 | 16 | 1.99 | 50.5
16.5 | 1500 | 2 | 8.5 | 6.5 | 1 | 8 | 0.875 | 5.75 | 5.75 | 5.5 | 216 | 165.1 | 145 | 145 | 140 | 1.5 | N/A | 4.12 | 2.38 | 2.25 | 2.25 | 4 | 1.5 | 2.44 | 2.46 | (4) | 0.31 | 0.69 | 38.1 | N/A | 105 | 60.5 | 57 | 57 | 102 | 38 | 62 | 62.5 | (4) | 8 | 18 | 2.5 | 63.5
16.5 | 1500 | 2.5 | 9.62 | 7.5 | 1.125 | 8 | 1 | 6.25 | 6.25 | 6 | 244 | 190.5 | 160 | 160 | 150 | 1.62 | N/A | 4.88 | 2.88 | 2.5 | 2.5 | 4.12 | 1.88 | 2.94 | 2.97 | (4) | 0.31 | 0.75 | 41.1 | N/A | 124 | 73.2 | 64 | 64 | 105 | 48 | 74.7 | 75.4 | (4) | 8 | 19 | 3 | 76.2
16.5 | 1500 | 3 | 10.5 | 8 | 1.125 | 8 | 1.125 | 7 | 7 | 6.75 | 267 | 203.2 | 180 | 180 | 170 | 1.88 | N/A | 5.25 | 3.5 | … | 2.88 | 4.62 | … | … | 3.6 | (4) | 0.38 | … | 47.8 | N/A | 133 | 88.9 | … | 73 | 117 | … | … | 91.4 | (4) | 10 | … | … | …
16.5 | 1500 | 4 | 12.25 | 9.5 | 1.375 | 8 | 1.25 | 7.75 | 7.75 | 7.5 | 311 | 241.3 | 195 | 195 | 190 | 2.12 | N/A | 6.38 | 4.5 | … | 3.56 | 4.88 | … | … | 4.6 | (4) | 0.44 | … | 53.8 | N/A | 162 | 114.3 | … | 90 | 124 | … | … | 116.8 | (4) | 11 | … | … | …
16.5 | 1500 | 5 | 14.75 | 11.5 | 1.625 | 8 | 1.5 | 9.75 | 9.75 | 9.5 | 375 | 292.1 | 250 | 250 | 240 | 2.88 | N/A | 7.75 | 5.56 | … | 4.12 | 6.12 | … | … | 5.69 | (4) | 0.44 | … | 73.2 | N/A | 197 | 141.2 | … | 105 | 155 | … | … | 144.5 | (4) | 11 | … | … | …
16.5 | 1500 | 6 | 15.5 | 12.5 | 1.5 | 12 | 1.375 | 10.25 | 10.5 | 10 | 394 | 317.5 | 260 | 265 | 255 | 3.25 | N/A | 9 | 6.63 | … | 4.69 | 6.75 | … | … | 6.75 | (4) | 0.5 | … | 82.6 | N/A | 229 | 168.4 | … | 119 | 171 | … | … | 171.4 | (4) | 13 | … | … | …
16.5 | 1500 | 8 | 19 | 15.5 | 1.75 | 12 | 1.625 | 11.5 | 11.75 | 11.25 | 483 | 393.7 | 290 | 300 | 285 | 3.62 | N/A | 11.5 | 8.63 | … | 5.62 | 8.38 | … | … | 8.75 | (4) | 0.5 | … | 91.9 | N/A | 292 | 219.2 | … | 143 | 213 | … | … | 222.2 | (4) | 13 | … | … | …
16.5 | 1500 | 10 | 23 | 19 | 2 | 12 | 1.875 | 13.25 | 13.5 | 13 | 584 | 482.6 | 335 | 345 | 330 | 4.25 | N/A | 14.5 | 10.75 | … | 7 | 10 | … | … | 10.92 | (4) | 0.5 | … | 108 | N/A | 368 | 273 | … | 178 | 254 | … | … | 277.4 | (4) | 13 | … | … | …
16.5 | 1500 | 12 | 26.5 | 22.5 | 2.125 | 16 | 2 | 14.75 | 15.25 | 14.5 | 673 | 571.5 | 375 | 385 | 370 | 4.88 | N/A | 17.75 | 12.75 | … | 8.62 | 11.12 | … | … | 12.92 | (4) | 0.5 | … | 124 | N/A | 451 | 323.8 | … | 219 | 282 | … | … | 328.2 | (4) | 13 | … | … | …
16.5 | 1500 | 14 | 29.5 | 25 | 2.375 | 16 | 2.25 | 16 | 16.75 | 15.75 | 749 | 635 | 405 | 425 | 400 | 5.25 | N/A | 19.5 | 14 | … | 9.5 | 11.75 | … | … | 14.18 | (4) | 0.5 | … | 133.4 | N/A | 495 | 355.6 | … | 241 | 298 | … | … | 360.2 | (4) | 13 | … | … | …
16.5 | 1500 | 16 | 32.5 | 27.75 | 2.625 | 16 | 2.5 | 17.5 | 18.5 | 17.25 | 826 | 704.8 | 445 | 470 | 440 | 5.75 | N/A | 21.75 | 16 | … | 10.25 | 12.25 | … | … | 16.19 | (4) | 0.5 | … | 146 | N/A | 552 | 406.4 | … | 260 | 311 | … | … | 411.2 | (4) | 13 | … | … | …
16.5 | 1500 | 18 | 36 | 30.5 | 2.875 | 16 | 2.75 | 19.5 | 20.75 | 19.25 | 914 | 774.7 | 495 | 525 | 490 | 6.38 | N/A | 23.5 | 18 | … | 10.88 | 12.88 | … | … | 18.2 | (4) | 0.5 | … | 162.1 | N/A | 597 | 457.2 | … | 276 | 327 | … | … | 462.3 | (4) | 13 | … | … | …
16.5 | 1500 | 20 | 38.75 | 32.75 | 3.125 | 16 | 3 | 21.25 | 22.25 | 21 | 984 | 831.8 | 540 | 565 | 535 | 7 | N/A | 25.25 | 20 | … | 11.5 | 14 | … | … | 20.25 | (4) | 0.5 | … | 177.8 | N/A | 641 | 508 | … | 292 | 356 | … | … | 514.4 | (4) | 13 | … | … | …
16.5 | 1500 | 24 | 46 | 39 | 3.625 | 16 | 3 | 24.25 | 25.5 | 24 | 1168 | 990.6 | 615 | 650 | 610 | 8 | N/A | 30 | 24 | … | 13 | 16 | … | … | 24.25 | (4) | 0.5 | … | 203.2 | N/A | 762 | 609.6 | … | 330 | 406 | … | … | 616 | (4) | 13 | … | … | …
16.5 | 2500 | 0.5 | 5.25 | 3.5 | 0.875 | 4 | 0.75 | 4.75 | 4.75 | 4.5 | 133 | 88.9 | 120 | 120 | 115 | 1.19 | N/A | 1.69 | 0.84 | 1.56 | 1.56 | 2.88 | 1.12 | N/A | 0.9 | (4) | 0.12 | N/A | 30.2 | N/A | 43 | 21.3 | 40 | 40 | 73 | 28 | N/A | 22.9 | (4) | 3 | N/A | 0.93 | 23.6
16.5 | 2500 | 0.75 | 5.5 | 3.75 | 0.875 | 4 | 0.75 | 5 | 5 | 4.75 | 140 | 95.2 | 125 | 125 | 120 | 1.25 | N/A | 2 | 1.05 | 1.69 | 1.69 | 3.12 | 1.25 | N/A | 1.11 | (4) | 0.12 | N/A | 31.8 | N/A | 51 | 26.7 | 43 | 43 | 79 | 32 | N/A | 28.2 | (4) | 3 | N/A | 1.14 | 29
16.5 | 2500 | 1 | 6.25 | 4.25 | 1 | 4 | 0.875 | 5.5 | 5.5 | 5.25 | 159 | 108 | 140 | 140 | 135 | 1.38 | N/A | 2.25 | 1.32 | 1.88 | 1.88 | 3.5 | 1.38 | N/A | 1.38 | (4) | 0.12 | N/A | 35.1 | N/A | 57 | 33.5 | 52 | 48 | 89 | 35 | N/A | 35.1 | (4) | 3 | N/A | 1.41 | 35.8
16.5 | 2500 | 1.25 | 7.25 | 5.12 | 1.125 | 4 | 1 | 6 | 6 | 5.75 | 184 | 130 | 150 | 150 | 145 | 1.5 | N/A | 2.88 | 1.66 | 2.06 | 2.06 | 3.75 | 1.5 | N/A | 1.72 | (4) | 0.19 | N/A | 38.1 | N/A | 73 | 42.2 | 60 | 52 | 95 | 38 | N/A | 43.7 | (4) | 5 | N/A | 1.75 | 44.4
16.5 | 2500 | 1.5 | 8 | 5.75 | 1.25 | 4 | 1.125 | 6.75 | 6.75 | 6.5 | 203 | 146 | 170 | 170 | 165 | 1.75 | N/A | 3.12 | 1.9 | 2.38 | 2.38 | 4.38 | 1.75 | N/A | 1.97 | (4) | 0.25 | N/A | 44.4 | N/A | 79 | 48.3 | 70 | 60 | 111 | 44 | N/A | 50 | (4) | 6 | N/A | 1.99 | 50.5
16.5 | 2500 | 2 | 9.25 | 6.75 | 1.125 | 8 | 1 | 7 | 7 | 6.75 | 235 | 171.4 | 180 | 180 | 170 | 2 | N/A | 3.75 | 2.38 | 2.75 | 2.75 | 5 | 2 | N/A | 2.46 | (4) | 0.31 | N/A | 50.8 | N/A | 95 | 60.5 | 79 | 70 | 127 | 51 | N/A | 62.5 | (4) | 8 | N/A | 2.5 | 63.5
16.5 | 2500 | 2.5 | 10.5 | 7.75 | 1.25 | 8 | 1.125 | 7.75 | 8 | 7.5 | 267 | 196.8 | 195 | 205 | 190 | 2.25 | N/A | 4.5 | 2.88 | 3.12 | 3.12 | 5.62 | 2.25 | N/A | 2.97 | (4) | 0.31 | N/A | 57.2 | N/A | 114 | 73.2 | … | 79 | 143 | 57 | N/A | 75.4 | (4) | 8 | N/A | 3 | 76.2
16.5 | 2500 | 3 | 12 | 9 | 1.375 | 8 | 1.25 | 8.75 | 9 | 8.5 | 305 | 228.6 | 220 | 230 | 215 | 2.62 | N/A | 5.25 | 3.5 | … | 3.62 | 6.62 | … | N/A | 3.6 | (4) | 0.38 | N/A | 66.5 | N/A | 133 | 88.9 | … | 92 | 168 | … | N/A | 91.4 | (4) | 10 | N/A | … | …
16.5 | 2500 | 4 | 14 | 10.75 | 1.625 | 8 | 1.5 | 10 | 10.25 | 9.75 | 356 | 273 | 255 | 260 | 250 | 3 | N/A | 6.5 | 4.5 | … | 4.25 | 7.5 | … | N/A | 4.6 | (4) | 0.44 | N/A | 76.2 | N/A | 165 | 114.3 | … | 108 | 190 | … | N/A | 116.8 | (4) | 11 | N/A | … | …
16.5 | 2500 | 5 | 16.5 | 12.75 | 1.875 | 8 | 1.75 | 11.75 | 12.25 | 11.5 | 419 | 323.8 | 300 | 310 | 290 | 3.62 | N/A | 8 | 5.56 | … | 5.12 | 9 | … | N/A | 5.69 | (4) | 0.44 | N/A | 91.9 | N/A | 203 | 141.2 | … | 130 | 229 | … | N/A | 144.5 | (4) | 11 | N/A | … | …
16.5 | 2500 | 6 | 19 | 14.5 | 2.125 | 8 | 2 | 13.5 | 14 | 13.25 | 483 | 368.3 | 345 | 355 | 335 | 4.25 | N/A | 9.25 | 6.63 | … | 6 | 10.75 | … | N/A | 6.75 | (4) | 0.5 | N/A | 108 | N/A | 235 | 168.4 | … | 152 | 273 | … | N/A | 171.4 | (4) | 13 | N/A | … | …
16.5 | 2500 | 8 | 21.75 | 17.25 | 2.125 | 12 | 2 | 15 | 15.5 | 14.75 | 552 | 438.2 | 380 | 395 | 375 | 5 | N/A | 12 | 8.63 | … | 7 | 12.5 | … | N/A | 8.75 | (4) | 0.5 | N/A | 127 | N/A | 605 | 219.2 | … | 178 | 318 | … | N/A | 222.2 | (4) | 13 | N/A | … | …
16.5 | 2500 | 10 | 26.5 | 21.25 | 2.625 | 12 | 2.5 | 19.25 | 20 | 19 | 673 | 539.8 | 490 | 510 | 485 | 6.5 | N/A | 14.75 | 10.75 | … | 9 | 16.5 | … | N/A | 10.92 | (4) | 0.5 | N/A | 165.1 | N/A | 375 | 273 | … | 229 | 419 | … | N/A | 277.4 | (4) | 13 | N/A | … | …
16.5 | 2500 | 12 | 30 | 24.38 | 2.875 | 12 | 2.75 | 21.25 | 22 | 21 | 762 | 619.3 | 540 | 560 | 535 | 7.25 | N/A | 17.38 | 12.75 | … | 10 | 18.25 | … | N/A | 12.92 | (4) | 0.5 | N/A | 184.2 | N/A | 441 | 323.8 | … | 2543 | 464 | … | N/A | 328.2 | (4) | 13 | N/A | … | …
ASME | Flange Class | Nominal Pipe Size (NPS) | Outside Diameter Flange (O) | Min Thickness Flange- WNF | Min Thickness Flange- WNF-Blind | Length Through Hub (Y) | Diameter of Hub (X) | Hub Diameter Top (A) | Raised Face Diameter (R) | Drilling-Daimeter Bolt Circle | Drilling- # Bolt Holes | Drilling- Diameter Bolt Hole | Diameter of Bolt | Min Fillet Radius | Length of Bolts- Stud Bolt Raised Face (.25 in) | Length of Bolts- Stud Bolt Ring Joint | Outside Diameter Flange (O) | Min Thickness Flange- WNF | Min Thickness Flange-Blind | Length Through Hub (Y) | Diameter of Hub (X) | Hub Diameter Top (A) | Raised Face Diameter (R) | Drilling-Daimeter Bolt Circle | Min Fillet Radius | Length of Bolts- Stud Bolt Raised Face (6.44mm) | Length of Bolts- Stud Bolt Ring Joint
16.47 Series A | 400 | 26 | 38.25 | 3.5 | 3.88 | 7.62 | 28.62 | 26 | 29.5 | 34.5 | 28 | 1.875 | 1.75 | 0.44 | 12 | 12.5 | 972 | 88.9 | 98.6 | 194 | 727 | 660.4 | 749 | 876.3 | 11 | 310 | 320
16.47 Series A | 400 | 28 | 40.75 | 3.75 | 4.12 | 8.12 | 30.81 | 28 | 31.5 | 37 | 28 | 2 | 1.875 | 0.5 | 13 | 13.5 | 1035 | 95.2 | 104.6 | 206 | 783 | 711.2 | 800 | 939.8 | 13 | 330 | 340
16.47 Series A | 400 | 30 | 43 | 4 | 4.38 | 8.62 | 32.94 | 30 | 33.75 | 39.25 | 28 | 2.125 | 2 | 0.5 | 13.5 | 14 | 1092 | 101.6 | 111.3 | 219 | 837 | 762 | 857 | 997 | 13 | 345 | 360
16.47 Series A | 400 | 32 | 45.25 | 4.25 | 4.56 | 9.12 | 35 | 32 | 36 | 41.5 | 28 | 2.125 | 2 | 0.5 | 14 | 14.75 | 1149 | 108 | 115.8 | 232 | 339 | 812.8 | 914 | 1054.1 | 13 | 360 | 375
16.47 Series A | 400 | 34 | 47.5 | 4.38 | 4.81 | 9.5 | 37.19 | 34 | 38 | 43.5 | 28 | 2.125 | 2 | 0.56 | 14.5 | 15 | 1206 | 111.3 | 122.2 | 241 | 945 | 863.6 | 965 | 1104.9 | 14 | 365 | 380
16.47 Series A | 400 | 36 | 50 | 4.5 | 5.06 | 9.88 | 39.38 | 36 | 40.25 | 46 | 32 | 2.125 | 2 | 0.56 | 14.5 | 15.25 | 1270 | 114.3 | 128.5 | 251 | 1000 | 914.4 | 1022 | 1168.4 | 14 | 375 | 385
16.47 Series A | 400 | 38 | 47.5 | 4.88 | 4.88 | 8.12 | 39.5 | 38 | 40.75 | 44 | 32 | 1.875 | 1.75 | 0.56 | 15 | … | 1206 | 124 | 124 | 206 | 1003 | 965.2 | 1035 | 1117.6 | 14 | 380 | …
16.47 Series A | 400 | 40 | 50 | 5.12 | 5.12 | 8.5 | 41.5 | 40 | 43 | 46.25 | 32 | 2 | 1.875 | 0.56 | 15.5 | … | 1270 | 130 | 130 | 216 | 1054 | 1016 | 1092 | 1174.8 | 14 | 405 | …
16.47 Series A | 400 | 42 | 52 | 5.25 | 5.25 | 8.81 | 43.62 | 42 | 45 | 48.25 | 32 | 2 | 1.875 | 0.56 | 16 | … | 1321 | 133.4 | 133.4 | 224 | 1108 | 1066.8 | 1143 | 1225.6 | 14 | 405 | …
16.47 Series A | 400 | 44 | 54.5 | 5.5 | 5.5 | 9.18 | 45.62 | 44 | 47.25 | 50.5 | 32 | 2.125 | 2 | 0.56 | 16.5 | … | 1384 | 139.7 | 139.7 | 233 | 1159 | 1117.6 | 1200 | 1282.7 | 14 | 425 | …
16.47 Series A | 400 | 46 | 56.75 | 5.75 | 5.75 | 9.62 | 47.75 | 46 | 49.5 | 52.75 | 36 | 2.125 | 2 | 0.56 | 17 | … | 1441 | 146 | 146 | 244 | 1213 | 1168.4 | 1257 | 1339.8 | 14 | 435 | …
16.47 Series A | 400 | 48 | 59.5 | 6 | 6 | 10.12 | 49.88 | 48 | 51.5 | 55.25 | 28 | 2.375 | 2.25 | 0.56 | 18 | … | 1511 | 152.4 | 152.4 | 257 | 1267 | 1219.2 | 1308 | 1403.4 | 14 | 460 | …
16.47 Series A | 400 | 50 | 61.75 | 6.19 | 6.25 | 10.56 | 52 | 50 | 53.62 | 57.5 | 32 | 2.375 | 2.25 | 0.56 | 18.5 | … | 1568 | 157.2 | 158.8 | 268 | 1321 | 1270 | 1362 | 1460.5 | 14 | 470 | …
16.47 Series A | 400 | 52 | 63.75 | 6.38 | 6.44 | 10.88 | 54 | 52 | 55.62 | 59.5 | 32 | 2.375 | 2.25 | 0.56 | 19 | … | 1619 | 162.1 | 163.6 | 276 | 1372 | 1320.8 | 1413 | 1511.3 | 14 | 480 | …
16.47 Series A | 400 | 54 | 67 | 6.69 | 6.75 | 11.38 | 56.12 | 54 | 57.88 | 62.25 | 28 | 2.625 | 2.5 | 0.56 | 20 | … | 1702 | 169.9 | 171.4 | 289 | 1425 | 1371.6 | 1470 | 1581.2 | 14 | 510 | …
16.47 Series A | 400 | 56 | 69 | 6.88 | 6.94 | 11.75 | 58.25 | 56 | 60.12 | 64.25 | 32 | 2.625 | 2.5 | 0.56 | 20.5 | … | 1753 | 174.8 | 176.3 | 298 | 1480 | 1422.4 | 1527 | 1632 | 14 | 520 | …
16.47 Series A | 400 | 58 | 71 | 7 | 7.12 | 12.06 | 60.25 | 58 | 62.12 | 66.25 | 32 | 2.625 | 2.5 | 0.56 | 20.75 | … | 1803 | 177.8 | 180.8 | 306 | 1530 | 1473.2 | 1578 | 1682.8 | 14 | 530 | …
16.47 Series A | 400 | 60 | 74.25 | 7.31 | 7.44 | 12.56 | 62.38 | 60 | 64.38 | 69 | 32 | 2.875 | 2.75 | 0.56 | 21.75 | … | 1886 | 185.7 | 189 | 319 | 1584 | 1524 | 1635 | 1752.6 | 14 | 560 | …
16.47 Series A | 600 | 26 | 40 | 4.25 | 4.94 | 8.75 | 29.44 | 26 | 29.5 | 36 | 28 | 2 | 1.875 | 0.5 | 14 | 14.25 | 1016 | 108 | 125.5 | 222 | 748 | 660.4 | 749 | 914.4 | 13 | 355 | 365
16.47 Series A | 600 | 28 | 42.25 | 4.38 | 5.19 | 9.25 | 31.62 | 28 | 31.5 | 38 | 28 | 2.125 | 2 | 0.5 | 14.5 | 15 | 1073 | 111.3 | 131.8 | 235 | 803 | 711.2 | 800 | 965.2 | 13 | 365 | 375
16.47 Series A | 600 | 30 | 44.5 | 4.5 | 5.5 | 9.75 | 33.94 | 30 | 33.75 | 40.25 | 28 | 2.375 | 2 | 0.5 | 14.5 | 15 | 1130 | 114.3 | 139.7 | 248 | 862 | 762 | 857 | 1022.4 | 13 | 375 | 385
16.47 Series A | 600 | 32 | 47 | 4.62 | 5.81 | 10.25 | 36.12 | 32 | 36 | 42.5 | 28 | 2.375 | 2.25 | 0.56 | 15.25 | 16 | 1194 | 117.3 | 147.6 | 260 | 917 | 812.8 | 914 | 1079.5 | 13 | 390 | 405
16.47 Series A | 600 | 34 | 49 | 4.75 | 6.06 | 10.62 | 38.31 | 34 | 38 | 44.5 | 28 | 2.625 | 2.25 | 0.56 | 15.5 | 16.25 | 1245 | 120.6 | 153.9 | 270 | 973 | 863.6 | 965 | 1130.3 | 14 | 400 | 410
16.47 Series A | 600 | 36 | 51.75 | 4.88 | 6.38 | 11.12 | 40.62 | 36 | 40.25 | 47 | 28 | 2.375 | 2.5 | 0.56 | 16.5 | 17 | 1314 | 124 | 162.1 | 282 | 1032 | 914.4 | 1022 | 1193.8 | 14 | 415 | 430
16.47 Series A | 600 | 38 | 50 | 6 | 6.12 | 10 | 40.25 | 38 | 41.5 | 45.75 | 28 | 2.375 | 2.25 | 0.56 | 18.25 | … | 1270 | 152.4 | 155.4 | 254 | 1022 | 965.2 | 1054 | 1162 | 14 | 465 | …
16.47 Series A | 600 | 40 | 52 | 6.25 | 6.38 | 10.38 | 42.25 | 40 | 43.75 | 47.75 | 32 | 2.625 | 2.25 | 0.56 | 18.75 | … | 1321 | 158.8 | 162.1 | 264 | 1073 | 1016 | 1111 | 1212.8 | 14 | 480 | …
16.47 Series A | 600 | 42 | 55.25 | 6.62 | 6.75 | 11 | 44.38 | 42 | 46 | 50.5 | 28 | 2.625 | 2.5 | 0.56 | 20 | … | 1403 | 168.1 | 171.4 | 279 | 1127 | 1066.8 | 1168 | 1282.7 | 14 | 510 | …
16.47 Series A | 600 | 44 | 57.25 | 6.81 | 7 | 11.38 | 46.5 | 44 | 48.25 | 52.5 | 32 | 2.625 | 2.5 | 0.56 | 20.25 | … | 1454 | 173 | 177.8 | 289 | 1181 | 1117.6 | 1226 | 1333.5 | 14 | 520 | …
16.47 Series A | 600 | 46 | 59.5 | 7.06 | 7.31 | 11.81 | 48.62 | 46 | 50.25 | 54.75 | 32 | 2.875 | 2.5 | 0.56 | 20.75 | … | 1511 | 179.3 | 185.7 | 300 | 1235 | 1168.4 | 1276 | 1390.6 | 14 | 530 | …
16.47 Series A | 600 | 48 | 62.75 | 7.44 | 7.69 | 12.44 | 50.75 | 48 | 52.5 | 57.5 | 32 | 3.125 | 2.75 | 0.56 | 22 | … | 15.94 | 189 | 195.3 | 316 | 1289 | 1219.2 | 1334 | 1460.5 | 14 | 565 | …
16.47 Series A | 600 | 50 | 65.75 | 7.75 | 8 | 12.94 | 52.88 | 50 | 54.5 | 60 | 28 | 3.125 | 3 | 0.56 | 23.25 | … | 1670 | 196.8 | 203.2 | 329 | 1343 | 1270 | 1384 | 1524 | 14 | 595 | …
16.47 Series A | 600 | 52 | 67.75 | 8 | 8.25 | 13.25 | 54.88 | 52 | 56.5 | 62 | 32 | 3.125 | 3 | 0.56 | 23.75 | … | 1721 | 203.2 | 209.6 | 337 | 1394 | 1320.8 | 1435 | 1574.8 | 14 | 605 | …
16.47 Series A | 600 | 54 | 70 | 8.25 | 8.56 | 13.75 | 57 | 54 | 58.75 | 64.25 | 32 | 3.125 | 3 | 0.56 | 2425 | … | 1778 | 209.6 | 217.4 | 349 | 1448 | 1371.6 | 1492 | 1632 | 14 | 620 | …
16.47 Series A | 600 | 56 | 73 | 8.56 | 8.88 | 14.25 | 59.12 | 56 | 60.75 | 66.75 | 32 | 3.375 | 3.25 | 0.62 | 25.5 | … | 1854 | 217.4 | 225.6 | 362 | 1502 | 1422.4 | 1543 | 1695.4 | 16 | 645 | …
16.47 Series A | 600 | 58 | 75 | 8.75 | 9.12 | 14.53 | 61.12 | 58 | 63 | 68.75 | 32 | 3.375 | 3.25 | 0.62 | 25.75 | … | 1905 | 222.2 | 231.6 | 370 | 1553 | 1473.2 | 1600 | 1746.2 | 16 | 655 | …
16.47 Series A | 600 | 60 | 78.5 | 9.19 | 9.56 | 15.31 | 63.38 | 60 | 65.25 | 71.75 | 28 | 3.625 | 3.5 | 0.69 | 27.25 | … | 1994 | 233.4 | 242.8 | 389 | 1610 | 1524 | 1657 | 1822.4 | 17 | 690 | …
16.47 Series A | 900 | 26 | 42.75 | 5.5 | 6.31 | 11.25 | 30.5 | 26 | 29.5 | 37.5 | 20 | 2.875 | 2.75 | 0.44 | 18.25 | 19 | 1086 | 139.7 | 160.3 | 286 | 775 | 660.4 | 749 | 952.5 | 11 | 465 | 485
16.47 Series A | 900 | 28 | 46 | 5.62 | 6.753 | 11.75 | 32.75 | 28 | 31.5 | 40.25 | 20 | 3.125 | 3 | 0.5 | 19 | 19.75 | 1168 | 142.7 | 171.4 | 298 | 832 | 711.2 | 800 | 1022.4 | 13 | 485 | 505
16.47 Series A | 900 | 30 | 48.5 | 5.88 | 7.18 | 12.25 | 35 | 30 | 33.75 | 42.75 | 20 | 3.125 | 3 | 0.5 | 19.5 | 20.25 | 1232 | 129.4 | 182.4 | 311 | 889 | 762 | 857 | 1085.8 | 13 | 495 | 520
16.47 Series A | 900 | 32 | 51.75 | 6.25 | 7.62 | 13 | 37.25 | 32 | 36 | 45.5 | 20 | 3.375 | 3.25 | 0.5 | 20.75 | 21.5 | 1314 | 158.8 | 193.5 | 330 | 946 | 812.8 | 914 | 1155.7 | 13 | 530 | 550
16.47 Series A | 900 | 34 | 55 | 6.5 | 8.06 | 13.75 | 39.62 | 34 | 38 | 48.25 | 20 | 3.625 | 3.5 | 0.56 | 21.75 | 22.75 | 1397 | 165.1 | 204.7 | 349 | 1006 | 863.6 | 965 | 1225.6 | 14 | 555 | 580
16.47 Series A | 900 | 36 | 57.5 | 6.75 | 8.44 | 14.25 | 41.88 | 36 | 40.25 | 50.75 | 20 | 3.625 | 3.5 | 0.56 | 22.25 | 23.25 | 1460 | 171.4 | 214.4 | 362 | 1064 | 914.4 | 1022 | 1289 | 14 | 565 | 595
16.47 Series A | 900 | 38 | 57.5 | 7.5 | 8.5 | 13.88 | 42.25 | 38 | 43.25 | 50.75 | 20 | 3.625 | 3.5 | 0.75 | 23.75 | … | 1460 | 190.5 | 215.9 | 353 | 1073 | 965.2 | 1099 | 1289 | 19 | 605 | …
16.47 Series A | 900 | 40 | 59.5 | 7.75 | 8.81 | 14.31 | 44.38 | 40 | 45.75 | 52.75 | 24 | 3.625 | 3.5 | 0.81 | 24.5 | … | 1511 | 196.8 | 223.8 | 363 | 1127 | 1016 | 1162 | 1339.8 | 21 | 620 | …
16.47 Series A | 900 | 42 | 61.5 | 8.12 | 9.12 | 14.62 | 46.31 | 42 | 47.75 | 54.75 | 24 | 3.625 | 3.5 | 0.81 | 25 | … | 1562 | 206.2 | 231.6 | 371 | 1176 | 1066.8 | 1213 | 1390.6 | 21 | 635 | …
16.47 Series A | 900 | 44 | 64.88 | 8.44 | 9.56 | 15.38 | 48.62 | 44 | 50 | 57.75 | 24 | 3.875 | 3.75 | 0.88 | 26 | … | 1648 | 214.4 | 242.8 | 391 | 1235 | 1117.6 | 1270 | 1463.5 | 22 | 665 | …
16.47 Series A | 900 | 46 | 68.25 | 8.88 | 10.06 | 16.18 | 50.88 | 46 | 52.5 | 60.5 | 24 | 4.125 | 4 | 0.88 | 27.5 | … | 1734 | 225.6 | 255.5 | 411 | 1292 | 1168.4 | 1334 | 1536.7 | 22 | 7000 | …
16.47 Series A | 900 | 48 | 70.25 | 9.19 | 10.38 | 16.5 | 52.88 | 48 | 54.5 | 62.5 | 24 | 4.125 | 4 | 0.94 | 28 | … | 1784 | 233.4 | 263.7 | 419 | 1343 | 1219.2 | 1384 | 1587.5 | 24 | 715 | …
16.47 Series A | 900 | 50 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series A | 900 | 52 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series A | 900 | 54 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series A | 900 | 56 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series A | 900 | 58 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series A | 900 | 60 | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | … | …
16.47 Series B | 400 | 26 | 33.5 | 3.5 | 3.5 | 5.88 | 27.12 | 26 | 28 | 30.75 | 28 | 1.5 | 1.375 | 0.44 | 14.25 | N/A | 851 | 88.9 | 88.9 | 149 | 689 | 660.4 | 711 | 781 | 11 | 290 | N/A
16.47 Series B | 400 | 28 | 36 | 3.75 | 3.75 | 6.25 | 29.12 | 28 | 30 | 33 | 24 | 1.625 | 1.5 | 0.5 | 14.75 | N/A | 914 | 95.2 | 95.2 | 159 | 740 | 711.2 | 762 | 838.2 | 13 | 310 | N/A
16.47 Series B | 400 | 30 | 38.25 | 4 | 4 | 6.69 | 31.25 | 30 | 32.25 | 35.25 | 28 | 1.625 | 1.5 | 0.5 | 15.5 | N/A | 972 | 101.6 | 101.6 | 170 | 794 | 768 | 819 | 895.4 | 13 | 320 | N/A
16.47 Series B | 400 | 32 | 40.75 | 4.25 | 4.25 | 7.06 | 33.25 | 32 | 34.38 | 37.25 | 28 | 1.75 | 1.625 | 0.5 | 16.25 | N/A | 1035 | 108 | 108 | 179 | 845 | 812.8 | 873 | 952.5 | 13 | 345 | N/A
16.47 Series B | 400 | 34 | 42.75 | 4.38 | 4.38 | 7.38 | 35.38 | 34 | 36.5 | 39.5 | 32 | 1.75 | 1.625 | 0.56 | 17.25 | N/A | 1086 | 111.3 | 111.3 | 187 | 899 | 863.6 | 927 | 1003.3 | 14 | 345 | N/A
16.47 Series B | 400 | 36 | 45.5 | 4.69 | 4.69 | 7.88 | 37.5 | 36 | 38.62 | 42 | 28 | 1.875 | 1.75 | 0.56 | 18 | N/A | 1156 | 119.1 | 119.1 | 200 | 952 | 914.4 | 981 | 1066.8 | 14 | 370 | N/A
16.47 Series B | 400 | 38 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 400 | 40 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 400 | 42 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 400 | 44 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 400 | 46 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 400 | 48 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 400 | 50 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 400 | 52 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 400 | 54 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 400 | 56 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 400 | 58 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 400 | 60 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 600 | 26 | 35 | 4.38 | 4.38 | 7.12 | 27.5 | 26 | 28.62 | 31.75 | 28 | 1.75 | 1.625 | 0.5 | 14.25 | N/A | 889 | 111.3 | 111.3 | 181 | 698 | 660.4 | 727 | 806.4 | 13 | 360 | N/A
16.47 Series B | 600 | 28 | 37.5 | 4.56 | 4.56 | 7.5 | 29.62 | 28 | 30.88 | 34 | 28 | 1.875 | 1.75 | 0.5 | 14.75 | N/A | 952 | 115.8 | 115.8 | 190 | 752 | 711.2 | 784 | 863.6 | 13 | 375 | N/A
16.47 Series B | 600 | 30 | 40.25 | 4.94 | 5 | 8.06 | 31.75 | 30 | 33.12 | 36.5 | 28 | 2 | 1.875 | 0.5 | 15.5 | N/A | 1022 | 125.5 | 127 | 205 | 806 | 762 | 841 | 927.1 | 13 | 395 | N/A
16.47 Series B | 600 | 32 | 42.75 | 5.12 | 5.31 | 8.5 | 33.88 | 32 | 35.25 | 38.75 | 28 | 2.125 | 2 | 0.5 | 16.25 | N/A | 1086 | 130 | 134.9 | 216 | 861 | 812.8 | 895 | 984.2 | 13 | 415 | N/A
16.47 Series B | 600 | 34 | 45.75 | 5.56 | 5.68 | 9.19 | 36 | 34 | 37.5 | 41.5 | 24 | 2.375 | 2.25 | 0.56 | 17.25 | N/A | 1162 | 141.2 | 144.3 | 233 | 914 | 863.6 | 952 | 1054.1 | 14 | 440 | N/A
16.47 Series B | 600 | 36 | 47.75 | 5.75 | 5.94 | 9.56 | 38.12 | 36 | 39.75 | 43.5 | 28 | 2.375 | 2.25 | 0.56 | 18 | N/A | 1213 | 146 | 150.9 | 243 | 968 | 914.4 | 1010 | 1104.9 | 14 | 460 | N/A
16.47 Series B | 600 | 38 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 600 | 40 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 600 | 42 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 600 | 44 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 600 | 46 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 600 | 48 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 600 | 50 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 600 | 52 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 600 | 54 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 600 | 56 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 600 | 58 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 600 | 60 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 900 | 26 | 40.25 | 5.31 | 6.06 | 10.19 | 29.25 | 26 | 30 | 35.5 | 20 | 2.625 | 2.5 | 0.44 | 17.75 | N/A | 1022 | 134.9 | 153.9 | 259 | 743 | 660.4 | 762 | 901.7 | 11 | 450 | N/A
16.47 Series B | 900 | 28 | 43.5 | 5.81 | 6.56 | 10.88 | 31.38 | 28 | 32.25 | 38.25 | 20 | 2.875 | 2.75 | 0.5 | 19.25 | N/A | 1105 | 147.6 | 166.6 | 276 | 797 | 711.2 | 819 | 971.6 | 13 | 495 | N/A
16.47 Series B | 900 | 30 | 46.5 | 6.12 | 6.93 | 11.38 | 33.5 | 30 | 34.5 | 40.75 | 20 | 3.125 | 3 | 0.5 | 20 | N/A | 1181 | 155.4 | 176 | 289 | 851 | 762 | 876 | 1035 | 13 | 510 | N/A
16.47 Series B | 900 | 32 | 48.75 | 6.31 | 7.31 | 11.94 | 35.75 | 32 | 36.5 | 43 | 20 | 3.125 | 3 | 0.5 | 20.75 | N/A | 1238 | 160.3 | 185.7 | 303 | 908 | 812.8 | 927 | 1092.2 | 13 | 530 | N/A
16.47 Series B | 900 | 34 | 51.75 | 6.75 | 7.68 | 12.56 | 37.88 | 34 | 39 | 45.5 | 20 | 3.375 | 3.25 | 0.56 | 22.25 | N/A | 1314 | 171.4 | 195 | 319 | 962 | 863.6 | 991 | 1155.7 | 14 | 565 | N/A
16.47 Series B | 900 | 36 | 53 | 6.81 | 7.94 | 12.81 | 40 | 36 | 40.5 | 47.25 | 24 | 3.125 | 3 | 0.56 | 22.5 | N/A | 1346 | 173 | 201.7 | 325 | 1016 | 914.4 | 1029 | 1200.2 | 14 | 570 | N/A
16.47 Series B | 900 | 38 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 900 | 40 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 900 | 42 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 900 | 44 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 900 | 46 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 900 | 48 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 900 | 50 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 900 | 52 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 900 | 54 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 900 | 56 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 900 | 58 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
16.47 Series B | 900 | 60 | … | … | … | … | … | … | … | … | … | … | … | … | … | N/A | … | … | … | … | … | … | … | … | … | … | N/A
ASME | Flange Class | Nominal Pipe Size (NPS) | Outside Diameter Flange (O) | Min Thickness Flange- WNF | Min Thickness Flange- WNF-Blind | Length Through Hub (Y) | Diameter of Hub (X) | Hub Diameter Top (A) | Raised Face Diameter (R) | Drilling-Daimeter Bolt Circle | Drilling- # Bolt Holes | Drilling- Diameter Bolt Hole | Diameter of Bolt | Min Fillet Radius | Length of Bolts- Stud Bolt Raised Face (.06 in) | Length of Bolts- Stud Bolt Ring Joint | Outside Diameter Flange (O) | Min Thickness Flange- WNF | Min Thickness Flange-Blind | Length Through Hub (Y) | Diameter of Hub (X) | Hub Diameter Top (A) | Raised Face Diameter (R) | Drilling-Daimeter Bolt Circle | Min Fillet Radius | Length of Bolts- Stud Bolt Raised Face (1.6 mm) | Length of Bolts- Stud Bolt Ring Joint
16.47 Series A | 300 | 26 | 38.25 | 3.07 | 3.25 | 7.19 | 28.38 | 26 | 29.5 | 34.5 | 28 | 1.75 | 1.625 | 0.38 | 10.5 | 11.5 | 972 | 78 | 82.6 | 183 | 721 | 660.4 | 749 | 876.3 | 10 | 270 | 290
16.47 Series A | 300 | 28 | 40.75 | 3.32 | 3.5 | 7.69 | 30.5 | 28 | 31.5 | 37 | 28 | 1.75 | 1.625 | 0.44 | 11 | 12 | 1035 | 84.3 | 88.9 | 195 | 775 | 711.2 | 800 | 939.8 | 11 | 280 | 300
16.47 Series A | 300 | 30 | 43 | 3.57 | 3.69 | 8.19 | 32.56 | 30 | 33.75 | 39.25 | 28 | 1.875 | 1.75 | 0.44 | 11.75 | 12.75 | 1092 | 90.7 | 93.7 | 208 | 827 | 762 | 857 | 997 | 11 | 300 | 320
16.47 Series A | 300 | 32 | 45.25 | 3.82 | 3.88 | 8.69 | 34.69 | 32 | 36 | 41.5 | 28 | 2 | 1.875 | 0.44 | 12.75 | 13.75 | 1149 | 97 | 98.6 | 221 | 881 | 812.8 | 914 | 1054.1 | 11 | 320 | 345
16.47 Series A | 300 | 34 | 47.5 | 3.94 | 4.07 | 9.07 | 36.88 | 34 | 38 | 43.5 | 28 | 2 | 1.875 | 0.5 | 13 | 13.75 | 1206 | 100.1 | 103.4 | 230 | 937 | 863.6 | 965 | 1104.9 | 13 | 330 | 350
16.47 Series A | 300 | 36 | 50 | 4.07 | 4.32 | 9.44 | 39 | 36 | 40.25 | 46 | 32 | 2.125 | 2 | 0.5 | 13.5 | 14.25 | 1270 | 103.4 | 109.7 | 240 | 991 | 914.4 | 1022 | 1168.4 | 13 | 340 | 365
16.47 Series A | 300 | 38 | 46 | 4.19 | 4.19 | 7.06 | 39.12 | 38 | 40.5 | 43 | 32 | 1.625 | 1.5 | 0.5 | 12.5 | … | 1168 | 106.4 | 106.4 | 179 | 994 | 965.2 | 1029 | 1092.2 | 13 | 32 | …
16.47 Series A | 300 | 40 | 48.75 | 4.44 | 4.44 | 7.56 | 41.25 | 40 | 42.75 | 45.5 | 32 | 1.75 | 1.625 | 0.5 | 13.25 | … | 1238 | 112.8 | 112.8 | 192 | 1048 | 1016 | 1086 | 1155.7 | 13 | 340 | …
16.47 Series A | 300 | 42 | 50.75 | 4.63 | 4.63 | 7.82 | 43.25 | 42 | 44.75 | 47.5 | 32 | 1.75 | 1.625 | 0.5 | 13.75 | … | 1289 | 117.6 | 117.6 | 199 | 1099 | 1066.8 | 1137 | 1206.5 | 13 | 350 | …
16.47 Series A | 300 | 44 | 53.25 | 4.82 | 4.82 | 8.06 | 45.25 | 44 | 47 | 49.75 | 32 | 1.875 | 1.75 | 0.5 | 14.5 | … | 1353 | 122.4 | 122.4 | 205 | 1149 | 1117.6 | 1194 | 1263.6 | 13 | 365 | …
16.47 Series A | 300 | 46 | 55.75 | 5 | 5 | 8.44 | 47.38 | 46 | 49 | 52 | 28 | 2 | 1.875 | 0.5 | 15 | … | 1416 | 127 | 127 | 214 | 1203 | 1168.4 | 1245 | 1320.8 | 13 | 380 | …
16.47 Series A | 300 | 48 | 57.75 | 5.19 | 5.19 | 8.75 | 49.38 | 48 | 51.25 | 54 | 32 | 2 | 1.875 | 0.5 | 15.5 | … | 1467 | 131.8 | 131.8 | 222 | 1254 | 1219.2 | 1302 | 1371.6 | 13 | 390 | …
16.47 Series A | 300 | 50 | 60.25 | 5.44 | 5.44 | 9.07 | 51.38 | 50 | 53.5 | 56.25 | 32 | 2.125 | 2 | 0.5 | 16 | … | 1530 | 138.2 | 138.2 | 230 | 1305 | 1270 | 1359 | 1428.8 | 13 | 410 | …
16.47 Series A | 300 | 52 | 62.25 | 5.63 | 5.63 | 9.32 | 53.38 | 52 | 55.5 | 58.25 | 32 | 2.125 | 2 | 0.5 | 16.5 | … | 1581 | 143 | 143 | 237 | 1356 | 1320.8 | 1410 | 1479.6 | 13 | 420 | …
16.47 Series A | 300 | 54 | 65.25 | 5.94 | 5.94 | 9.88 | 55.5 | 54 | 57.75 | 61 | 28 | 2.375 | 2.25 | 0.5 | 17.5 | … | 1657 | 150.9 | 150.9 | 251 | 1410 | 1371.6 | 1467 | 1549.4 | 13 | 450 | …
16.47 Series A | 300 | 56 | 67.25 | 6 | 6 | 10.19 | 57.62 | 56 | 59.75 | 63 | 28 | 2.375 | 2.25 | 0.5 | 17.75 | … | 1708 | 152.4 | 152.4 | 259 | 1464 | 1422.4 | 1518 | 1600.2 | 13 | 450 | …
16.47 Series A | 300 | 58 | 69.25 | 6.19 | 6.19 | 10.44 | 59.62 | 58 | 62 | 65 | 32 | 2.375 | 2.25 | 0.5 | 18.25 | … | 1759 | 157.2 | 157.2 | 265 | 1514 | 1473.2 | 1575 | 1651 | 13 | 465 | …
16.47 Series A | 300 | 60 | 71.25 | 6.38 | 6.38 | 10.69 | 61.62 | 60 | 64 | 67 | 32 | 2.375 | 1.25 | 0.5 | 18.75 | … | 1810 | 160.1 | 160.1 | 272 | 1565 | 1524 | 1626 | 1701.8 | 13 | 475 | …
16.47 Series A | 150 | 26 | 34.25 | 2.63 | 2.63 | 4.69 | 26.62 | 26 | 29.5 | 31.75 | 24 | 1.375 | 1.25 | 0.38 | 8.75 | N/A | 870 | 66.8 | 66.8 | 119 | 676 | 660.4 | 749 | 806.4 | 10 | 225 | N/A
16.47 Series A | 150 | 28 | 36.5 | 2.75 | 2.75 | 4.88 | 28.62 | 28 | 31.5 | 34 | 28 | 1.375 | 1.25 | 0.44 | 9 | N/A | 927 | 69.8 | 69.8 | 124 | 727 | 711.2 | 800 | 863.6 | 11 | 230 | N/A
16.47 Series A | 150 | 30 | 38.75 | 2.88 | 2.88 | 5.32 | 30.75 | 30 | 33.75 | 36 | 28 | 1.375 | 1.25 | 0.44 | 9.25 | N/A | 984 | 73.2 | 73.2 | 135 | 781 | 762 | 857 | 914.4 | 11 | 235 | N/A
16.47 Series A | 150 | 32 | 41.75 | 3.13 | 3.13 | 5.63 | 32.75 | 32 | 36 | 38.5 | 28 | 1.625 | 1.5 | 0.44 | 10.5 | N/A | 1060 | 79.5 | 79.5 | 143 | 832 | 812.8 | 914 | 977.9 | 11 | 265 | N/A
16.47 Series A | 150 | 34 | 43.75 | 3.19 | 3.19 | 5.82 | 34.75 | 34 | 38 | 40.5 | 32 | 1.625 | 1.5 | 0.5 | 10.5 | N/A | 1111 | 81 | 81 | 148 | 883 | 863.6 | 965 | 1028.7 | 13 | 270 | N/A
16.47 Series A | 150 | 36 | 46 | 3.5 | 3.5 | 6.13 | 36.75 | 36 | 40.25 | 42.75 | 32 | 1.625 | 1.5 | 0.5 | 11.25 | N/A | 1168 | 88.9 | 88.9 | 156 | 933 | 914.4 | 1022 | 1085.8 | 13 | 285 | N/A
16.47 Series A | 150 | 38 | 48.75 | 3.38 | 3.38 | 6.13 | 39 | 38 | 42.25 | 45.25 | 32 | 1.625 | 1.5 | 0.5 | 11 | N/A | 1238 | 85.9 | 85.9 | 156 | 991 | 965.2 | 1073 | 1149.4 | 13 | 280 | N/A
16.47 Series A | 150 | 40 | 50.75 | 3.5 | 3.5 | 6.38 | 41 | 40 | 44.25 | 47.25 | 36 | 1.625 | 1.5 | 0.5 | 11.25 | N/A | 1289 | 88.9 | 88.9 | 162 | 1041 | 1016 | 1124 | 1200.2 | 13 | 285 | N/A
16.47 Series A | 150 | 42 | 53 | 3.75 | 3.75 | 6.69 | 43 | 42 | 47 | 49.5 | 36 | 1.625 | 1.5 | 0.5 | 11.75 | N/A | 1346 | 95.2 | 95.2 | 170 | 1092 | 1066.8 | 1194 | 1257.3 | 13 | 300 | N/A
16.47 Series A | 150 | 44 | 55.25 | 3.94 | 3.94 | 6.94 | 45 | 44 | 49 | 51.75 | 40 | 1.625 | 1.5 | 0.5 | 12 | N/A | 1403 | 100.1 | 100.1 | 176 | 1143 | 1117.6 | 1245 | 1314.4 | 13 | 305 | N/A
16.47 Series A | 150 | 46 | 57.25 | 4 | 4 | 7.25 | 47.12 | 46 | 51 | 53.75 | 40 | 1.625 | 1.5 | 0.5 | 12.25 | N/A | 1454 | 101.6 | 101.6 | 184 | 1197 | 1168.4 | 1295 | 1365.2 | 13 | 310 | N/A
16.47 Series A | 150 | 48 | 59.5 | 4.19 | 4.19 | 7.5 | 49.12 | 48 | 52.5 | 56 | 44 | 1.625 | 1.5 | 0.5 | 12.5 | N/A | 1511 | 106.4 | 106.4 | 191 | 1248 | 1219.2 | 1359 | 1422.4 | 13 | 320 | N/A
16.47 Series A | 150 | 50 | 67.75 | 4.32 | 4.32 | 7.94 | 51.25 | 50 | 55.5 | 58.25 | 44 | 1.875 | 1.75 | 0.5 | 13.5 | N/A | 1568 | 109.7 | 109.7 | 202 | 1302 | 1270 | 1410 | 1479.6 | 13 | 340 | N/A
16.47 Series A | 150 | 52 | 64 | 4.5 | 4.5 | 8.19 | 53.25 | 52 | 57.5 | 60.5 | 44 | 1.875 | 1.75 | 0.5 | 13.75 | N/A | 1626 | 114.3 | 114.3 | 208 | 1353 | 1320.8 | 1431 | 1536.7 | 13 | 350 | N/A
16.47 Series A | 150 | 54 | 66.25 | 4.69 | 4.69 | 8.44 | 55.25 | 54 | 59.5 | 62.75 | 44 | 1.875 | 1.75 | 0.5 | 14 | N/A | 1683 | 119.1 | 119.1 | 214 | 1403 | 1371.6 | 15111 | 1593.8 | 13 | 360 | N/A
16.47 Series A | 150 | 56 | 68.75 | 4.82 | 4.82 | 8.94 | 57.38 | 56 | 62 | 65 | 48 | 1.875 | 1.75 | 0.5 | 14.5 | N/A | 1746 | 122.4 | 122.4 | 227 | 1457 | 1422.4 | 1575 | 1651 | 13 | 365 | N/A
16.47 Series A | 150 | 58 | 71 | 5 | 5 | 9.19 | 59.38 | 58 | 64 | 67.25 | 48 | 1.875 | 1.75 | 0.5 | 14.75 | N/A | 1803 | 127 | 127 | 233 | 1508 | 1473.2 | 1626 | 1708.2 | 13 | 380 | N/A
16.47 Series A | 150 | 60 | 73 | 5.13 | 5.13 | 9.38 | 61.38 | 60 | 66 | 69.25 | 52 | 1.875 | 1.75 | 0.5 | 15 | N/A | 1854 | 130.3 | 130.3 | 238 | 1559 | 1524 | 1676 | 1759 | 13 | 380 | N/A
16.47 Series B | 75 | 26 | 30 | 1.25 | 1.25 | 2.25 | 26.62 | 26.06 | 27.75 | 28.5 | 36 | 0.75 | 0.625 | 0.31 | 4.5 | N/A | 760 | 31.8 | 31.8 | 57 | 676 | 661.9 | 705 | 723.9 | 8 | 115 | N/A
16.47 Series B | 75 | 28 | 32 | 1.25 | 1.25 | 2.38 | 28.62 | 28.06 | 29.75 | 30.5 | 40 | 0.75 | 0.625 | 0.31 | 4.5 | N/A | 813 | 31.8 | 31.8 | 60 | 727 | 712.7 | 756 | 774.7 | 8 | 115 | N/A
16.47 Series B | 75 | 30 | 34 | 1.25 | 1.25 | 2.5 | 30.62 | 30.06 | 31.75 | 32.5 | 44 | 0.75 | 0.625 | 0.31 | 4.75 | N/A | 864 | 31.8 | 31.8 | 64 | 778 | 763.5 | 806 | 825.5 | 8 | 115 | N/A
16.47 Series B | 75 | 32 | 36 | 1.32 | 1.38 | 2.69 | 32.62 | 32.06 | 33.75 | 34.5 | 48 | 0.75 | 0.625 | 0.31 | 4.75 | N/A | 914 | 33.5 | 35.1 | 68 | 829 | 814.3 | 857 | 876.3 | 8 | 120 | N/A
16.47 Series B | 75 | 34 | 38 | 1.32 | 1.44 | 2.82 | 34.62 | 34.06 | 35.75 | 36.5 | 52 | 0.75 | 0.625 | 0.31 | 4.75 | N/A | 965 | 33.5 | 36.6 | 72 | 879 | 865.1 | 908 | 927.1 | 8 | 120 | N/A
16.47 Series B | 75 | 36 | 40.69 | 1.38 | 1.61 | 3.32 | 36.81 | 36.06 | 38 | 39.06 | 40 | 0.875 | 0.75 | 0.38 | 5 | N/A | 1034 | 35.1 | 40.9 | 84 | 935 | 915.9 | 965 | 992.1 | 10 | 130 | N/A
16.47 Series B | 75 | 38 | 42.69 | 1.44 | 1.69 | 3.44 | 38.81 | 38.06 | 40 | 41.06 | 40 | 0.875 | 0.75 | 0.38 | 5.25 | N/A | 1084 | 36.6 | 42.9 | 87 | 986 | 966.7 | 1016 | 1042.9 | 10 | 130 | N/A
16.47 Series B | 75 | 40 | 44.69 | 1.44 | 1.69 | 3.57 | 40.81 | 40.06 | 42 | 43.06 | 44 | 0.875 | 0.75 | 0.38 | 5.25 | N/A | 1135 | 36.6 | 42.9 | 91 | 1037 | 1017.5 | 1067 | 1093.7 | 110 | 130 | N/A
16.47 Series B | 75 | 42 | 46.69 | 1.5 | 1.82 | 3.69 | 42.81 | 42.06 | 44 | 45.06 | 48 | 0.875 | 0.75 | 0.38 | 5.25 | N/A | 1186 | 38.1 | 46.2 | 94 | 1087 | 1068.3 | 1118 | 1144.5 | 10 | 135 | N/A
16.47 Series B | 75 | 44 | 49.25 | 1.63 | 1.88 | 4.07 | 44.88 | 44.06 | 46.25 | 47.38 | 36 | 1 | 0.875 | 0.38 | 5.75 | N/A | 1251 | 41.4 | 47.8 | 103 | 1140 | 1119.1 | 1175 | 1203.5 | 10 | 150 | N/A
16.47 Series B | 75 | 46 | 51.25 | 1.69 | 1.94 | 4.19 | 46.88 | 46.06 | 48.25 | 49.38 | 40 | 1 | 0.875 | 0.38 | 6 | N/A | 1302 | 42.9 | 49.3 | 106 | 1191 | 1169.9 | 1226 | 1254.3 | 10 | 150 | N/A
16.47 Series B | 75 | 48 | 53.25 | 1.75 | 2.07 | 4.32 | 48.88 | 48.06 | 50.25 | 51.38 | 44 | 1 | 0.875 | 0.38 | 6 | N/A | 1353 | 44.6 | 52.6 | 110 | 1242 | 1220.7 | 1276 | 1305.1 | 10 | 160 | N/A
16.47 Series B | 75 | 50 | 55.25 | 1.82 | 2.13 | 4.5 | 50.94 | 50.06 | 52.25 | 53.38 | 44 | 1 | 0.875 | 0.38 | 6.25 | N/A | 1403 | 46.2 | 54.1 | 114 | 1294 | 1271.5 | 1327 | 1355.9 | 10 | 160 | N/A
16.47 Series B | 75 | 52 | 57.38 | 1.82 | 2.19 | 4.69 | 52.94 | 52.06 | 54.25 | 55.5 | 48 | 1 | 0.875 | 0.38 | 6.25 | N/A | 1457 | 46.2 | 55.6 | 119 | 1345 | 1322.3 | 1378 | 1409.7 | 10 | 16 | N/A
16.47 Series B | 75 | 54 | 59.38 | 1.88 | 2.32 | 4.88 | 55 | 54.06 | 56.25 | 57.5 | 48 | 1 | 0.875 | 0.38 | 6.25 | N/A | 1508 | 47.8 | 58.9 | 124 | 1397 | 1373.1 | 1429 | 1460.5 | 10 | 160 | N/A
16.47 Series B | 75 | 56 | 62 | 1.94 | 2.38 | 5.25 | 57.12 | 56.06 | 58.5 | 59.88 | 40 | 1.125 | 1 | 0.44 | 6.75 | N/A | 1575 | 49.3 | 60.5 | 133 | 1451 | 1423.9 | 1486 | 1521 | 11 | 170 | N/A
16.47 Series B | 75 | 58 | 64 | 2 | 2.44 | 5.38 | 59.12 | 58.06 | 60.5 | 61.88 | 44 | 1.125 | 1 | 0.44 | 7 | N/A | 1626 | 50.8 | 62 | 137 | 1502 | 1474.7 | 1537 | 1571.8 | 11 | 180 | N/A
16.47 Series B | 75 | 60 | 66 | 2.13 | 2.57 | 5.63 | 61.12 | 60.06 | 62.5 | 63.88 | 44 | 1.125 | 1 | 0.44 | 7.25 | N/A | 1676 | 54.1 | 65.3 | 143 | 1553 | 1525.5 | 1588 | 1622.6 | 11 | 185 | N/A
16.47 Series B | 150 | 26 | 30.94 | 1.57 | 1.69 | 3.44 | 26.94 | 26.06 | 28 | 29.31 | 36 | 0.875 | 0.75 | 0.38 | 5.5 | N/A | 786 | 39.9 | 42.9 | 87 | 683 | 661.9 | 711 | 744.5 | 10 | 140 | N/A
16.47 Series B | 150 | 28 | 32.94 | 1.69 | 1.82 | 3.69 | 28.94 | 28.06 | 30 | 31.31 | 40 | 0.875 | 0.75 | 0.38 | 5.75 | N/A | 837 | 42.9 | 46.2 | 94 | 735 | 712.7 | 762 | 795.3 | 10 | 145 | N/A
16.47 Series B | 150 | 30 | 34.94 | 1.69 | 1.94 | 3.88 | 31 | 30.06 | 32 | 33.31 | 44 | 0.875 | 0.75 | 0.38 | 5.75 | N/A | 887 | 42.9 | 49.3 | 98 | 787 | 763.5 | 813 | 846.1 | 10 | 145 | N/A
16.47 Series B | 150 | 32 | 37.06 | 1.75 | 2.07 | 4.19 | 33.06 | 32.06 | 34 | 35.44 | 48 | 0.875 | 0.75 | 0.38 | 5.75 | N/A | 941 | 44.4 | 52.6 | 106 | 840 | 814.3 | 864 | 900.2 | 10 | 150 | N/A
16.47 Series B | 150 | 34 | 39.56 | 1.88 | 2.19 | 4.28 | 35.12 | 34.06 | 36.25 | 37.69 | 40 | 1 | 0.875 | 0.38 | 6.25 | N/A | 1005 | 47.8 | 55.6 | 109 | 892 | 865.1 | 921 | 957.3 | 10 | 165 | N/A
16.47 Series B | 150 | 36 | 41.62 | 2 | 2.25 | 4.57 | 37.19 | 36.06 | 38.25 | 39.75 | 44 | 1 | 0.875 | 0.38 | 6.5 | N/A | 1057 | 50.8 | 57.2 | 116 | 945 | 915.9 | 972 | 1009.6 | 10 | 165 | N/A
16.47 Series B | 150 | 38 | 44.25 | 2.07 | 2.44 | 4.82 | 39.25 | 38.12 | 40.25 | 42.12 | 40 | 1.125 | 1 | 0.38 | 7.25 | N/A | 1124 | 52.6 | 62 | 122 | 997 | 968.2 | 1022 | 1069.8 | 10 | 185 | N/A
16.47 Series B | 150 | 40 | 46.25 | 2.13 | 2.57 | 5 | 41.31 | 40.12 | 42.5 | 44.12 | 44 | 1.125 | 1 | 0.38 | 7.25 | N/A | 1175 | 54.1 | 65.3 | 127 | 1049 | 1019 | 1080 | 1120.6 | 10 | 185 | N/A
16.47 Series B | 150 | 42 | 48.25 | 2.25 | 2.63 | 5.19 | 43.38 | 42.12 | 44.5 | 46.12 | 48 | 1.125 | 1 | 0.44 | 7.5 | N/A | 1226 | 57.2 | 66.8 | 132 | 1102 | 1069.8 | 1130 | 1171.4 | 11 | 190 | N/A
16.47 Series B | 150 | 44 | 50.25 | 2.32 | 2.75 | 5.32 | 445.38 | 44.12 | 46.5 | 48.12 | 52 | 1.125 | 1 | 0.44 | 7.75 | N/A | 1276 | 58.9 | 69.8 | 135 | 1153 | 1120.6 | 1181 | 1222.2 | 11 | 195 | N/A
16.47 Series B | 150 | 46 | 52.81 | 2.38 | 2.88 | 5.63 | 47.44 | 46.12 | 48.62 | 50.56 | 40 | 1.25 | 1.125 | 0.44 | 8 | N/A | 1341 | 60.5 | 73.2 | 143 | 1205 | 1171.4 | 1235 | 1284.2 | 11 | 205 | N/A
16.47 Series B | 150 | 48 | 54.81 | 2.5 | 3 | 5.82 | 49.5 | 48.12 | 50.75 | 52.56 | 44 | 1.25 | 1.125 | 0.44 | 8.25 | N/A | 1392 | 63.5 | 76.2 | 148 | 1257 | 1222.2 | 1289 | 1335 | 11 | 210 | N/A
16.47 Series B | 150 | 50 | 56.81 | 2.63 | 3.13 | 6 | 51.5 | 50.12 | 52.75 | 54.56 | 48 | 1.25 | 1.125 | 0.44 | 8.5 | N/A | 1443 | 66.8 | 79.5 | 152 | 1308 | 1273 | 1340 | 1385.8 | 11 | 215 | N/A
16.47 Series B | 150 | 52 | 58.81 | 2.69 | 3.25 | 6.13 | 53.56 | 52.12 | 54.75 | 56.56 | 52 | 1.25 | 1.125 | 0.44 | 8.75 | N/A | 1494 | 68.3 | 82.6 | 156 | 1360 | 1323.8 | 1391 | 1436.6 | 11 | 220 | N/A
16.47 Series B | 150 | 54 | 61 | 2.75 | 3.38 | 6.32 | 55.62 | 54.12 | 56.75 | 58.75 | 56 | 1.25 | 1.125 | 0.44 | 8.75 | N/A | 1549 | 69.8 | 85.9 | 161 | 1413 | 1374.6 | 1441 | 1492.2 | 11 | 225 | N/A
16.47 Series B | 150 | 56 | 63 | 2.82 | 3.5 | 6.5 | 57.62 | 56.12 | 58.75 | 60.75 | 60 | 1.25 | 1.125 | 0.56 | 9 | N/A | 1600 | 71.6 | 88.9 | 165 | 1465 | 1425.4 | 1492 | 1543 | 14 | 225 | N/A
16.47 Series B | 150 | 58 | 65.94 | 2.88 | 3.62 | 6.82 | 59.69 | 58.12 | 60.75 | 63.44 | 48 | 1.375 | 1.25 | 0.56 | 9.25 | N/A | 1675 | 73.2 | 91.9 | 173 | 1516 | 1476.2 | 1543 | 1611.4 | 14 | 235 | N/A
16.47 Series B | 150 | 60 | 67.94 | 2.94 | 3.75 | 7 | 61.81 | 60.12 | 63 | 65.44 | 52 | 1.375 | 1.25 | 0.56 | 9.5 | N/A | 1726 | 74.7 | 95.2 | 178 | 1570 | 1527 | 1600 | 1662.2 | 14 | 240 | N/A
16.47 Series B | 300 | 26 | 34.12 | 3.44 | 3.44 | 5.63 | 27.62 | 26.19 | 29 | 31.62 | 32 | 1.375 | 1.25 | 0.56 | 10.5 | N/A | 867 | 87.4 | 87.4 | 143 | 702 | 665.2 | 737 | 803.1 | 14 | 270 | N/A
16.47 Series B | 300 | 28 | 36.25 | 3.44 | 3.44 | 5.81 | 29.75 | 28.19 | 31 | 33.75 | 36 | 1.375 | 1.25 | 0.56 | 10.5 | N/A | 921 | 87.4 | 87.4 | 148 | 756 | 716 | 787 | 857.2 | 14 | 270 | N/A
16.47 Series B | 300 | 30 | 39 | 3.63 | 3.63 | 6.16 | 32 | 30.25 | 33.25 | 36.25 | 36 | 1.5 | 1.375 | 0.56 | 11.25 | N/A | 991 | 92.2 | 92.2 | 156 | 813 | 768.4 | 845 | 920.8 | 14 | 285 | N/A
16.47 Series B | 300 | 32 | 41.5 | 4 | 4 | 6.56 | 34 | 32.25 | 35.5 | 38.5 | 32 | 1.625 | 1.5 | 0.62 | 12.25 | N/A | 1054 | 101.6 | 101.6 | 167 | 864 | 819.2 | 902 | 977.9 | 16 | 310 | N/A
16.47 Series B | 300 | 34 | 43.62 | 4 | 4 | 6.75 | 36.12 | 34.25 | 37.5 | 40.62 | 36 | 1.625 | 1.5 | 0.62 | 12.25 | N/A | 1108 | 101.6 | 101.6 | 171 | 917 | 870 | 952 | 1031.7 | 16 | 310 | N/A
16.47 Series B | 300 | 36 | 46.12 | 4 | 4 | 7.06 | 38 | 36.25 | 39.75 | 42.88 | 32 | 1.75 | 1.625 | 0.62 | 12.5 | N/A | 1171 | 101.6 | 101.6 | 179 | 965 | 920.8 | 1010 | 1089.2 | 16 | 320 | N/A
16.47 Series B | 300 | 38 | 48.12 | 4.31 | 4.31 | 7.5 | 40 | 38.25 | 41.75 | 44.88 | 36 | 1.75 | 1.625 | 0.62 | 13 | N/A | 1222 | 109.5 | 109.5 | 190 | 1016 | 971.6 | 1060 | 1140 | 16 | 335 | N/A
16.47 Series B | 300 | 40 | 50.12 | 4.5 | 4.5 | 7.75 | 42 | 40.25 | 43.88 | 46.88 | 40 | 1.75 | 1.625 | 0.62 | 13.5 | N/A | 1273 | 114.3 | 114.3 | 197 | 1067 | 1022.4 | 1115 | 1190.8 | 16 | 345 | N/A
16.47 Series B | 300 | 42 | 52.5 | 4.63 | 4.63 | 8 | 44 | 42.31 | 46 | 49 | 36 | 1.875 | 1.75 | 0.62 | 14 | N/A | 1334 | 117.6 | 117.6 | 203 | 1118 | 1074.7 | 1168 | 1244.6 | 16 | 355 | N/A
16.47 Series B | 300 | 44 | 54.5 | 4.94 | 4.94 | 8.38 | 46.19 | 44.31 | 48 | 51 | 40 | 1.875 | 1.75 | 0.62 | 14.5 | N/A | 1384 | 125.5 | 125.5 | 213 | 1173 | 1125.5 | 1219 | 1295.4 | 16 | 370 | N/A
16.47 Series B | 300 | 46 | 57.5 | 5 | 5.06 | 8.69 | 48.38 | 46.31 | 50 | 53.75 | 36 | 2 | 1.875 | 0.62 | 15 | N/A | 1460 | 127 | 128.5 | 221 | 1229 | 1176.3 | 1270 | 1365.2 | 16 | 380 | N/A
16.47 Series B | 300 | 48 | 59.5 | 5 | 5.25 | 8.75 | 50.31 | 48.31 | 52.25 | 55.75 | 40 | 2 | 1.875 | 0.62 | 15 | N/A | 1511 | 127 | 133.4 | 222 | 1278 | 1227.1 | 1327 | 1416 | 16 | 380 | N/A
16.47 Series B | 300 | 50 | 61.5 | 5.38 | 5.44 | 9.19 | 52.38 | 50.31 | 54.25 | 57.75 | 44 | 2 | 1.875 | 0.62 | 15.75 | N/A | 1562 | 136.7 | 138.2 | 233 | 1330 | 1277.9 | 1378 | 1466.8 | 16 | 400 | N/A
16.47 Series B | 300 | 52 | 63.5 | 5.56 | 5.61 | 9.5 | 54.44 | 52.31 | 56.25 | 59.75 | 48 | 2 | 1.875 | 0.62 | 16 | N/A | 1613 | 141.2 | 142.5 | 241 | 1383 | 1328.7 | 1429 | 1517.6 | 16 | 410 | N/A
16.47 Series B | 300 | 54 | 65.88 | 5.32 | 5.81 | 9.38 | 56.5 | 54.31 | 58.25 | 62.12 | 48 | 2 | 1.875 | 0.62 | 15.75 | N/A | 1673 | 135.1 | 147.6 | 238 | 1435 | 1379.5 | 1480 | 1577.8 | 16 | 400 | N/A
16.47 Series B | 300 | 56 | 69.5 | 6 | 6.12 | 10.5 | 58.81 | 56.31 | 60.5 | 65 | 36 | 2.375 | 2.25 | 0.69 | 17.75 | N/A | 1765 | 152.4 | 155.4 | 267 | 1494 | 14300.3 | 1537 | 1651 | 17 | 450 | N/A
16.47 Series B | 300 | 58 | 71.94 | 6 | 6.31 | 10.75 | 60.94 | 58.31 | 62.75 | 67.44 | 40 | 2.375 | 2.25 | 0.69 | 17.75 | N/A | 1827 | 152.4 | 160.3 | 273 | 1548 | 1481.1 | 1594 | 1713 | 17 | 450 | N/A
16.47 Series B | 300 | 60 | 73.94 | 5.88 | 6.5 | 10.63 | 62.94 | 60.31 | 65 | 69.44 | 40 | 2.375 | 2.25 | 0.69 | 17.5 | N/A | 1878 | 149.4 | 165.1 | 270 | 1599 | 1531.9 | 1651 | 1763.8 | 17 | 450 | N/A
ASME | Flange Class | Nominal Pipe Size (NPS) | Diameter Flange (O) | Min Thickness Flange (Q) | Hub- Min Diameter (X) | Hub- Min Length (Y) | Hub- Min Thread Length (T) | Blind Flange- Diameter of Port (I) | Blind Flange- Wall Thickness (V) | Raised Face Diameter (W) | Bolt Hole- Diameter Bolt Circle | Bolt Hole- Diameter Bolt Holes | Bolting- # of Bolts | Bolting- Bolt Diameter | Bolting- Length of Bolts | Bolting- Length of Stud Bolts | Diameter Flange (O) | Min Thickness Flange (Q) | Hub- Min Diameter (X) | Hub- Min Length (Y) | Hub- Min Thread Length (T) | Blind Flange- Diameter of Port (I) | Blind Flange- Wall Thickness (V) | Raised Face Diameter (W) | Bolt Hole- Diameter Bolt Circle | Bolting- Length of Bolts | Bolting- Length of Stud Bolts
16.1 | 25 | 4 | 9 | 0.75 | 5.31 | 1.31 | N/A | N/A | N/A | N/A | 7.5 | 0.75 | 8 | 0.625 | 2.5 | N/A | 230 | 19 | 135 | 33 | N/A | N/A | N/A | N/A | 191 | 64 | N/A
16.1 | 25 | 5 | 10 | 0.75 | 6.44 | 1.44 | N/A | N/A | N/A | N/A | 8.5 | 0.75 | 8 | 0.625 | 2.5 | N/A | 255 | 19 | 164 | 37 | N/A | N/A | N/A | N/A | 216 | 64 | N/A
16.1 | 25 | 6 | 11 | 0.75 | 7.56 | 1.56 | N/A | N/A | N/A | N/A | 9.5 | 0.75 | 8 | 0.625 | 2.5 | N/A | 280 | 19 | 192 | 40 | N/A | N/A | N/A | N/A | 241 | 64 | N/A
16.1 | 25 | 8 | 13.5 | 0.75 | 9.69 | 1.75 | N/A | N/A | N/A | N/A | 11.75 | 0.75 | 8 | 0.625 | 2.5 | N/A | 345 | 19 | 246 | 45 | N/A | N/A | N/A | N/A | 299 | 64 | N/A
16.1 | 25 | 10 | 16 | 0.88 | 11.94 | 1.94 | N/A | N/A | N/A | N/A | 14.25 | 0.75 | 12 | 0.625 | 3 | N/A | 405 | 22.2 | 303 | 49 | N/A | N/A | N/A | N/A | 368 | 70 | N/A
16.1 | 25 | 12 | 19 | 1 | 14.06 | 2.19 | N/A | N/A | N/A | N/A | 17 | 0.75 | 12 | 0.625 | 3 | N/A | 485 | 25.4 | 357 | 56 | N/A | N/A | N/A | N/A | 432 | 76 | N/A
16.1 | 25 | 14 | 21 | 1.12 | 15.37 | 2.25 | N/A | N/A | N/A | N/A | 18.75 | 0.875 | 12 | 0.75 | 3.5 | N/A | 535 | 28.6 | 391 | 57 | N/A | N/A | N/A | N/A | 476 | 89 | N/A
16.1 | 25 | 16 | 23.5 | 1.12 | 17.5 | 2.5 | N/A | N/A | N/A | N/A | 21.25 | 0.875 | 16 | 0.75 | 3.5 | N/A | 595 | 28.6 | 445 | 64 | N/A | N/A | N/A | N/A | 540 | 89 | N/A
16.1 | 25 | 18 | 25 | 1.25 | 19.62 | 2.69 | N/A | N/A | N/A | N/A | 22.75 | 0.875 | 16 | 0.75 | 4 | N/A | 635 | 31.8 | 498 | 68 | N/A | N/A | N/A | N/A | 578 | 95 | N/A
16.1 | 25 | 20 | 27.5 | 1.25 | 21.75 | 2.88 | N/A | N/A | N/A | N/A | 25 | 0.875 | 20 | 0.75 | 4 | N/A | 700 | 31.8 | 552 | 78 | N/A | N/A | N/A | N/A | 635 | 95 | N/A
16.1 | 25 | 24 | 32 | 1.38 | 26 | 3.25 | N/A | N/A | N/A | N/A | 29.5 | 0.875 | 20 | 0.75 | 4 | N/A | 815 | 34.9 | 560 | 83 | N/A | N/A | N/A | N/A | 749 | 102 | N/A
16.1 | 25 | 30 | 38.75 | 1.5 | … | … | N/A | N/A | N/A | N/A | 36 | 1 | 28 | 0.875 | 4.5 | N/A | 985 | 38.1 | … | … | N/A | N/A | N/A | N/A | 914 | 114 | N/A
16.1 | 25 | 36 | 46 | 1.62 | … | … | N/A | N/A | N/A | N/A | 42.75 | 1 | 32 | 0.875 | 5 | N/A | 1170 | 41.3 | … | … | N/A | N/A | N/A | N/A | 1085 | 121 | N/A
16.1 | 25 | 42 | 53 | 1.75 | … | … | N/A | N/A | N/A | N/A | 49.5 | 1.125 | 36 | 1 | 5.5 | N/A | 1345 | 44.5 | … | … | N/A | N/A | N/A | N/A | 1257 | 133 | N/A
16.1 | 25 | 48 | 59.5 | 2 | … | … | N/A | N/A | N/A | N/A | 56 | 1.125 | 44 | 1 | 6 | N/A | 1510 | 50.8 | … | … | N/A | N/A | N/A | N/A | 1422 | 146 | N/A
16.1 | 25 | 54 | 66.25 | 2.25 | … | … | N/A | N/A | N/A | N/A | 62.75 | 1.125 | 44 | 1 | 6.5 | N/A | 1685 | 57.2 | … | … | N/A | N/A | N/A | N/A | 1594 | 159 | N/A
16.1 | 25 | 60 | 73 | 2.25 | … | … | N/A | N/A | N/A | N/A | 69.25 | 1.25 | 52 | 1.125 | 6.5 | N/A | 1855 | 57.2 | … | … | N/A | N/A | N/A | N/A | 1759 | 159 | N/A
16.1 | 25 | 72 | 86.5 | 2.5 | … | … | N/A | N/A | N/A | N/A | 82.5 | 1.25 | 60 | 1.125 | 7 | N/A | 2195 | 63.5 | … | … | N/A | N/A | N/A | N/A | 2095 | 172 | N/A
16.1 | 25 | 84 | 99.75 | 2.75 | … | … | N/A | N/A | N/A | N/A | 95.5 | 1.375 | 64 | 1.25 | 7.5 | N/A | 2535 | 69.9 | … | … | N/A | N/A | N/A | N/A | 2425 | 191 | N/A
16.1 | 25 | 96 | 113.25 | 3 | … | … | N/A | N/A | N/A | N/A | 108.5 | 1.375 | 68 | 1.25 | 8 | N/A | 2875 | 76.2 | … | … | N/A | N/A | N/A | N/A | 2756 | 203 | N/A
16.1 | 125 | 1 | 4.25 | 0.44 | 1.94 | 0.69 | N/A | 1 | 0.38 | N/A | 3.12 | 0.625 | 4 | 0.5 | 2 | … | 110 | 11.1 | 49 | 18 | N/A | 25 | 9.6 | N/A | 79 | 45 | …
16.1 | 125 | 1.25 | 4.62 | 0.5 | 2.31 | 0.81 | N/A | 1.25 | 0.44 | N/A | 3.5 | 0.625 | 4 | 0.5 | 2 | … | 115 | 12.7 | 59 | 21 | N/A | 32 | 11.1 | N/A | 89 | 51 | …
16.1 | 125 | 1.5 | 5 | 0.56 | 2.56 | 0.88 | N/A | 1.5 | 0.5 | N/A | 3.88 | 0.625 | 4 | 0.5 | 2 | … | 125 | 14.3 | 65 | 22 | N/A | 38 | 12.7 | N/A | 98 | 51 | …
16.1 | 125 | 2 | 6 | 0.62 | 3.06 | 1 | N/A | 2 | 0.56 | N/A | 4.75 | 0.75 | 4 | 0.625 | 2.5 | … | 150 | 15.9 | 78 | 25 | N/A | 51 | 14.3 | N/A | 121 | 57 | …
16.1 | 125 | 2.5 | 7 | 0.69 | 3.56 | 1.12 | N/A | 2.5 | 0.63 | N/A | 5.5 | 0.75 | 4 | 0.625 | 2.5 | … | 180 | 17.5 | 91 | 29 | N/A | 64 | 15.9 | N/A | 140 | 64 | …
16.1 | 125 | 3 | 7.5 | 0.75 | 4.25 | 1.19 | N/A | 3 | 0.69 | N/A | 6 | 0.75 | 4 | 0.625 | 2.5 | … | 190 | 19 | 108 | 30 | N/A | 76 | 17.5 | N/A | 152 | 64 | …
16.1 | 125 | 3.5 | 8.5 | 0.81 | 4.81 | 1.25 | N/A | 3.5 | 0.75 | N/A | 7 | 0.75 | 8 | 0.625 | 3 | … | 215 | 20.6 | 122 | 32 | N/A | 89 | 19 | N/A | 178 | 70 | …
16.1 | 125 | 4 | 9 | 0.94 | 5.31 | 1.31 | N/A | 4 | 0.88 | N/A | 7.5 | 0.75 | 8 | 0.625 | 3 | … | 230 | 23.8 | 135 | 33 | N/A | 102 | 22.2 | N/A | 191 | 76 | …
16.1 | 125 | 5 | 10 | 0.94 | 6.44 | 1.44 | N/A | 5 | 0.88 | N/A | 8.5 | 0.875 | 8 | 0.75 | 3 | … | 255 | 23.8 | 164 | 37 | N/A | 125 | 22.2 | N/A | 216 | 76 | …
16.1 | 125 | 6 | 11 | 1 | 7.56 | 1.56 | N/A | 6 | 0.94 | N/A | 9.5 | 0.875 | 8 | 0.75 | 3.5 | … | 280 | 25.4 | 192 | 40 | N/A | 152 | 23.8 | N/A | 241 | 83 | …
16.1 | 125 | 8 | 13.5 | 1.12 | 9.69 | 1.75 | N/A | 8 | 1.06 | N/A | 11.75 | 0.875 | 8 | 0.75 | 3.5 | … | 345 | 28.6 | 246 | 45 | N/A | 203 | 27 | N/A | 299 | 89 | …
16.1 | 125 | 10 | 16 | 1.19 | 11.94 | 1.94 | N/A | 10 | 1.12 | N/A | 14.25 | 1 | 12 | 0.875 | 4 | … | 405 | 30.2 | 303 | 49 | N/A | 254 | 28.6 | N/A | 362 | 95 | …
16.1 | 125 | 12 | 19 | 1.25 | 14.06 | 2.19 | N/A | 12 | 0.81 | N/A | 17 | 1 | 12 | 0.875 | 4 | … | 485 | 31.8 | 357 | 56 | N/A | 305 | 20.6 | N/A | 432 | 95 | …
16.1 | 125 | 14 | 14 | 1.38 | 15.38 | 2.25 | N/A | 14 | 0.88 | N/A | 18.75 | 1.125 | 12 | 1 | 4.5 | … | 535 | 35.1 | 391 | 57 | N/A | 356 | 22.2 | N/A | 476 | 108 | …
16.1 | 125 | 16 | 23.5 | 1.44 | 17.5 | 2.5 | N/A | 16 | 1 | N/A | 21.25 | 1.125 | 16 | 1 | 4.5 | … | 595 | 36.5 | 445 | 64 | N/A | 406 | 25.4 | N/A | 540 | 114 | …
16.1 | 125 | 18 | 25 | 1.56 | 19.62 | 2.69 | N/A | 18 | 1.06 | N/A | 22.75 | 1.25 | 16 | 1.125 | 5 | … | 635 | 39.7 | 499 | 68 | N/A | 457 | 27 | N/A | 578 | 121 | …
16.1 | 125 | 20 | 27.5 | 1.69 | 21.75 | 2.88 | N/A | 20 | 1.12 | N/A | 25 | 1.25 | 20 | 1.125 | 5 | … | 700 | 42.9 | 553 | 73 | N/A | 508 | 28.6 | N/A | 635 | 127 | …
16.1 | 125 | 24 | 32 | 1.88 | 26 | 3.25 | N/A | 24 | 1.25 | N/A | 29.5 | 1.375 | 20 | 1.25 | 5.5 | … | 815 | 47.6 | 660 | 83 | N/A | 610 | 31.8 | N/A | 749 | 140 | …
16.1 | 125 | 30 | 38.75 | 2.12 | … | … | N/A | 30 | 1.44 | N/A | 36 | 1.375 | 28 | 1.25 | 6.5 | … | 985 | 54 | … | … | N/A | 762 | 36.6 | N/A | 914 | 159 | …
16.1 | 125 | 36 | 46 | 2.38 | … | … | N/A | 36 | 1.62 | N/A | 42.75 | 1.625 | 32 | 1.5 | 7 | 9 | 1170 | 60.3 | … | … | N/A | 914 | 41.3 | N/A | 1086 | 178 | 222
16.1 | 125 | 42 | 53 | 2.62 | … | … | N/A | 42 | 1.81 | N/A | 49.5 | 1.625 | 36 | 1.5 | 7.5 | 9.5 | 1345 | 66.7 | … | … | N/A | 1066 | 46 | N/A | 1257 | 191 | 235
16.1 | 125 | 48 | 59.5 | 2.75 | … | … | N/A | 48 | 2 | N/A | 56 | 1.625 | 44 | 1.5 | 8 | 9.5 | 1510 | 69.9 | … | … | N/A | 1219 | 50.8 | N/A | 1422 | 197 | 242
16.1 | 125 | 54 (9) | 66.25 | 3 | … | … | N/A | … | … | N/A | 62.75 | 2 | 44 | 1.75 | 8.5 | 10.5 | 1685 | 76.2 | … | … | N/A | … | … | N/A | 1594 | 216 | 267
16.1 | 125 | 60 (9) | 73 | 3.12 | … | … | N/A | … | … | N/A | 69.25 | 2 | 52 | 1.75 | 9 | 11 | 1855 | 79.4 | … | … | N/A | … | … | N/A | 1759 | 222 | 273
16.1 | 125 | 66 (9) | 80 | 3.38 | … | … | N/A | … | … | N/A | 76 | 2 | 52 | 1.75 | 9.5 | 11.5 | 2032 | 85.7 | … | … | N/A | … | … | N/A | 1930 | 241 | 292
16.1 | 125 | 72 (9) | 86.5 | 3.5 | … | … | N/A | … | … | N/A | 82.5 | 2 | 60 | 1.75 | 9.5 | 11.5 | 2195 | 88.9 | … | … | N/A | … | … | N/A | 2096 | 241 | 292
16.1 | 125 | 78 (9) | 93 | 3.75 | … | … | N/A | … | … | N/A | 89 | 2.25 | 64 | 2 | 10.5 | 12.5 | 2365 | 95.3 | … | … | N/A | … | … | N/A | 2261 | 267 | 318
16.1 | 125 | 84 (9) | 99.75 | 3.88 | … | … | N/A | … | … | N/A | 95.5 | 2.25 | 64 | 2 | 10.5 | 13 | 2535 | 98.4 | … | … | N/A | … | … | N/A | 2426 | 267 | 324
16.1 | 125 | 90 (9) | 106.5 | 4.12 | … | … | N/A | … | … | N/A | 102 | 2.5 | 68 | 2.25 | 11.5 | 14 | 2720 | 104.6 | … | … | N/A | … | … | N/A | 2591 | 292 | 357
16.1 | 125 | 96 (9) | 113.25 | 4.25 | … | … | N/A | … | … | N/A | 108.5 | 2.5 | 68 | 2.25 | 11.5 | 14 | 2875 | 108 | … | … | N/A | … | … | N/A | 2756 | 292 | 356
16.1 | 250 | 1 | 4.88 | 0.69 | 2.06 | 0.88 | 0.68 | 1 | … | 2.69 | 3.5 | 0.75 | 4 | 0.62 | 2.5 | … | 125 | 17.5 | 52 | 22 | 18 | 25 | … | 68 | 89 | 64 | …
16.1 | 250 | 1.25 | 5.25 | 0.75 | 2.5 | 1 | 0.81 | 1.25 | … | 3.06 | 3.88 | 0.75 | 4 | 0.62 | 2.5 | … | 135 | 19 | 64 | 25 | 19 | 32 | … | 78 | 98 | 64 | …
16.1 | 250 | 1.5 | 6.12 | 0.81 | 2.75 | 1.12 | 0.87 | 1.5 | … | 3.56 | 4.5 | 0.875 | 4 | 0.75 | 3 | … | 155 | 20.6 | 70 | 29 | 22 | 38 | … | 91 | 114 | 70 | …
16.1 | 250 | 2 | 6.5 | 0.88 | 3.31 | 1.25 | 1 | 2 | .. | 4.19 | 5 | 0.75 | 8 | 0.62 | 3 | … | 165 | 22.2 | 84 | 32 | 25 | 51 | … | 106 | 127 | 70 | …
16.1 | 250 | 2.5 | 7.5 | 1 | 3.94 | 1.43 | 1.13 | 2.5 | … | 4.94 | 5.88 | 0.875 | 8 | 0.75 | 3.5 | … | 190 | 25.4 | 100 | 37 | 29 | 64 | … | 125 | 149 | 83 | …
16.1 | 250 | 3 | 8.25 | 1.12 | 4.62 | 1.56 | 1.19 | 3 | … | 5.69 | 6.62 | 0.875 | 8 | 0.75 | 3.5 | … | 210 | 28.6 | 118 | 40 | 31 | 76 | … | 144 | 168 | 89 | …
16.1 | 250 | 3.5 | 9 | 1.19 | 5.25 | 1.62 | 1.25 | 3.5 | .. | 6.31 | 7.25 | 0.875 | 8 | 0.75 | 3.5 | … | 230 | 30.2 | 133 | 41 | 32 | 89 | … | 160 | 184 | 89 | …
16.1 | 250 | 4 | 10 | 1.25 | 5.75 | 1.75 | 1.31 | 4 | … | 6.94 | 7.88 | 0.875 | 8 | 0.75 | 4 | … | 255 | 31.8 | 146 | 44 | 33 | 102 | … | 176 | 200 | 95 | …
16.1 | 250 | 5 | 11 | 1.38 | 7 | 1.88 | 1.44 | 5 | … | 8.31 | 9.25 | 0.875 | 8 | 0.75 | 4 | … | 280 | 34.9 | 178 | 48 | 36 | 127 | … | 211 | 235 | 102 | …
16.1 | 250 | 6 | 12.5 | 1.44 | 8.12 | 1.94 | 1.56 | 6 | .. | 9.69 | 10.62 | 0.875 | 12 | 0.75 | 4 | … | 320 | 36.5 | 206 | 49 | 39 | 152 | … | 246 | 270 | 102 | …
16.1 | 250 | 8 | 15 | 1.62 | 10.25 | 2.19 | 1.75 | 8 | … | 11.94 | 13 | 1.125 | 12 | 0.88 | 4.5 | … | 380 | 41.3 | 260 | 56 | 43 | 203 | … | 303 | 330 | 114 | …
16.1 | 250 | 10 | 17.5 | 1.88 | 12.62 | 2.38 | 1.94 | 10 | 0.94 | 14.06 | 15.25 | 1.25 | 16 | 1 | 5.5 | … | 445 | 47.6 | 321 | 60 | 49 | 254 | 23.8 | 357 | 387 | 131 | …
16.1 | 250 | 12 | 20.5 | 2 | 14.75 | 2.56 | 2.19 | 12 | 1 | 16.44 | 17.75 | 1.25 | 16 | 1.12 | 5.5 | … | 520 | 50.8 | 375 | 65 | 54 | 305 | 25.4 | 418 | 451 | 140 | …
16.1 | 250 | 14 | 23 | 2.12 | 16.25 | 2.69 | 2.25 | 13.25 | 1.12 | 18.94 | 20.25 | 1.375 | 20 | 1.12 | 6 | … | 585 | 54 | 413 | 68 | 57 | 337 | 28.6 | 481 | 514 | 152 | …
16.1 | 250 | 16 | 25 | 2.25 | 18.38 | 2.88 | 2.5 | 15.25 | 1.25 | 21.06 | 22.5 | 1.375 | 20 | 1.25 | 6.5 | … | 650 | 57.2 | 467 | 73 | 62 | 387 | 31.8 | 535 | 572 | 159 | …
16.1 | 250 | 18 | 28 | 2.38 | … | … | … | 17 | 1.38 | 23.31 | 24.75 | 1.375 | 24 | 1.25 | 6.5 | … | 710 | 60.3 | … | … | … | 432 | 34.9 | 592 | 629 | 165 | …
16.1 | 250 | 20 | 30.5 | 2.5 | … | … | … | 19 | 1.5 | 25.56 | 27 | 1.375 | 24 | 1.25 | 7 | … | 775 | 63.5 | … | … | … | 483 | 38.1 | 649 | 686 | 172 | …
16.1 | 250 | 24 | 36 | 2.75 | … | … | … | 23 | 1.62 | 30.31 | 32 | 1.625 | 24 | 1.5 | 7.5 | 9.5 | 915 | 69.8 | … | … | … | 584 | 41.3 | 770 | 813 | 191 | 241
16.1 | 250 | 30 | 43 | 3 | … | … | … | 29 | 2 | 37.19 | 39.25 | 2 | 28 | 1.75 | 8.5 | 10.5 | 1090 | 76.2 | … | … | … | 737 | 50.8 | 945 | 997 | 216 | 268
16.1 | 250 | 36 (10) | 50 | 3.38 | … | … | … | … | … | 43.69 | 46 | 2.25 | 32 | 2 | 9.5 | 12 | 1270 | 85.7 | … | … | … | … | … | 1110 | 1168 | 241 | 298
16.1 | 250 | 42 (10) | 57 | 3.69 | … | … | … | … | … | 50.44 | 52.75 | 2.25 | 36 | 2 | 10 | 12.5 | 1450 | 93.7 | … | … | … | … | … | 1281 | 1340 | 254 | 318
16.1 | 250 | 48 (10) | 65 | 4 | … | … | … | … | … | 58.44 | 60.75 | 2.25 | 40 | 2 | 11 | 13 | 1650 | 101.6 | … | … | … | … | … | 1484 | 1543 | 273 | 330
AWWA | Flange Class | Pipe Size in. | OD Flange (A) in. | ID Flange (B) in. | Bolt Number | Bolt Circle Diameter (C) in. | Diameter of Bolts in. | Flange Thickness in. | Min Thickness in. | Flange Dimensions in. (T) | Flange Dimensions in. (L) | Flange Dimensions in. (E) | Psi | Max Pressure (psi)
C207 | B | 4 | 9 | 4.57 | 8 | 7.5 | 0.625 | 0.625 | 0.625 | N/A | N/A | N/A | 86 | 129
C207 | B | 5 | 10 | 5.66 | 8 | 8.5 | 0.75 | 0.625 | 0.625 | N/A | N/A | N/A | 86 | 129
C207 | B | 6 | 11 | 6.72 | 8 | 9.5 | 0.75 | 0.688 | 0.688 | N/A | N/A | N/A | 86 | 129
C207 | B | 8 | 13.5 | 8.72 | 8 | 11.75 | 0.75 | 0.688 | 0.688 | N/A | N/A | N/A | 86 | 129
C207 | B | 10 | 16 | 10.88 | 12 | 14.25 | 0.875 | 0.688 | 0.688 | N/A | N/A | N/A | 86 | 129
C207 | B | 12 | 19 | 12.88 | 12 | 17 | 0.875 | 0.688 | 0.719 | N/A | N/A | N/A | 86 | 129
C207 | B | 14 | 21 | 14.19 | 12 | 18.75 | 1 | 0.688 | 0.791 | N/A | N/A | N/A | 86 | 129
C207 | B | 16 | 23.5 | 16.19 | 16 | 21.25 | 1 | 0.688 | 0.892 | N/A | N/A | N/A | 86 | 129
C207 | B | 18 | 25 | 18.19 | 16 | 22.75 | 1.125 | 0.688 | 0.95 | N/A | N/A | N/A | 86 | 129
C207 | B | 20 | 27.5 | 20.19 | 20 | 25 | 1.125 | 0.688 | 1.04 | N/A | N/A | N/A | 86 | 129
C207 | B | 22 | 29.5 | 22.19 | 20 | 27.25 | 1.25 | 0.75 | 1.132 | N/A | N/A | N/A | 86 | 129
C207 | B | 24 | 32 | 24.19 | 20 | 29.5 | 1.25 | 0.75 | 1.216 | N/A | N/A | N/A | 86 | 129
C207 | B | 26 | 34.25 |  | 24 | 31.75 | 1.25 | 0.812 | 1.307 | N/A | N/A | N/A | 86 | 129
C207 | B | 28 | 36.5 |  | 28 | 34 | 1.25 | 0.875 | 1.398 | N/A | N/A | N/A | 86 | 129
C207 | B | 30 | 38.75 |  | 28 | 36 | 1.25 | 0.875 | 1.477 | N/A | N/A | N/A | 86 | 129
C207 | B | 32 | 41.75 |  | 28 | 38.5 | 1.5 | 0.938 | 1.581 | N/A | N/A | N/A | 86 | 129
C207 | B | 34 | 43.75 |  | 32 | 40.5 | 1.5 | 0.938 | 1.661 | N/A | N/A | N/A | 86 | 129
C207 | B | 36 | 46 |  | 32 | 42.75 | 1.5 | 1 | 1.751 | N/A | N/A | N/A | 86 | 129
C207 | B | 38 | 48.75 |  | 32 | 45.25 | 1.5 | 1 | 1.853 | N/A | N/A | N/A | 86 | 129
C207 | B | 40 | 50.75 |  | 36 | 47.25 | 1.5 | 1 | 1.933 | N/A | N/A | N/A | 86 | 129
C207 | B | 42 | 53 |  | 36 | 49.5 | 1.5 | 1.125 | 2.023 | N/A | N/A | N/A | 86 | 129
C207 | B | 44 | 55.25 |  | 40 | 51.75 | 1.5 | 1.125 | 2.114 | N/A | N/A | N/A | 86 | 129
C207 | B | 46 | 57.25 |  | 40 | 53.75 | 1.5 | 1.125 | 2.194 | N/A | N/A | N/A | 86 | 129
C207 | B | 48 | 59.5 |  | 44 | 56 | 1.5 | 1.25 | 2.285 | N/A | N/A | N/A | 86 | 129
C207 | B | 50 | 61.75 |  | 44 | 58.25 | 1.75 | 1.25 | 2.377 | N/A | N/A | N/A | 86 | 129
C207 | B | 52 | 64 |  | 44 | 60.5 | 1.75 | 1.25 | 2.468 | N/A | N/A | N/A | 86 | 129
C207 | B | 54 | 66.25 |  | 44 | 62.75 | 1.75 | 1.375 | 2.559 | N/A | N/A | N/A | 86 | 129
C207 | B | 60 | 73 |  | 52 | 69.25 | 1.75 | 1.5 | 2.82 | N/A | N/A | N/A | 86 | 129
C207 | B | 66 | 80 |  | 52 | 76 | 1.75 | 1.625 | 3.092 | N/A | N/A | N/A | 86 | 129
C207 | B | 72 | 86.5 |  | 60 | 82.5 | 1.75 | 1.75 | 3.353 | N/A | N/A | N/A | 86 | 129
C207 | B | 78 | 93 |  | 64 | 89 | 2 | 2 |  | N/A | N/A | N/A | 86 | 129
C207 | B | 84 | 99.75 |  | 64 | 95.5 | 2 | 2 |  | N/A | N/A | N/A | 86 | 129
C207 | B | 90 | 106.5 |  | 68 | 102 | 2.25 | 2.25 |  | N/A | N/A | N/A | 86 | 129
C207 | B | 96 | 113.25 |  | 68 | 108.5 | 2.25 | 2.25 |  | N/A | N/A | N/A | 86 | 129
C207 | B | 102 | 120 |  | 72 | 114.5 | 2.5 | 2.5 |  | N/A | N/A | N/A | 86 | 129
C207 | B | 108 | 126.75 |  | 72 | 120.75 | 2.5 | 2.5 |  | N/A | N/A | N/A | 86 | 129
C207 | B | 114 | 133.5 |  | 76 | 126.75 | 2.75 | 2.75 |  | N/A | N/A | N/A | 86 | 129
C207 | B | 120 | 140.25 |  | 76 | 132.75 | 2.75 | 2.75 |  | N/A | N/A | N/A | 86 | 129
C207 | B | 126 | 147 |  | 80 | 139.25 | 3 | 3 |  | N/A | N/A | N/A | 86 | 129
C207 | B | 132 | 153.75 |  | 80 | 145.75 | 3 | 3 |  | N/A | N/A | N/A | 86 | 129
C207 | B | 144 | 167.25 |  | 84 | 158.25 | 3.25 | 3.25 |  | N/A | N/A | N/A | 86 | 129
C207 | D | 4 | 9 | 4.57 | 8 | 7.5 | 0.625 | 0.625 | 0.625 | 0.5 | 0.875 | 5.312 | 175-150 | 262.5
C207 | D | 5 | 10 | 5.66 | 8 | 8.5 | 0.75 | 0.625 | 0.65 | 0.562 | 1.25 | 6.312 | 175-150 | 262.5
C207 | D | 6 | 11 | 6.72 | 8 | 9.5 | 0.75 | 0.688 | 0.693 | 0.562 | 1.25 | 7.562 | 175-150 | 262.5
C207 | D | 8 | 13.5 | 8.72 | 8 | 11.75 | 0.75 | 0.688 | 0.812 | 0.562 | 1.25 | 9.688 | 175-150 | 262.5
C207 | D | 10 | 16 | 10.88 | 12 | 14.25 | 0.875 | 0.688 | 0.953 | 0.688 | 1.25 | 12 | 175-150 | 262.5
C207 | D | 12 | 19 | 12.88 | 12 | 17 | 0.875 | 0.812 | 1.117 | 0.688 | 1.25 | 14.375 | 175-150 | 262.5
C207 | D | 14 | 21 | 14.19 | 12 | 18.75 | 1 | 0.938 | 1.133 | 0.75 | 1.25 | 15.75 | 175-150 | 225
C207 | D | 16 | 23.5 | 16.19 | 16 | 21.25 | 1 | 1 | 1.265 | 0.75 | 1.25 | 18 | 175-150 | 225
C207 | D | 18 | 25 | 18.19 | 16 | 22.75 | 1.125 | 1.062 | 1.331 | 0.75 | 1.25 | 19.875 | 175-150 | 225
C207 | D | 20 | 27.5 | 20.19 | 20 | 25 | 1.125 | 1.125 | 1.448 | 0.75 | 1.25 | 22 | 175-150 | 225
C207 | D | 22 | 29.5 | 22.19 | 20 | 27.25 | 1.25 | 1.188 | 1.568 | 1 | 1.75 | 24.25 | 175-150 | 225
C207 | D | 24 | 32 | 24.19 | 20 | 29.5 | 1.25 | 1.25 | 1.661 | 1 | 1.75 | 26.125 | 175-150 | 225
C207 | D | 26 | 34.25 |  | 24 | 31.75 | 1.25 | 1.312 | 1.786 | 1 | 1.75 | 28.5 | 175-150 | 225
C207 | D | 28 | 36.5 |  | 28 | 34 | 1.25 | 1.312 | 1.906 | 1 | 1.75 | 30.5 | 175-150 | 225
C207 | D | 30 | 38.75 |  | 28 | 36 | 1.25 | 1.375 | 2.008 | 1 | 1.75 | 32.5 | 175-150 | 225
C207 | D | 32 | 41.75 |  | 28 | 38.5 | 1.5 | 1.5 | 2.15 | 1.125 | 1.75 | 34.75 | 175-150 | 225
C207 | D | 34 | 43.75 |  | 32 | 40.5 | 1.5 | 1.5 | 2.252 | 1.125 | 1.75 | 36.75 | 175-150 | 225
C207 | D | 36 | 46 |  | 32 | 42.75 | 1.5 | 1.625 | 2.37 | 1.125 | 1.75 | 38.75 | 175-150 | 225
C207 | D | 38 | 48.75 |  | 32 | 45.25 | 1.5 | 1.625 | 2.506 | 1.125 | 1.75 | 40.75 | 175-150 | 225
C207 | D | 40 | 50.75 |  | 36 | 47.25 | 1.5 | 1.625 | 2.609 | 1.125 | 1.75 | 43 | 175-150 | 225
C207 | D | 42 | 53 |  | 36 | 49.5 | 1.5 | 1.75 | 2.729 | 1.25 | 1.75 | 45 | 175-150 | 225
C207 | D | 44 | 55.25 |  | 40 | 51.75 | 1.5 | 1.75 | 2.849 | 1.25 | 2.25 | 47 | 175-150 | 225
C207 | D | 46 | 57.25 |  | 40 | 53.75 | 1.5 | 1.75 | 2.952 | 1.25 | 2.25 | 49 | 175-150 | 225
C207 | D | 48 | 59.5 |  | 44 | 56 | 1.5 | 1.875 | 3.072 | 1.375 | 2.5 | 51 | 175-150 | 225
C207 | D | 50 | 61.75 |  | 44 | 58.25 | 1.75 | 2 | 3.196 | 1.375 | 2.5 | 53 | 175-150 | 225
C207 | D | 52 | 64 |  | 44 | 60.5 | 1.75 | 2 | 3.315 | 1.375 | 2.5 | 55 | 175-150 | 225
C207 | D | 54 | 66.25 |  | 44 | 62.75 | 1.75 | 2.125 | 3.435 | 1.375 | 2.5 | 57 | 175-150 | 225
C207 | D | 60 | 73 |  | 52 | 69.25 | 1.75 | 2.25 | 3.779 | 1.5 | 2.75 | 63 | 175-150 | 225
C207 | D | 66 | 80 |  | 52 | 76 | 1.75 | 2.5 | 4.136 | 1.5 | 2.75 | 69 | 175-150 | 225
C207 | D | 72 | 86.5 |  | 60 | 82.5 | 1.75 | 2.625 | 4.48 | 1.5 | 2.75 | 75 | 175-150 | 225
C207 | D | 78 | 93 |  | 64 | 89 | 2 | 2.75 |  | 1.75 | 3 | 81.25 | 175-150 | 225
C207 | D | 84 | 99.75 |  | 64 | 95.5 | 2 | 2.875 |  | 1.75 | 3 | 87.5 | 175-150 | 225
C207 | D | 90 | 106.5 |  | 68 | 102 | 2.25 | 3 |  | 2 | 3.25 | 93.75 | 175-150 | 225
C207 | D | 96 | 113.25 |  | 68 | 108.5 | 2.25 | 3.25 |  | 2 | 3.25 | 100 | 175-150 | 225
C207 | D | 102 | 120 |  | 72 | 114.5 | 2.5 | 3.25 |  |  |  |  | 175-150 | 225
C207 | D | 108 | 126.75 |  | 72 | 120.75 | 2.5 | 3.375 |  |  |  |  | 175-150 | 225
C207 | D | 114 | 133.5 |  | 76 | 126.75 | 2.75 | 3.5 |  |  |  |  | 175-150 | 225
C207 | D | 120 | 140.25 |  | 76 | 132.75 | 2.75 | 3.5 |  |  |  |  | 175-150 | 225
C207 | D | 126 | 147 |  | 80 | 139.25 | 3 | 3.75 |  |  |  |  | 175-150 | 225
C207 | D | 132 | 153.75 |  | 80 | 145.75 | 3 | 3.875 |  |  |  |  | 175-150 | 225
C207 | D | 144 | 167.25 |  | 84 | 158.25 | 3.25 | 4.125 |  |  |  |  | 175-150 | 225
C207 | E | 4 | 9 | 4.57 | 8 | 7.5 | 0.625 | 1.125 | 1.125 | 0.938 | 1.312 | 5.312 | 275 | 412.5
C207 | E | 5 | 10 | 5.66 | 8 | 8.5 | 0.75 | 1.188 | 1.188 | 0.938 | 1.438 | 6.438 | 275 | 412.5
C207 | E | 6 | 11 | 6.72 | 8 | 9.5 | 0.75 | 1.313 | 1.313 | 1 | 1.562 | 7.562 | 275 | 412.5
C207 | E | 8 | 13.5 | 8.72 | 8 | 11.75 | 0.75 | 1.5 | 1.5 | 1.125 | 1.75 | 9.688 | 275 | 412.5
C207 | E | 10 | 16 | 10.88 | 12 | 14.25 | 0.875 | 1.563 | 1.563 | 1.188 | 1.938 | 12 | 275 | 412.5
C207 | E | 12 | 19 | 12.88 | 12 | 17 | 0.875 | 1.75 | 1.75 | 1.25 | 2.188 | 14.375 | 275 | 412.5
C207 | E | 14 | 21 | 14.19 | 12 | 18.75 | 1 | 1.875 | 1.875 | 1.375 | 2.25 | 15.75 | 275 | 412.5
C207 | E | 16 | 23.5 | 16.19 | 16 | 21.25 | 1 | 2 | 2 | 1.438 | 2.5 | 18 | 275 | 412.5
C207 | E | 18 | 25 | 18.19 | 16 | 22.75 | 1.125 | 2.125 | 2.125 | 1.562 | 2.688 | 19.875 | 275 | 412.5
C207 | E | 20 | 27.5 | 20.19 | 20 | 25 | 1.125 | 2.375 | 2.375 | 1.688 | 2.875 | 22 | 275 | 412.5
C207 | E | 22 | 29.5 | 22.19 | 20 | 27.25 | 1.25 | 2.5 | 2.5 | 1.812 | 3.125 | 24 | 275 | 412.5
C207 | E | 24 | 32 | 24.19 | 20 | 29.5 | 1.25 | 2.625 | 2.625 | 1.875 | 3.25 | 26.125 | 275 | 412.5
C207 | E | 26 | 34.25 |  | 24 | 31.75 | 1.25 | 2.75 | 2.75 | 2 | 3.375 | 28.5 | 275 | 412.5
C207 | E | 28 | 36.5 |  | 28 | 34 | 1.25 | 2.75 | 2.75 | 2.062 | 3.438 | 30.75 | 275 | 412.5
C207 | E | 30 | 38.75 |  | 28 | 36 | 1.25 | 2.875 | 2.875 | 2.125 | 3.5 | 32.75 | 275 | 412.5
C207 | E | 32 | 41.75 |  | 28 | 38.5 | 1.5 | 3 | 3 | 2.25 | 3.625 | 35 | 275 | 412.5
C207 | E | 34 | 43.75 |  | 32 | 40.5 | 1.5 | 3 | 3.05 | 2.312 | 3.688 | 37 | 275 | 412.5
C207 | E | 36 | 46 |  | 32 | 42.75 | 1.5 | 3.125 | 3.209 | 2.375 | 3.75 | 39.25 | 275 | 412.5
C207 | E | 38 | 48.75 |  | 32 | 45.25 | 1.5 | 3.125 | 3.394 | 2.375 | 3.75 | 41.75 | 275 | 412.5
C207 | E | 40 | 50.75 |  | 36 | 47.25 | 1.5 | 3.25 | 3.533 | 2.5 | 3.875 | 43.75 | 275 | 412.5
C207 | E | 42 | 53 |  | 36 | 49.5 | 1.5 | 3.375 | 3.695 | 2.625 | 4 | 46 | 275 | 412.5
C207 | E | 44 | 55.25 |  | 40 | 51.75 | 1.5 | 3.375 | 3.857 | 2.625 | 4 | 48 | 275 | 412.5
C207 | E | 46 | 57.25 |  | 40 | 53.75 | 1.5 | 3.438 | 3.997 | 2.688 | 4.062 | 50 | 275 | 412.5
C207 | E | 48 | 59.5 |  | 44 | 56 | 1.5 | 3.5 | 4.159 | 2.75 | 4.125 | 52.25 | 275 | 412.5
C207 | E | 50 | 61.75 |  | 44 | 58.25 | 1.75 | 3.5 | 4.327 | 2.75 | 4.125 | 54.25 | 275 | 412.5
C207 | E | 52 | 64 |  | 44 | 60.5 | 1.75 | 3.625 | 4.489 | 2.875 | 4.25 | 56.5 | 275 | 412.5
C207 | E | 54 | 66.25 |  | 44 | 62.75 | 1.75 | 3.75 | 4.651 | 3 | 4.375 | 58.75 | 275 | 412.5
C207 | E | 60 | 73 |  | 52 | 69.75 | 1.75 | 3.875 | 5.116 | 3.125 | 4.5 | 65.25 | 275 | 412.5
C207 | E | 66 | 80 |  | 52 | 76 | 1.75 | 4.25 | 5.601 | 3.375 | 4.875 | 71.5 | 275 | 412.5
C207 | E | 72 | 86.5 |  | 60 | 82.5 | 1.75 | 4.375 | 6.066 | 3.5 | 5 | 78.5 | 275 | 412.5
C207 | E | 78 | 93 |  | 64 | 89 | 2 | 4.75 |  | 3.875 | 5.375 | 84.5 | 275 | 412.5
C207 | E | 84 | 99.75 |  | 64 | 95.5 | 2 | 4.75 |  | 3.875 | 5.375 | 90.5 | 275 | 412.5
C207 | E | 90 | 106.5 |  | 68 | 102 | 2.25 | 5.125 |  | 4.25 | 5.75 | 96.75 | 275 | 412.5
C207 | E | 96 | 113.25 |  | 68 | 108.5 | 2.25 | 5.125 |  | 4.25 | 5.75 | 102.75 | 275 | 412.5
C207 | E | 102 | 120 |  | 72 | 114.5 | 2.5 | 5.5 |  |  |  |  | 275 | 412.5
C207 | E | 108 | 126.75 |  | 72 | 120.75 | 2.5 | 5.5 |  |  |  |  | 275 | 412.5
C207 | E | 114 | 133.5 |  | 76 | 126.75 | 2.75 | 5.875 |  |  |  |  | 275 | 412.5
C207 | E | 120 | 140.25 |  | 76 | 132.75 | 2.75 | 5.875 |  |  |  |  | 275 | 412.5
C207 | E | 126 | 147 |  | 80 | 139.25 | 3 | 6.25 |  |  |  |  | 275 | 412.5
C207 | E | 132 | 153.75 |  | 80 | 145.75 | 3 | 6.25 |  |  |  |  | 275 | 412.5
C207 | E | 144 | 167.25 |  | 84 | 158.25 | 3.25 | 6.75 |  |  |  |  | 275 | 412.5
C207 | F | 4 | 10 | 4.57 | 8 | 7.88 | 0.75 | 1.13 | 1.13 | N/A | N/A | N/A | 300 | 450
C207 | F | 5 | 11 | 5.66 | 8 | 9.25 | 0.75 | 1.21 | 1.21 | N/A | N/A | N/A | 300 | 450
C207 | F | 6 | 12.5 | 6.73 | 12 | 10.62 | 0.75 | 1.31 | 1.31 | N/A | N/A | N/A | 300 | 450
C207 | F | 8 | 15 | 8.73 | 12 | 13 | 0.875 | 1.31 | 1.31 | N/A | N/A | N/A | 300 | 450
C207 | F | 10 | 17.5 | 10.88 | 16 | 15.25 | 1 | 1.5 | 1.5 | N/A | N/A | N/A | 300 | 450
C207 | F | 12 | 20.5 | 12.88 | 16 | 17.75 | 1.125 | 1.63 | 1.63 | N/A | N/A | N/A | 300 | 450
C207 | F | 14 | 23 | 14.19 | 20 | 20.25 | 1.125 | 1.94 | 1.94 | N/A | N/A | N/A | 300 | 450
C207 | F | 16 | 25.5 | 16.19 | 20 | 22.5 | 1.25 | 2.14 | 2.14 | N/A | N/A | N/A | 300 | 450
C207 | F | 18 | 28 | 18.19 | 24 | 24.75 | 1.25 | 2.25 | 2.25 | N/A | N/A | N/A | 300 | 450
C207 | F | 20 | 30.5 | 20.19 | 24 | 27 | 1.25 | 2.33 | 2.33 | N/A | N/A | N/A | 300 | 450
C207 | F | 22 | 33 | 22.19 | 24 | 29.25 | 1.255 | 2.5 | 2.5 | N/A | N/A | N/A | 300 | 450
C207 | F | 24 | 36 | 24.19 | 24 | 32 | 1.5 | 2.69 | 2.69 | N/A | N/A | N/A | 300 | 450
C207 | F | 26 | 38.25 | - | 28 | 34.5 | 1.75 | 3 | 3 | N/A | N/A | N/A | 300 | 450
C207 | F | 28 | 40.75 | - | 28 | 37 | 1.75 | 3.13 | 3.13 | N/A | N/A | N/A | 300 | 450
C207 | F | 30 | 43 | - | 28 | 39.25 | 1.75 | 3.15 | 3.166 | N/A | N/A | N/A | 300 | 450
C207 | F | 32 | 45.25 | - | 28 | 41.5 | 1.75 | 3.25 | 3.332 | N/A | N/A | N/A | 300 | 450
C207 | F | 34 | 47.5 | - | 28 | 43.5 | 1.75 | 3.38 | 3.475 | N/A | N/A | N/A | 300 | 450
C207 | F | 36 | 50 | - | 32 | 46 | 2 | 3.46 | 3.671 | N/A | N/A | N/A | 300 | 450
C207 | F | 38 | 52.25 | - | 32 | 48 | 2 | 3.5 | 3.815 | N/A | N/A | N/A | 300 | 450
C207 | F | 40 | 54.25 | - | 36 | 50.25 | 2 | 3.63 | 3.982 | N/A | N/A | N/A | 300 | 450
C207 | F | 42 | 57 | - | 36 | 52.75 | 2 | 3.81 | 4.171 | N/A | N/A | N/A | 300 | 450
C207 | F | 44 | 59.25 | - | 36 | 55 | 2 | 4 | 4.338 | N/A | N/A | N/A | 300 | 450
C207 | F | 46 | 61.5 | - | 40 | 57.25 | 2 | 4.13 | 4.505 | N/A | N/A | N/A | 300 | 450
C207 | F | 48 | 65 | - | 40 | 60.75 | 2 | 4.5 | 4.781 | N/A | N/A | N/A | 300 | 450

## Common (hidden)
Type | Standard | Flange Class | Pipe size | Number of Bolts | Bolt Diameter | Outside Flange Diameter | Bolt Diameter- Circle | Min Flange Thickness | Outside Flange Diameter (mm) | Bolt Diameter- Circle (mm) | Min Flange Thickness (mm)
AWWA | C207 | B | 4 | 8 | 0.625 | 9 | 7.5 | 0.625 | 228.6 | 190.5 | 15.875
AWWA | C207 | B | 5 | 8 | 0.75 | 10 | 8.5 | 0.625 | 254 | 215.9 | 15.875
AWWA | C207 | B | 6 | 8 | 0.75 | 11 | 9.5 | 0.688 | 279.4 | 241.3 | 17.4752
AWWA | C207 | B | 8 | 8 | 0.75 | 13.5 | 11.75 | 0.688 | 342.9 | 298.45 | 17.4752
AWWA | C207 | B | 10 | 12 | 0.875 | 16 | 14.25 | 0.688 | 406.4 | 361.95 | 17.4752
AWWA | C207 | B | 12 | 12 | 0.875 | 19 | 17 | 0.719 | 482.6 | 431.8 | 18.2626
AWWA | C207 | B | 14 | 12 | 1 | 21 | 18.75 | 0.791 | 533.4 | 476.25 | 20.0914
AWWA | C207 | B | 16 | 16 | 1 | 23.5 | 21.25 | 0.892 | 596.9 | 539.75 | 22.6568
AWWA | C207 | B | 18 | 16 | 1.125 | 25 | 22.75 | 0.95 | 635 | 577.85 | 24.13
AWWA | C207 | B | 20 | 20 | 1.125 | 27.5 | 25 | 1.04 | 698.5 | 635 | 26.416
AWWA | C207 | B | 22 | 20 | 1.25 | 29.5 | 27.25 | 1.132 | 749.3 | 692.15 | 28.7528
AWWA | C207 | B | 24 | 20 | 1.25 | 32 | 29.5 | 1.216 | 812.8 | 749.3 | 30.8864
AWWA | C207 | B | 26 | 24 | 1.25 | 34.25 | 31.75 | 1.307 | 869.95 | 806.45 | 33.1978
AWWA | C207 | B | 28 | 28 | 1.25 | 36.5 | 34 | 1.398 | 927.1 | 863.6 | 35.5092
AWWA | C207 | B | 30 | 28 | 1.25 | 38.75 | 36 | 1.477 | 984.25 | 914.4 | 37.5158
AWWA | C207 | B | 32 | 28 | 1.5 | 41.75 | 38.5 | 1.581 | 1060.45 | 977.9 | 40.1574
AWWA | C207 | B | 34 | 32 | 1.5 | 43.75 | 40.5 | 1.661 | 1111.25 | 1028.7 | 42.1894
AWWA | C207 | B | 36 | 32 | 1.5 | 46 | 42.75 | 1.751 | 1168.4 | 1085.85 | 44.4754
AWWA | C207 | B | 38 | 32 | 1.5 | 48.75 | 45.25 | 1.853 | 1238.25 | 1149.35 | 47.0662
AWWA | C207 | B | 40 | 36 | 1.5 | 50.75 | 47.25 | 1.933 | 1289.05 | 1200.15 | 49.0982
AWWA | C207 | B | 42 | 36 | 1.5 | 53 | 49.5 | 2.023 | 1346.2 | 1257.3 | 51.3842
AWWA | C207 | B | 44 | 40 | 1.5 | 55.25 | 51.75 | 2.114 | 1403.35 | 1314.45 | 53.6956
AWWA | C207 | B | 46 | 40 | 1.5 | 57.25 | 53.75 | 2.194 | 1454.15 | 1365.25 | 55.7276
AWWA | C207 | B | 48 | 44 | 1.5 | 59.5 | 56 | 2.285 | 1511.3 | 1422.4 | 58.039
AWWA | C207 | B | 50 | 44 | 1.75 | 61.75 | 58.25 | 2.377 | 1568.45 | 1479.55 | 60.3758
AWWA | C207 | B | 52 | 44 | 1.75 | 64 | 60.5 | 2.468 | 1625.6 | 1536.7 | 62.6872
AWWA | C207 | B | 54 | 44 | 1.75 | 66.25 | 62.75 | 2.559 | 1682.75 | 1593.85 | 64.9986
AWWA | C207 | B | 60 | 52 | 1.75 | 73 | 69.25 | 2.82 | 1854.2 | 1758.95 | 71.628
AWWA | C207 | B | 66 | 52 | 1.75 | 80 | 76 | 3.092 | 2032 | 1930.4 | 78.5368
AWWA | C207 | B | 72 | 60 | 1.75 | 86.5 | 82.5 | 3.353 | 2197.1 | 2095.5 | 85.1662
AWWA | C207 | B | 78 | 64 | 2 | 93 | 89 |  | 2362.2 | 2260.6
AWWA | C207 | B | 84 | 64 | 2 | 99.75 | 95.5 |  | 2533.65 | 2425.7
AWWA | C207 | B | 90 | 68 | 2.25 | 106.5 | 102 |  | 2705.1 | 2590.8
AWWA | C207 | B | 96 | 68 | 2.25 | 113.25 | 108.5 |  | 2876.55 | 2755.9
AWWA | C207 | B | 102 | 72 | 2.5 | 120 | 114.5 |  | 3048 | 2908.3
AWWA | C207 | B | 108 | 72 | 2.5 | 126.75 | 120.75 |  | 3219.45 | 3067.05
AWWA | C207 | B | 114 | 76 | 2.75 | 133.5 | 126.75 |  | 3390.9 | 3219.45
AWWA | C207 | B | 120 | 76 | 2.75 | 140.25 | 132.75 |  | 3562.35 | 3371.85
AWWA | C207 | B | 126 | 80 | 3 | 147 | 139.25 |  | 3733.8 | 3536.95
AWWA | C207 | B | 132 | 80 | 3 | 153.75 | 145.75 |  | 3905.25 | 3702.05
AWWA | C207 | B | 144 | 84 | 3.25 | 167.25 | 158.25 |  | 4248.15 | 4019.55
AWWA | C207 | D | 4 | 8 | 0.625 | 9 | 7.5 | 0.625 | 228.6 | 190.5 | 15.875
AWWA | C207 | D | 5 | 8 | 0.75 | 10 | 8.5 | 0.65 | 254 | 215.9 | 16.51
AWWA | C207 | D | 6 | 8 | 0.75 | 11 | 9.5 | 0.693 | 279.4 | 241.3 | 17.6022
AWWA | C207 | D | 8 | 8 | 0.75 | 13.5 | 11.75 | 0.812 | 342.9 | 298.45 | 20.6248
AWWA | C207 | D | 10 | 12 | 0.875 | 16 | 14.25 | 0.953 | 406.4 | 361.95 | 24.2062
AWWA | C207 | D | 12 | 12 | 0.875 | 19 | 17 | 1.117 | 482.6 | 431.8 | 28.3718
AWWA | C207 | D | 14 | 12 | 1 | 21 | 18.75 | 1.133 | 533.4 | 476.25 | 28.7782
AWWA | C207 | D | 16 | 16 | 1 | 23.5 | 21.25 | 1.265 | 596.9 | 539.75 | 32.131
AWWA | C207 | D | 18 | 16 | 1.125 | 25 | 22.75 | 1.331 | 635 | 577.85 | 33.8074
AWWA | C207 | D | 20 | 20 | 1.125 | 27.5 | 25 | 1.448 | 698.5 | 635 | 36.7792
AWWA | C207 | D | 22 | 20 | 1.25 | 29.5 | 27.25 | 1.568 | 749.3 | 692.15 | 39.8272
AWWA | C207 | D | 24 | 20 | 1.25 | 32 | 29.5 | 1.661 | 812.8 | 749.3 | 42.1894
AWWA | C207 | D | 26 | 24 | 1.25 | 34.25 | 31.75 | 1.786 | 869.95 | 806.45 | 45.3644
AWWA | C207 | D | 28 | 28 | 1.25 | 36.5 | 34 | 1.906 | 927.1 | 863.6 | 48.4124
AWWA | C207 | D | 30 | 28 | 1.25 | 38.75 | 36 | 2.008 | 984.25 | 914.4 | 51.0032
AWWA | C207 | D | 32 | 28 | 1.5 | 41.75 | 38.5 | 2.15 | 1060.45 | 977.9 | 54.61
AWWA | C207 | D | 34 | 32 | 1.5 | 43.75 | 40.5 | 2.252 | 1111.25 | 1028.7 | 57.2008
AWWA | C207 | D | 36 | 32 | 1.5 | 46 | 42.75 | 2.37 | 1168.4 | 1085.85 | 60.198
AWWA | C207 | D | 38 | 32 | 1.5 | 48.75 | 45.25 | 2.506 | 1238.25 | 1149.35 | 63.6524
AWWA | C207 | D | 40 | 36 | 1.5 | 50.75 | 47.25 | 2.609 | 1289.05 | 1200.15 | 66.2686
AWWA | C207 | D | 42 | 36 | 1.5 | 53 | 49.5 | 2.729 | 1346.2 | 1257.3 | 69.3166
AWWA | C207 | D | 44 | 40 | 1.5 | 55.25 | 51.75 | 2.849 | 1403.35 | 1314.45 | 72.3646
AWWA | C207 | D | 46 | 40 | 1.5 | 57.25 | 53.75 | 2.952 | 1454.15 | 1365.25 | 74.9808
AWWA | C207 | D | 48 | 44 | 1.5 | 59.5 | 56 | 3.072 | 1511.3 | 1422.4 | 78.0288
AWWA | C207 | D | 50 | 44 | 1.75 | 61.75 | 58.25 | 3.196 | 1568.45 | 1479.55 | 81.1784
AWWA | C207 | D | 52 | 44 | 1.75 | 64 | 60.5 | 3.315 | 1625.6 | 1536.7 | 84.201
AWWA | C207 | D | 54 | 44 | 1.75 | 66.25 | 62.75 | 3.435 | 1682.75 | 1593.85 | 87.249
AWWA | C207 | D | 60 | 52 | 1.75 | 73 | 69.25 | 3.779 | 1854.2 | 1758.95 | 95.9866
AWWA | C207 | D | 66 | 52 | 1.75 | 80 | 76 | 4.136 | 2032 | 1930.4 | 105.0544
AWWA | C207 | D | 72 | 60 | 1.75 | 86.5 | 82.5 | 4.48 | 2197.1 | 2095.5 | 113.792
AWWA | C207 | D | 78 | 64 | 2 | 93 | 89 |  | 2362.2 | 2260.6
AWWA | C207 | D | 84 | 64 | 2 | 99.75 | 95.5 |  | 2533.65 | 2425.7
AWWA | C207 | D | 90 | 68 | 2.25 | 106.5 | 102 |  | 2705.1 | 2590.8
AWWA | C207 | D | 96 | 68 | 2.25 | 113.25 | 108.5 |  | 2876.55 | 2755.9
AWWA | C207 | D | 102 | 72 | 2.5 | 120 | 114.5 |  | 3048 | 2908.3
AWWA | C207 | D | 108 | 72 | 2.5 | 126.75 | 120.75 |  | 3219.45 | 3067.05
AWWA | C207 | D | 114 | 76 | 2.75 | 133.5 | 126.75 |  | 3390.9 | 3219.45
AWWA | C207 | D | 120 | 76 | 2.75 | 140.25 | 132.75 |  | 3562.35 | 3371.85
AWWA | C207 | D | 126 | 80 | 3 | 147 | 139.25 |  | 3733.8 | 3536.95
AWWA | C207 | D | 132 | 80 | 3 | 153.75 | 145.75 |  | 3905.25 | 3702.05
AWWA | C207 | D | 144 | 84 | 3.25 | 167.25 | 158.25 |  | 4248.15 | 4019.55
AWWA | C207 | E | 4 | 8 | 0.625 | 9 | 7.5 | 1.125 | 228.6 | 190.5 | 28.575
AWWA | C207 | E | 5 | 8 | 0.75 | 10 | 8.5 | 1.188 | 254 | 215.9 | 30.1752
AWWA | C207 | E | 6 | 8 | 0.75 | 11 | 9.5 | 1.313 | 279.4 | 241.3 | 33.3502
AWWA | C207 | E | 8 | 8 | 0.75 | 13.5 | 11.75 | 1.5 | 342.9 | 298.45 | 38.1
AWWA | C207 | E | 10 | 12 | 0.875 | 16 | 14.25 | 1.563 | 406.4 | 361.95 | 39.7002
AWWA | C207 | E | 12 | 12 | 0.875 | 19 | 17 | 1.75 | 482.6 | 431.8 | 44.45
AWWA | C207 | E | 14 | 12 | 1 | 21 | 18.75 | 1.875 | 533.4 | 476.25 | 47.625
AWWA | C207 | E | 16 | 16 | 1 | 23.5 | 21.25 | 2 | 596.9 | 539.75 | 50.8
AWWA | C207 | E | 18 | 16 | 1.125 | 25 | 22.75 | 2.125 | 635 | 577.85 | 53.975
AWWA | C207 | E | 20 | 20 | 1.125 | 27.5 | 25 | 2.375 | 698.5 | 635 | 60.325
AWWA | C207 | E | 22 | 20 | 1.25 | 29.5 | 27.25 | 2.5 | 749.3 | 692.15 | 63.5
AWWA | C207 | E | 24 | 20 | 1.25 | 32 | 29.5 | 2.625 | 812.8 | 749.3 | 66.675
AWWA | C207 | E | 26 | 24 | 1.25 | 34.25 | 31.75 | 2.75 | 869.95 | 806.45 | 69.85
AWWA | C207 | E | 28 | 28 | 1.25 | 36.5 | 34 | 2.75 | 927.1 | 863.6 | 69.85
AWWA | C207 | E | 30 | 28 | 1.25 | 38.75 | 36 | 2.875 | 984.25 | 914.4 | 73.025
AWWA | C207 | E | 32 | 28 | 1.5 | 41.75 | 38.5 | 3 | 1060.45 | 977.9 | 76.2
AWWA | C207 | E | 34 | 32 | 1.5 | 43.75 | 40.5 | 3.05 | 1111.25 | 1028.7 | 77.47
AWWA | C207 | E | 36 | 32 | 1.5 | 46 | 42.75 | 3.209 | 1168.4 | 1085.85 | 81.5086
AWWA | C207 | E | 38 | 32 | 1.5 | 48.75 | 45.25 | 3.394 | 1238.25 | 1149.35 | 86.2076
AWWA | C207 | E | 40 | 36 | 1.5 | 50.75 | 47.25 | 3.533 | 1289.05 | 1200.15 | 89.7382
AWWA | C207 | E | 42 | 36 | 1.5 | 53 | 49.5 | 3.695 | 1346.2 | 1257.3 | 93.853
AWWA | C207 | E | 44 | 40 | 1.5 | 55.25 | 51.75 | 3.857 | 1403.35 | 1314.45 | 97.9678
AWWA | C207 | E | 46 | 40 | 1.5 | 57.25 | 53.75 | 3.997 | 1454.15 | 1365.25 | 101.5238
AWWA | C207 | E | 48 | 44 | 1.5 | 59.5 | 56 | 4.159 | 1511.3 | 1422.4 | 105.6386
AWWA | C207 | E | 50 | 44 | 1.75 | 61.75 | 58.25 | 4.327 | 1568.45 | 1479.55 | 109.9058
AWWA | C207 | E | 52 | 44 | 1.75 | 64 | 60.5 | 4.489 | 1625.6 | 1536.7 | 114.0206
AWWA | C207 | E | 54 | 44 | 1.75 | 66.25 | 62.75 | 4.651 | 1682.75 | 1593.85 | 118.1354
AWWA | C207 | E | 60 | 52 | 1.75 | 73 | 69.75 | 5.116 | 1854.2 | 1771.65 | 129.9464
AWWA | C207 | E | 66 | 52 | 1.75 | 80 | 76 | 5.601 | 2032 | 1930.4 | 142.2654
AWWA | C207 | E | 72 | 60 | 1.75 | 86.5 | 82.5 | 6.066 | 2197.1 | 2095.5 | 154.0764
AWWA | C207 | E | 78 | 64 | 2 | 93 | 89 |  | 2362.2 | 2260.6
AWWA | C207 | E | 84 | 64 | 2 | 99.75 | 95.5 |  | 2533.65 | 2425.7
AWWA | C207 | E | 90 | 68 | 2.25 | 106.5 | 102 |  | 2705.1 | 2590.8
AWWA | C207 | E | 96 | 68 | 2.25 | 113.25 | 108.5 |  | 2876.55 | 2755.9
AWWA | C207 | E | 102 | 72 | 2.5 | 120 | 114.5 |  | 3048 | 2908.3
AWWA | C207 | E | 108 | 72 | 2.5 | 126.75 | 120.75 |  | 3219.45 | 3067.05
AWWA | C207 | E | 114 | 76 | 2.75 | 133.5 | 126.75 |  | 3390.9 | 3219.45
AWWA | C207 | E | 120 | 76 | 2.75 | 140.25 | 132.75 |  | 3562.35 | 3371.85
AWWA | C207 | E | 126 | 80 | 3 | 147 | 139.25 |  | 3733.8 | 3536.95
AWWA | C207 | E | 132 | 80 | 3 | 153.75 | 145.75 |  | 3905.25 | 3702.05
AWWA | C207 | E | 144 | 84 | 3.25 | 167.25 | 158.25 |  | 4248.15 | 4019.55
AWWA | C207 | F | 4 | 8 | 0.75 | 10 | 7.88 | 1.13 | 254 | 200.152 | 28.702
AWWA | C207 | F | 5 | 8 | 0.75 | 11 | 9.25 | 1.21 | 279.4 | 234.95 | 30.734
AWWA | C207 | F | 6 | 12 | 0.75 | 12.5 | 10.62 | 1.31 | 317.5 | 269.748 | 33.274
AWWA | C207 | F | 8 | 12 | 0.875 | 15 | 13 | 1.31 | 381 | 330.2 | 33.274
AWWA | C207 | F | 10 | 16 | 1 | 17.5 | 15.25 | 1.5 | 444.5 | 387.35 | 38.1
AWWA | C207 | F | 12 | 16 | 1.125 | 20.5 | 17.75 | 1.63 | 520.7 | 450.85 | 41.402
AWWA | C207 | F | 14 | 20 | 1.125 | 23 | 20.25 | 1.94 | 584.2 | 514.35 | 49.276
AWWA | C207 | F | 16 | 20 | 1.25 | 25.5 | 22.5 | 2.14 | 647.7 | 571.5 | 54.356
AWWA | C207 | F | 18 | 24 | 1.25 | 28 | 24.75 | 2.25 | 711.2 | 628.65 | 57.15
AWWA | C207 | F | 20 | 24 | 1.25 | 30.5 | 27 | 2.33 | 774.7 | 685.8 | 59.182
AWWA | C207 | F | 22 | 24 | 1.255 | 33 | 29.25 | 2.5 | 838.2 | 742.95 | 63.5
AWWA | C207 | F | 24 | 24 | 1.5 | 36 | 32 | 2.69 | 914.4 | 812.8 | 68.326
AWWA | C207 | F | 26 | 28 | 1.75 | 38.25 | 34.5 | 3 | 971.55 | 876.3 | 76.2
AWWA | C207 | F | 28 | 28 | 1.75 | 40.75 | 37 | 3.13 | 1035.05 | 939.8 | 79.502
AWWA | C207 | F | 30 | 28 | 1.75 | 43 | 39.25 | 3.166 | 1092.2 | 996.95 | 80.4164
AWWA | C207 | F | 32 | 28 | 1.75 | 45.25 | 41.5 | 3.332 | 1149.35 | 1054.1 | 84.6328
AWWA | C207 | F | 34 | 28 | 1.75 | 47.5 | 43.5 | 3.475 | 1206.5 | 1104.9 | 88.265
AWWA | C207 | F | 36 | 32 | 2 | 50 | 46 | 3.671 | 1270 | 1168.4 | 93.2434
AWWA | C207 | F | 38 | 32 | 2 | 52.25 | 48 | 3.815 | 1327.15 | 1219.2 | 96.901
AWWA | C207 | F | 40 | 36 | 2 | 54.25 | 50.25 | 3.982 | 1377.95 | 1276.35 | 101.1428
AWWA | C207 | F | 42 | 36 | 2 | 57 | 52.75 | 4.171 | 1447.8 | 1339.85 | 105.9434
AWWA | C207 | F | 44 | 36 | 2 | 59.25 | 55 | 4.338 | 1504.95 | 1397 | 110.1852
AWWA | C207 | F | 46 | 40 | 2 | 61.5 | 57.25 | 4.505 | 1562.1 | 1454.15 | 114.427
AWWA | C207 | F | 48 | 40 | 2 | 65 | 60.75 | 4.781 | 1651 | 1543.05 | 121.4374
ASME | 16.5 | 150 | 0.5 | 4 | 0.625 | 3.5 | 2.38 | 0.38 | 88.9 | 60.452 | 9.652
ASME | 16.5 | 150 | 0.75 | 4 | 0.625 | 3.88 | 2.75 | 0.44 | 98.552 | 69.85 | 11.176
ASME | 16.5 | 150 | 1 | 4 | 0.625 | 4.25 | 3.12 | 0.5 | 107.95 | 79.248 | 12.7
ASME | 16.5 | 150 | 1.25 | 4 | 0.625 | 4.62 | 3.5 | 0.56 | 117.348 | 88.9 | 14.224
ASME | 16.5 | 150 | 1.5 | 4 | 0.625 | 5 | 3.88 | 0.62 | 127 | 98.552 | 15.748
ASME | 16.5 | 150 | 2 | 4 | 0.75 | 6 | 4.75 | 0.69 | 152.4 | 120.65 | 17.526
ASME | 16.5 | 150 | 2.5 | 4 | 0.75 | 7 | 5.5 | 0.81 | 177.8 | 139.7 | 20.574
ASME | 16.5 | 150 | 3 | 4 | 0.75 | 7.5 | 6 | 0.88 | 190.5 | 152.4 | 22.352
ASME | 16.5 | 150 | 3.5 | 8 | 0.75 | 8.5 | 7 | 0.88 | 215.9 | 177.8 | 22.352
ASME | 16.5 | 150 | 4 | 8 | 0.75 | 9 | 7.5 | 0.88 | 228.6 | 190.5 | 22.352
ASME | 16.5 | 150 | 5 | 8 | 0.875 | 10 | 8.5 | 0.88 | 254 | 215.9 | 22.352
ASME | 16.5 | 150 | 6 | 8 | 0.875 | 11 | 9.5 | 0.94 | 279.4 | 241.3 | 23.876
ASME | 16.5 | 150 | 8 | 8 | 0.875 | 13.5 | 11.75 | 1.06 | 342.9 | 298.45 | 26.924
ASME | 16.5 | 150 | 10 | 12 | 1 | 16 | 14.25 | 1.12 | 406.4 | 361.95 | 28.448
ASME | 16.5 | 150 | 12 | 12 | 1 | 19 | 17 | 1.19 | 482.6 | 431.8 | 30.226
ASME | 16.5 | 150 | 14 | 12 | 1.125 | 21 | 18.75 | 1.31 | 533.4 | 476.25 | 33.274
ASME | 16.5 | 150 | 16 | 16 | 1.125 | 23.5 | 21.25 | 1.38 | 596.9 | 539.75 | 35.052
ASME | 16.5 | 150 | 18 | 16 | 1.25 | 25 | 22.75 | 1.5 | 635 | 577.85 | 38.1
ASME | 16.5 | 150 | 20 | 20 | 1.25 | 27.5 | 25 | 1.62 | 698.5 | 635 | 41.148
ASME | 16.5 | 150 | 22 | 20 | 1.375 | 29.5 | 27.25 | 1.75 | 749.3 | 692.15 | 44.45
ASME | 16.5 | 150 | 24 | 20 | 1.375 | 32 | 29.5 | 1.81 | 812.8 | 749.3 | 45.974
ASME | 16.5 | 300 | 0.5 | 4 | 0.625 | 3.75 | 2.62 | 0.5 | 95.25 | 66.548 | 12.7
ASME | 16.5 | 300 | 0.75 | 4 | 0.75 | 4.62 | 3.25 | 0.56 | 117.348 | 82.55 | 14.224
ASME | 16.5 | 300 | 1 | 4 | 0.75 | 4.88 | 3.5 | 0.62 | 123.952 | 88.9 | 15.748
ASME | 16.5 | 300 | 1.25 | 4 | 0.75 | 5.25 | 3.88 | 0.69 | 133.35 | 98.552 | 17.526
ASME | 16.5 | 300 | 1.5 | 4 | 0.875 | 6.12 | 4.5 | 0.75 | 155.448 | 114.3 | 19.05
ASME | 16.5 | 300 | 2 | 8 | 0.75 | 6.5 | 5 | 0.81 | 165.1 | 127 | 20.574
ASME | 16.5 | 300 | 2.5 | 8 | 0.875 | 7.5 | 5.88 | 0.94 | 190.5 | 149.352 | 23.876
ASME | 16.5 | 300 | 3 | 8 | 0.875 | 8.25 | 6.62 | 1.06 | 209.55 | 168.148 | 26.924
ASME | 16.5 | 300 | 3.5 | 8 | 0.875 | 9 | 7.25 | 1.12 | 228.6 | 184.15 | 28.448
ASME | 16.5 | 300 | 4 | 8 | 0.875 | 10 | 7.88 | 1.19 | 254 | 200.152 | 30.226
ASME | 16.5 | 300 | 5 | 8 | 0.875 | 11 | 9.25 | 1.31 | 279.4 | 234.95 | 33.274
ASME | 16.5 | 300 | 6 | 12 | 0.875 | 12.5 | 10.62 | 1.38 | 317.5 | 269.748 | 35.052
ASME | 16.5 | 300 | 8 | 12 | 1 | 15 | 13 | 1.56 | 381 | 330.2 | 39.624
ASME | 16.5 | 300 | 10 | 16 | 1.125 | 17.5 | 15.25 | 1.81 | 444.5 | 387.35 | 45.974
ASME | 16.5 | 300 | 12 | 16 | 1.25 | 20.5 | 17.75 | 1.94 | 520.7 | 450.85 | 49.276
ASME | 16.5 | 300 | 14 | 20 | 1.25 | 23 | 20.25 | 2.06 | 584.2 | 514.35 | 52.324
ASME | 16.5 | 300 | 16 | 20 | 1.375 | 25.5 | 22.5 | 2.19 | 647.7 | 571.5 | 55.626
ASME | 16.5 | 300 | 18 | 24 | 1.375 | 28 | 24.75 | 2.31 | 711.2 | 628.65 | 58.674
ASME | 16.5 | 300 | 20 | 24 | 1.375 | 30.5 | 27 | 2.44 | 774.7 | 685.8 | 61.976
ASME | 16.5 | 300 | 22 | 24 | 1.625 | 33 | 29.25 | 2.56 | 838.2 | 742.95 | 65.024
ASME | 16.5 | 300 | 24 | 24 | 1.625 | 36 | 32 | 2.69 | 914.4 | 812.8 | 68.326
ASME | 16.5 | 400 | 0.5 | (5) | (5) | (5) | (5) | (4) | (5) | (5) | (5)
ASME | 16.5 | 400 | 0.75 | (5) | (5) | (5) | (5) | (4) | (5) | (5) | (5)
ASME | 16.5 | 400 | 1 | (5) | (5) | (5) | (5) | (4) | (5) | (5) | (5)
ASME | 16.5 | 400 | 1.25 | (5) | (5) | (5) | (5) | (4) | (5) | (5) | (5)
ASME | 16.5 | 400 | 1.5 | (5) | (5) | (5) | (5) | (4) | (5) | (5) | (5)
ASME | 16.5 | 400 | 2 | (5) | (5) | (5) | (5) | (4) | (5) | (5) | (5)
ASME | 16.5 | 400 | 2.5 | (5) | (5) | (5) | (5) | (4) | (5) | (5) | (5)
ASME | 16.5 | 400 | 3 | (5) | (5) | (5) | (5) | (4) | (5) | (5) | (5)
ASME | 16.5 | 400 | 3.5 | (5) | (5) | (5) | (5) | (4) | (5) | (5) | (5)
ASME | 16.5 | 400 | 4 | 8 | 1 | 10 | 7.88 | 1.38 | 254 | 200.152 | 35.052
ASME | 16.5 | 400 | 5 | 8 | 1 | 11 | 9.25 | 1.5 | 279.4 | 234.95 | 38.1
ASME | 16.5 | 400 | 6 | 12 | 1 | 12.5 | 10.62 | 1.62 | 317.5 | 269.748 | 41.148
ASME | 16.5 | 400 | 8 | 12 | 1.125 | 15 | 13 | 1.88 | 381 | 330.2 | 47.752
ASME | 16.5 | 400 | 10 | 16 | 1.25 | 17.5 | 15.25 | 2.12 | 444.5 | 387.35 | 53.848
ASME | 16.5 | 400 | 12 | 16 | 1.375 | 20.5 | 17.75 | 2.25 | 520.7 | 450.85 | 57.15
ASME | 16.5 | 400 | 14 | 20 | 1.375 | 23 | 20.25 | 2.38 | 584.2 | 514.35 | 60.452
ASME | 16.5 | 400 | 16 | 20 | 1.5 | 25.5 | 23 | 2.5 | 647.7 | 584.2 | 63.5
ASME | 16.5 | 400 | 18 | 24 | 1.5 | 28 | 24.75 | 2.62 | 711.2 | 628.65 | 66.548
ASME | 16.5 | 400 | 20 | 24 | 1.625 | 30.5 | 27 | 2.75 | 774.7 | 685.8 | 69.85
ASME | 16.5 | 400 | 22 | 24 | 1.75 | 33 | 29.25 | 2.88 | 838.2 | 742.95 | 73.152
ASME | 16.5 | 400 | 24 | 24 | 1.875 | 36 | 32 | 3 | 914.4 | 812.8 | 76.2
ASME | 16.5 | 600 | 0.5 | 4 | 0.625 | 3.75 | 2 | 0.56 | 95.25 | 50.8 | 14.224
ASME | 16.5 | 600 | 0.75 | 4 | 0.75 | 4.62 | 3.25 | 0.62 | 117.348 | 82.55 | 15.748
ASME | 16.5 | 600 | 1 | 4 | 0.75 | 4.88 | 3.5 | 0.69 | 123.952 | 88.9 | 17.526
ASME | 16.5 | 600 | 1.25 | 4 | 0.75 | 5.25 | 3.88 | 0.81 | 133.35 | 98.552 | 20.574
ASME | 16.5 | 600 | 1.5 | 4 | 0.875 | 6.12 | 4.5 | 0.88 | 155.448 | 114.3 | 22.352
ASME | 16.5 | 600 | 2 | 8 | 0.75 | 6.5 | 5 | 1 | 165.1 | 127 | 25.4
ASME | 16.5 | 600 | 2.5 | 8 | 0.875 | 7.5 | 5.88 | 1.12 | 190.5 | 149.352 | 28.448
ASME | 16.5 | 600 | 3 | 8 | 0.875 | 8.25 | 6.62 | 1.25 | 209.55 | 168.148 | 31.75
ASME | 16.5 | 600 | 3.5 | 8 | 1 | 9 | 7.25 | 1.38 | 228.6 | 184.15 | 35.052
ASME | 16.5 | 600 | 4 | 8 | 1 | 10.75 | 8.5 | 1.5 | 273.05 | 215.9 | 38.1
ASME | 16.5 | 600 | 5 | 8 | 1.125 | 13 | 10.5 | 1.75 | 330.2 | 266.7 | 44.45
ASME | 16.5 | 600 | 6 | 12 | 1.125 | 14 | 11.5 | 1.88 | 355.6 | 292.1 | 47.752
ASME | 16.5 | 600 | 8 | 12 | 1.25 | 16.5 | 13.75 | 2.19 | 419.1 | 349.25 | 55.626
ASME | 16.5 | 600 | 10 | 16 | 1.375 | 20 | 17 | 2.5 | 508 | 431.8 | 63.5
ASME | 16.5 | 600 | 12 | 20 | 1.375 | 22 | 19.25 | 2.62 | 558.8 | 488.95 | 66.548
ASME | 16.5 | 600 | 14 | 20 | 1.5 | 23.75 | 20.75 | 2.75 | 603.25 | 527.05 | 69.85
ASME | 16.5 | 600 | 16 | 20 | 1.625 | 27 | 23.75 | 3 | 685.8 | 603.25 | 76.2
ASME | 16.5 | 600 | 18 | 20 | 1.75 | 29.25 | 25.75 | 3.25 | 742.95 | 654.05 | 82.55
ASME | 16.5 | 600 | 20 | 24 | 1.75 | 32 | 28.5 | 3.5 | 812.8 | 723.9 | 88.9
ASME | 16.5 | 600 | 22 | 24 | 1.875 | 34.25 | 30.62 | 3.75 | 869.95 | 777.748 | 95.25
ASME | 16.5 | 600 | 24 | 24 | 2 | 37 | 33 | 4 | 939.8 | 838.2 | 101.6
ASME | 16.5 | 900 | 0.5 | (5) | (5) | (5) | (5) | (4) | (5) | (5) | (5)
ASME | 16.5 | 900 | 0.75 | (5) | (5) | (5) | (5) | (4) | (5) | (5) | (5)
ASME | 16.5 | 900 | 1 | (5) | (5) | (5) | (5) | (4) | (5) | (5) | (5)
ASME | 16.5 | 900 | 1.25 | (5) | (5) | (5) | (5) | (4) | (5) | (5) | (5)
ASME | 16.5 | 900 | 1.5 | (5) | (5) | (5) | (5) | (4) | (5) | (5) | (5)
ASME | 16.5 | 900 | 2 | (5) | (5) | (5) | (5) | (4) | (5) | (5) | (5)
ASME | 16.5 | 900 | 2.5 | (5) | (5) | (5) | (5) | (4) | (5) | (5) | (5)
ASME | 16.5 | 900 | 3 | 8 | 1 | 9.5 | 7.5 | 1.5 | 241.3 | 190.5 | 38.1
ASME | 16.5 | 900 | 4 | 8 | 1.25 | 11.5 | 9.25 | 1.75 | 292.1 | 234.95 | 44.45
ASME | 16.5 | 900 | 5 | 8 | 1.375 | 13.75 | 11 | 2 | 349.25 | 279.4 | 50.8
ASME | 16.5 | 900 | 6 | 12 | 1.25 | 15 | 12.5 | 2.19 | 381 | 317.5 | 55.626
ASME | 16.5 | 900 | 8 | 12 | 1.5 | 18.5 | 15.5 | 2.5 | 469.9 | 393.7 | 63.5
ASME | 16.5 | 900 | 10 | 16 | 1.5 | 21.5 | 18.5 | 2.75 | 546.1 | 469.9 | 69.85
ASME | 16.5 | 900 | 12 | 20 | 1.5 | 24 | 21 | 3.12 | 609.6 | 533.4 | 79.248
ASME | 16.5 | 900 | 14 | 20 | 1.625 | 25.25 | 22 | 3.38 | 641.35 | 558.8 | 85.852
ASME | 16.5 | 900 | 16 | 20 | 1.75 | 27.75 | 24.25 | 3.5 | 704.85 | 615.95 | 88.9
ASME | 16.5 | 900 | 18 | 20 | 2 | 31 | 27 | 4 | 787.4 | 685.8 | 101.6
ASME | 16.5 | 900 | 20 | 20 | 2.125 | 33.75 | 29.5 | 4.25 | 857.25 | 749.3 | 107.95
ASME | 16.5 | 900 | 24 | 20 | 2.625 | 41 | 35.5 | 5.5 | 1041.4 | 901.7 | 139.7
ASME | 16.5 | 1500 | 0.5 | 4 | 0.875 | 4.75 | 3.25 | 0.88 | 120.65 | 82.55 | 22.352
ASME | 16.5 | 1500 | 0.75 | 4 | 0.875 | 5.12 | 3.5 | 1 | 130.048 | 88.9 | 25.4
ASME | 16.5 | 1500 | 1 | 4 | 1 | 5.88 | 4 | 1.12 | 149.352 | 101.6 | 28.448
ASME | 16.5 | 1500 | 1.25 | 4 | 1 | 6.25 | 4.38 | 1.12 | 158.75 | 111.252 | 28.448
ASME | 16.5 | 1500 | 1.5 | 4 | 1.125 | 7 | 4.88 | 1.25 | 177.8 | 123.952 | 31.75
ASME | 16.5 | 1500 | 2 | 8 | 1 | 8.5 | 6.5 | 1.5 | 215.9 | 165.1 | 38.1
ASME | 16.5 | 1500 | 2.5 | 8 | 1.125 | 9.62 | 7.5 | 1.62 | 244.348 | 190.5 | 41.148
ASME | 16.5 | 1500 | 3 | 8 | 1.125 | 10.5 | 8 | 1.88 | 266.7 | 203.2 | 47.752
ASME | 16.5 | 1500 | 4 | 8 | 1.375 | 12.25 | 9.5 | 2.12 | 311.15 | 241.3 | 53.848
ASME | 16.5 | 1500 | 5 | 8 | 1.625 | 14.75 | 11.5 | 2.88 | 374.65 | 292.1 | 73.152
ASME | 16.5 | 1500 | 6 | 12 | 1.5 | 15.5 | 12.5 | 3.25 | 393.7 | 317.5 | 82.55
ASME | 16.5 | 1500 | 8 | 12 | 1.75 | 19 | 15.5 | 3.62 | 482.6 | 393.7 | 91.948
ASME | 16.5 | 1500 | 10 | 12 | 2 | 23 | 19 | 4.25 | 584.2 | 482.6 | 107.95
ASME | 16.5 | 1500 | 12 | 16 | 2.125 | 26.5 | 22.5 | 4.88 | 673.1 | 571.5 | 123.952
ASME | 16.5 | 1500 | 14 | 16 | 2.375 | 29.5 | 25 | 5.25 | 749.3 | 635 | 133.35
ASME | 16.5 | 1500 | 16 | 16 | 2.625 | 32.5 | 27.75 | 5.75 | 825.5 | 704.85 | 146.05
ASME | 16.5 | 1500 | 18 | 16 | 2.875 | 36 | 30.5 | 6.38 | 914.4 | 774.7 | 162.052
ASME | 16.5 | 1500 | 20 | 16 | 3.125 | 38.75 | 32.75 | 7 | 984.25 | 831.85 | 177.8
ASME | 16.5 | 1500 | 24 | 16 | 3.625 | 46 | 39 | 8 | 1168.4 | 990.6 | 203.2
ASME | 16.5 | 2500 | 0.5 | 4 | 0.875 | 5.25 | 3.5 | 1.19 | 133.35 | 88.9 | 30.226
ASME | 16.5 | 2500 | 0.75 | 4 | 0.875 | 5.5 | 3.75 | 1.25 | 139.7 | 95.25 | 31.75
ASME | 16.5 | 2500 | 1 | 4 | 1 | 6.25 | 4.25 | 1.38 | 158.75 | 107.95 | 35.052
ASME | 16.5 | 2500 | 1.25 | 4 | 1.125 | 7.25 | 5.12 | 1.5 | 184.15 | 130.048 | 38.1
ASME | 16.5 | 2500 | 1.5 | 4 | 1.25 | 8 | 5.75 | 1.75 | 203.2 | 146.05 | 44.45
ASME | 16.5 | 2500 | 2 | 8 | 1.125 | 9.25 | 6.75 | 2 | 234.95 | 171.45 | 50.8
ASME | 16.5 | 2500 | 2.5 | 8 | 1.25 | 10.5 | 7.75 | 2.25 | 266.7 | 196.85 | 57.15
ASME | 16.5 | 2500 | 3 | 8 | 1.375 | 12 | 9 | 2.62 | 304.8 | 228.6 | 66.548
ASME | 16.5 | 2500 | 4 | 8 | 1.625 | 14 | 10.75 | 3 | 355.6 | 273.05 | 76.2
ASME | 16.5 | 2500 | 5 | 8 | 1.875 | 16.5 | 12.75 | 3.62 | 419.1 | 323.85 | 91.948
ASME | 16.5 | 2500 | 6 | 8 | 2.125 | 19 | 14.5 | 4.25 | 482.6 | 368.3 | 107.95
ASME | 16.5 | 2500 | 8 | 12 | 2.125 | 21.75 | 17.25 | 5 | 552.45 | 438.15 | 127
ASME | 16.5 | 2500 | 10 | 12 | 2.625 | 26.5 | 21.25 | 6.5 | 673.1 | 539.75 | 165.1
ASME | 16.5 | 2500 | 12 | 12 | 2.875 | 30 | 24.38 | 7.25 | 762 | 619.252 | 184.15
ASME | 16.47 Series A | 400 | 26 | 28 | 1.75 | 38.25 | 34.5 | 3.5 | 971.55 | 876.3 | 88.9
ASME | 16.47 Series A | 400 | 28 | 28 | 1.875 | 40.75 | 37 | 3.75 | 1035.05 | 939.8 | 95.25
ASME | 16.47 Series A | 400 | 30 | 28 | 2 | 43 | 39.25 | 4 | 1092.2 | 996.95 | 101.6
ASME | 16.47 Series A | 400 | 32 | 28 | 2 | 45.25 | 41.5 | 4.25 | 1149.35 | 1054.1 | 107.95
ASME | 16.47 Series A | 400 | 34 | 28 | 2 | 47.5 | 43.5 | 4.38 | 1206.5 | 1104.9 | 111.252
ASME | 16.47 Series A | 400 | 36 | 32 | 2 | 50 | 46 | 4.5 | 1270 | 1168.4 | 114.3
ASME | 16.47 Series A | 400 | 38 | 32 | 1.75 | 47.5 | 44 | 4.88 | 1206.5 | 1117.6 | 123.952
ASME | 16.47 Series A | 400 | 40 | 32 | 1.875 | 50 | 46.25 | 5.12 | 1270 | 1174.75 | 130.048
ASME | 16.47 Series A | 400 | 42 | 32 | 1.875 | 52 | 48.25 | 5.25 | 1320.8 | 1225.55 | 133.35
ASME | 16.47 Series A | 400 | 44 | 32 | 2 | 54.5 | 50.5 | 5.5 | 1384.3 | 1282.7 | 139.7
ASME | 16.47 Series A | 400 | 46 | 36 | 2 | 56.75 | 52.75 | 5.75 | 1441.45 | 1339.85 | 146.05
ASME | 16.47 Series A | 400 | 48 | 28 | 2.25 | 59.5 | 55.25 | 6 | 1511.3 | 1403.35 | 152.4
ASME | 16.47 Series A | 400 | 50 | 32 | 2.25 | 61.75 | 57.5 | 6.19 | 1568.45 | 1460.5 | 157.226
ASME | 16.47 Series A | 400 | 52 | 32 | 2.25 | 63.75 | 59.5 | 6.38 | 1619.25 | 1511.3 | 162.052
ASME | 16.47 Series A | 400 | 54 | 28 | 2.5 | 67 | 62.25 | 6.69 | 1701.8 | 1581.15 | 169.926
ASME | 16.47 Series A | 400 | 56 | 32 | 2.5 | 69 | 64.25 | 6.88 | 1752.6 | 1631.95 | 174.752
ASME | 16.47 Series A | 400 | 58 | 32 | 2.5 | 71 | 66.25 | 7 | 1803.4 | 1682.75 | 177.8
ASME | 16.47 Series A | 400 | 60 | 32 | 2.75 | 74.25 | 69 | 7.31 | 1885.95 | 1752.6 | 185.674
ASME | 16.47 Series A | 600 | 26 | 28 | 1.875 | 40 | 36 | 4.25 | 1016 | 914.4 | 107.95
ASME | 16.47 Series A | 600 | 28 | 28 | 2 | 42.25 | 38 | 4.38 | 1073.15 | 965.2 | 111.252
ASME | 16.47 Series A | 600 | 30 | 28 | 2 | 44.5 | 40.25 | 4.5 | 1130.3 | 1022.35 | 114.3
ASME | 16.47 Series A | 600 | 32 | 28 | 2.25 | 47 | 42.5 | 4.62 | 1193.8 | 1079.5 | 117.348
ASME | 16.47 Series A | 600 | 34 | 28 | 2.25 | 49 | 44.5 | 4.75 | 1244.6 | 1130.3 | 120.65
ASME | 16.47 Series A | 600 | 36 | 28 | 2.5 | 51.75 | 47 | 4.88 | 1314.45 | 1193.8 | 123.952
ASME | 16.47 Series A | 600 | 38 | 28 | 2.25 | 50 | 45.75 | 6 | 1270 | 1162.05 | 152.4
ASME | 16.47 Series A | 600 | 40 | 32 | 2.25 | 52 | 47.75 | 6.25 | 1320.8 | 1212.85 | 158.75
ASME | 16.47 Series A | 600 | 42 | 28 | 2.5 | 55.25 | 50.5 | 6.62 | 1403.35 | 1282.7 | 168.148
ASME | 16.47 Series A | 600 | 44 | 32 | 2.5 | 57.25 | 52.5 | 6.81 | 1454.15 | 1333.5 | 172.974
ASME | 16.47 Series A | 600 | 46 | 32 | 2.5 | 59.5 | 54.75 | 7.06 | 1511.3 | 1390.65 | 179.324
ASME | 16.47 Series A | 600 | 48 | 32 | 2.75 | 62.75 | 57.5 | 7.44 | 1593.85 | 1460.5 | 188.976
ASME | 16.47 Series A | 600 | 50 | 28 | 3 | 65.75 | 60 | 7.75 | 1670.05 | 1524 | 196.85
ASME | 16.47 Series A | 600 | 52 | 32 | 3 | 67.75 | 62 | 8 | 1720.85 | 1574.8 | 203.2
ASME | 16.47 Series A | 600 | 54 | 32 | 3 | 70 | 64.25 | 8.25 | 1778 | 1631.95 | 209.55
ASME | 16.47 Series A | 600 | 56 | 32 | 3.25 | 73 | 66.75 | 8.56 | 1854.2 | 1695.45 | 217.424
ASME | 16.47 Series A | 600 | 58 | 32 | 3.25 | 75 | 68.75 | 8.75 | 1905 | 1746.25 | 222.25
ASME | 16.47 Series A | 600 | 60 | 28 | 3.5 | 78.5 | 71.75 | 9.19 | 1993.9 | 1822.45 | 233.426
ASME | 16.47 Series A | 900 | 26 | 20 | 2.75 | 42.75 | 37.5 | 5.5 | 1085.85 | 952.5 | 139.7
ASME | 16.47 Series A | 900 | 28 | 20 | 3 | 46 | 40.25 | 5.62 | 1168.4 | 1022.35 | 142.748
ASME | 16.47 Series A | 900 | 30 | 20 | 3 | 48.5 | 42.75 | 5.88 | 1231.9 | 1085.85 | 149.352
ASME | 16.47 Series A | 900 | 32 | 20 | 3.25 | 51.75 | 45.5 | 6.25 | 1314.45 | 1155.7 | 158.75
ASME | 16.47 Series A | 900 | 34 | 20 | 3.5 | 55 | 48.25 | 6.5 | 1397 | 1225.55 | 165.1
ASME | 16.47 Series A | 900 | 36 | 20 | 3.5 | 57.5 | 50.75 | 6.75 | 1460.5 | 1289.05 | 171.45
ASME | 16.47 Series A | 900 | 38 | 20 | 3.5 | 57.5 | 50.75 | 7.5 | 1460.5 | 1289.05 | 190.5
ASME | 16.47 Series A | 900 | 40 | 24 | 3.5 | 59.5 | 52.75 | 7.75 | 1511.3 | 1339.85 | 196.85
ASME | 16.47 Series A | 900 | 42 | 24 | 3.5 | 61.5 | 54.75 | 8.12 | 1562.1 | 1390.65 | 206.248
ASME | 16.47 Series A | 900 | 44 | 24 | 3.75 | 64.88 | 57.75 | 8.44 | 1647.952 | 1466.85 | 214.376
ASME | 16.47 Series A | 900 | 46 | 24 | 4 | 68.25 | 60.5 | 8.88 | 1733.55 | 1536.7 | 225.552
ASME | 16.47 Series A | 900 | 48 | 24 | 4 | 70.25 | 62.5 | 9.19 | 1784.35 | 1587.5 | 233.426
ASME | 16.47 Series A | 900 | 50 | … | … | … | … | … | … | … | …
ASME | 16.47 Series A | 900 | 52 | … | … | … | … | … | … | … | …
ASME | 16.47 Series A | 900 | 54 | … | … | … | … | … | … | … | …
ASME | 16.47 Series A | 900 | 56 | … | … | … | … | … | … | … | …
ASME | 16.47 Series A | 900 | 58 | … | … | … | … | … | … | … | …
ASME | 16.47 Series A | 900 | 60 | … | … | … | … | … | … | … | …
ASME | 16.47 Series A | 300 | 26 | 28 | 1.625 | 38.25 | 34.5 | 3.07 | 971.55 | 876.3 | 77.978
ASME | 16.47 Series A | 300 | 28 | 28 | 1.625 | 40.75 | 37 | 3.32 | 1035.05 | 939.8 | 84.328
ASME | 16.47 Series A | 300 | 30 | 28 | 1.75 | 43 | 39.25 | 3.57 | 1092.2 | 996.95 | 90.678
ASME | 16.47 Series A | 300 | 32 | 28 | 1.875 | 45.25 | 41.5 | 3.82 | 1149.35 | 1054.1 | 97.028
ASME | 16.47 Series A | 300 | 34 | 28 | 1.875 | 47.5 | 43.5 | 3.94 | 1206.5 | 1104.9 | 100.076
ASME | 16.47 Series A | 300 | 36 | 32 | 2 | 50 | 46 | 4.07 | 1270 | 1168.4 | 103.378
ASME | 16.47 Series A | 300 | 38 | 32 | 1.5 | 46 | 43 | 4.19 | 1168.4 | 1092.2 | 106.426
ASME | 16.47 Series A | 300 | 40 | 32 | 1.625 | 48.75 | 45.5 | 4.44 | 1238.25 | 1155.7 | 112.776
ASME | 16.47 Series A | 300 | 42 | 32 | 1.625 | 50.75 | 47.5 | 4.63 | 1289.05 | 1206.5 | 117.602
ASME | 16.47 Series A | 300 | 44 | 32 | 1.75 | 53.25 | 49.75 | 4.82 | 1352.55 | 1263.65 | 122.428
ASME | 16.47 Series A | 300 | 46 | 28 | 1.875 | 55.75 | 52 | 5 | 1416.05 | 1320.8 | 127
ASME | 16.47 Series A | 300 | 48 | 32 | 1.875 | 57.75 | 54 | 5.19 | 1466.85 | 1371.6 | 131.826
ASME | 16.47 Series A | 300 | 50 | 32 | 2 | 60.25 | 56.25 | 5.44 | 1530.35 | 1428.75 | 138.176
ASME | 16.47 Series A | 300 | 52 | 32 | 2 | 62.25 | 58.25 | 5.63 | 1581.15 | 1479.55 | 143.002
ASME | 16.47 Series A | 300 | 54 | 28 | 2.25 | 65.25 | 61 | 5.94 | 1657.35 | 1549.4 | 150.876
ASME | 16.47 Series A | 300 | 56 | 28 | 2.25 | 67.25 | 63 | 6 | 1708.15 | 1600.2 | 152.4
ASME | 16.47 Series A | 300 | 58 | 32 | 2.25 | 69.25 | 65 | 6.19 | 1758.95 | 1651 | 157.226
ASME | 16.47 Series A | 300 | 60 | 32 | 1.25 | 71.25 | 67 | 6.38 | 1809.75 | 1701.8 | 162.052
ASME | 16.47 Series A | 150 | 26 | 24 | 1.25 | 34.25 | 31.75 | 2.63 | 869.95 | 806.45 | 66.802
ASME | 16.47 Series A | 150 | 28 | 28 | 1.25 | 36.5 | 34 | 2.75 | 927.1 | 863.6 | 69.85
ASME | 16.47 Series A | 150 | 30 | 28 | 1.25 | 38.75 | 36 | 2.88 | 984.25 | 914.4 | 73.152
ASME | 16.47 Series A | 150 | 32 | 28 | 1.5 | 41.75 | 38.5 | 3.13 | 1060.45 | 977.9 | 79.502
ASME | 16.47 Series A | 150 | 34 | 32 | 1.5 | 43.75 | 40.5 | 3.19 | 1111.25 | 1028.7 | 81.026
ASME | 16.47 Series A | 150 | 36 | 32 | 1.5 | 46 | 42.75 | 3.5 | 1168.4 | 1085.85 | 88.9
ASME | 16.47 Series A | 150 | 38 | 32 | 1.5 | 48.75 | 45.25 | 3.38 | 1238.25 | 1149.35 | 85.852
ASME | 16.47 Series A | 150 | 40 | 36 | 1.5 | 50.75 | 47.25 | 3.5 | 1289.05 | 1200.15 | 88.9
ASME | 16.47 Series A | 150 | 42 | 36 | 1.5 | 53 | 49.5 | 3.75 | 1346.2 | 1257.3 | 95.25
ASME | 16.47 Series A | 150 | 44 | 40 | 1.5 | 55.25 | 51.75 | 3.94 | 1403.35 | 1314.45 | 100.076
ASME | 16.47 Series A | 150 | 46 | 40 | 1.5 | 57.25 | 53.75 | 4 | 1454.15 | 1365.25 | 101.6
ASME | 16.47 Series A | 150 | 48 | 44 | 1.5 | 59.5 | 56 | 4.19 | 1511.3 | 1422.4 | 106.426
ASME | 16.47 Series A | 150 | 50 | 44 | 1.75 | 67.75 | 58.25 | 4.32 | 1720.85 | 1479.55 | 109.728
ASME | 16.47 Series A | 150 | 52 | 44 | 1.75 | 64 | 60.5 | 4.5 | 1625.6 | 1536.7 | 114.3
ASME | 16.47 Series A | 150 | 54 | 44 | 1.75 | 66.25 | 62.75 | 4.69 | 1682.75 | 1593.85 | 119.126
ASME | 16.47 Series A | 150 | 56 | 48 | 1.75 | 68.75 | 65 | 4.82 | 1746.25 | 1651 | 122.428
ASME | 16.47 Series A | 150 | 58 | 48 | 1.75 | 71 | 67.25 | 5 | 1803.4 | 1708.15 | 127
ASME | 16.47 Series A | 150 | 60 | 52 | 1.75 | 73 | 69.25 | 5.13 | 1854.2 | 1758.95 | 130.302
ASME | 16.47 Series B | 400 | 26 | 28 | 1.375 | 33.5 | 30.75 | 3.5 | 850.9 | 781.05 | 88.9
ASME | 16.47 Series B | 400 | 28 | 24 | 1.5 | 36 | 33 | 3.75 | 914.4 | 838.2 | 95.25
ASME | 16.47 Series B | 400 | 30 | 28 | 1.5 | 38.25 | 35.25 | 4 | 971.55 | 895.35 | 101.6
ASME | 16.47 Series B | 400 | 32 | 28 | 1.625 | 40.75 | 37.25 | 4.25 | 1035.05 | 946.15 | 107.95
ASME | 16.47 Series B | 400 | 34 | 32 | 1.625 | 42.75 | 39.5 | 4.38 | 1085.85 | 1003.3 | 111.252
ASME | 16.47 Series B | 400 | 36 | 28 | 1.75 | 45.5 | 42 | 4.69 | 1155.7 | 1066.8 | 119.126
ASME | 16.47 Series B | 400 | 38 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 400 | 40 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 400 | 42 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 400 | 44 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 400 | 46 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 400 | 48 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 400 | 50 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 400 | 52 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 400 | 54 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 400 | 56 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 400 | 58 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 400 | 60 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 600 | 26 | 28 | 1.625 | 35 | 31.75 | 4.38 | 889 | 806.45 | 111.252
ASME | 16.47 Series B | 600 | 28 | 28 | 1.75 | 37.5 | 34 | 4.56 | 952.5 | 863.6 | 115.824
ASME | 16.47 Series B | 600 | 30 | 28 | 1.875 | 40.25 | 36.5 | 4.94 | 1022.35 | 927.1 | 125.476
ASME | 16.47 Series B | 600 | 32 | 28 | 2 | 42.75 | 38.75 | 5.12 | 1085.85 | 984.25 | 130.048
ASME | 16.47 Series B | 600 | 34 | 24 | 2.25 | 45.75 | 41.5 | 5.56 | 1162.05 | 1054.1 | 141.224
ASME | 16.47 Series B | 600 | 36 | 28 | 2.25 | 47.75 | 43.5 | 5.75 | 1212.85 | 1104.9 | 146.05
ASME | 16.47 Series B | 600 | 38 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 600 | 40 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 600 | 42 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 600 | 44 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 600 | 46 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 600 | 48 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 600 | 50 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 600 | 52 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 600 | 54 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 600 | 56 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 600 | 58 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 600 | 60 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 900 | 26 | 20 | 2.5 | 40.25 | 35.5 | 5.31 | 1022.35 | 901.7 | 134.874
ASME | 16.47 Series B | 900 | 28 | 20 | 2.75 | 43.5 | 38.25 | 5.81 | 1104.9 | 971.55 | 147.574
ASME | 16.47 Series B | 900 | 30 | 20 | 3 | 46.5 | 40.75 | 6.12 | 1181.1 | 1035.05 | 155.448
ASME | 16.47 Series B | 900 | 32 | 20 | 3 | 48.75 | 43 | 6.31 | 1238.25 | 1092.2 | 160.274
ASME | 16.47 Series B | 900 | 34 | 20 | 3.25 | 51.75 | 45.5 | 6.75 | 1314.45 | 1155.7 | 171.45
ASME | 16.47 Series B | 900 | 36 | 24 | 3 | 53 | 47.25 | 6.81 | 1346.2 | 1200.15 | 172.974
ASME | 16.47 Series B | 900 | 38 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 900 | 40 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 900 | 42 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 900 | 44 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 900 | 46 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 900 | 48 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 900 | 50 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 900 | 52 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 900 | 54 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 900 | 56 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 900 | 58 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 900 | 60 | … | … | … | … | … | … | … | …
ASME | 16.47 Series B | 75 | 26 | 36 | 0.625 | 30 | 28.5 | 1.25 | 762 | 723.9 | 31.75
ASME | 16.47 Series B | 75 | 28 | 40 | 0.625 | 32 | 30.5 | 1.25 | 812.8 | 774.7 | 31.75
ASME | 16.47 Series B | 75 | 30 | 44 | 0.625 | 34 | 32.5 | 1.25 | 863.6 | 825.5 | 31.75
ASME | 16.47 Series B | 75 | 32 | 48 | 0.625 | 36 | 34.5 | 1.32 | 914.4 | 876.3 | 33.528
ASME | 16.47 Series B | 75 | 34 | 52 | 0.625 | 38 | 36.5 | 1.32 | 965.2 | 927.1 | 33.528
ASME | 16.47 Series B | 75 | 36 | 40 | 0.75 | 40.69 | 39.06 | 1.38 | 1033.526 | 992.124 | 35.052
ASME | 16.47 Series B | 75 | 38 | 40 | 0.75 | 42.69 | 41.06 | 1.44 | 1084.326 | 1042.924 | 36.576
ASME | 16.47 Series B | 75 | 40 | 44 | 0.75 | 44.69 | 43.06 | 1.44 | 1135.126 | 1093.724 | 36.576
ASME | 16.47 Series B | 75 | 42 | 48 | 0.75 | 46.69 | 45.06 | 1.5 | 1185.926 | 1144.524 | 38.1
ASME | 16.47 Series B | 75 | 44 | 36 | 0.875 | 49.25 | 47.38 | 1.63 | 1250.95 | 1203.452 | 41.402
ASME | 16.47 Series B | 75 | 46 | 40 | 0.875 | 51.25 | 49.38 | 1.69 | 1301.75 | 1254.252 | 42.926
ASME | 16.47 Series B | 75 | 48 | 44 | 0.875 | 53.25 | 51.38 | 1.75 | 1352.55 | 1305.052 | 44.45
ASME | 16.47 Series B | 75 | 50 | 44 | 0.875 | 55.25 | 53.38 | 1.82 | 1403.35 | 1355.852 | 46.228
ASME | 16.47 Series B | 75 | 52 | 48 | 0.875 | 57.38 | 55.5 | 1.82 | 1457.452 | 1409.7 | 46.228
ASME | 16.47 Series B | 75 | 54 | 48 | 0.875 | 59.38 | 57.5 | 1.88 | 1508.252 | 1460.5 | 47.752
ASME | 16.47 Series B | 75 | 56 | 40 | 1 | 62 | 59.88 | 1.94 | 1574.8 | 1520.952 | 49.276
ASME | 16.47 Series B | 75 | 58 | 44 | 1 | 64 | 61.88 | 2 | 1625.6 | 1571.752 | 50.8
ASME | 16.47 Series B | 75 | 60 | 44 | 1 | 66 | 63.88 | 2.13 | 1676.4 | 1622.552 | 54.102
ASME | 16.47 Series B | 150 | 26 | 36 | 0.75 | 30.94 | 29.31 | 1.57 | 785.876 | 744.474 | 39.878
ASME | 16.47 Series B | 150 | 28 | 40 | 0.75 | 32.94 | 31.31 | 1.69 | 836.676 | 795.274 | 42.926
ASME | 16.47 Series B | 150 | 30 | 44 | 0.75 | 34.94 | 33.31 | 1.69 | 887.476 | 846.074 | 42.926
ASME | 16.47 Series B | 150 | 32 | 48 | 0.75 | 37.06 | 35.44 | 1.75 | 941.324 | 900.176 | 44.45
ASME | 16.47 Series B | 150 | 34 | 40 | 0.875 | 39.56 | 37.69 | 1.88 | 1004.824 | 957.326 | 47.752
ASME | 16.47 Series B | 150 | 36 | 44 | 0.875 | 41.62 | 39.75 | 2 | 1057.148 | 1009.65 | 50.8
ASME | 16.47 Series B | 150 | 38 | 40 | 1 | 44.25 | 42.12 | 2.07 | 1123.95 | 1069.848 | 52.578
ASME | 16.47 Series B | 150 | 40 | 44 | 1 | 46.25 | 44.12 | 2.13 | 1174.75 | 1120.648 | 54.102
ASME | 16.47 Series B | 150 | 42 | 48 | 1 | 48.25 | 46.12 | 2.25 | 1225.55 | 1171.448 | 57.15
ASME | 16.47 Series B | 150 | 44 | 52 | 1 | 50.25 | 48.12 | 2.32 | 1276.35 | 1222.248 | 58.928
ASME | 16.47 Series B | 150 | 46 | 40 | 1.125 | 52.81 | 50.56 | 2.38 | 1341.374 | 1284.224 | 60.452
ASME | 16.47 Series B | 150 | 48 | 44 | 1.125 | 54.81 | 52.56 | 2.5 | 1392.174 | 1335.024 | 63.5
ASME | 16.47 Series B | 150 | 50 | 48 | 1.125 | 56.81 | 54.56 | 2.63 | 1442.974 | 1385.824 | 66.802
ASME | 16.47 Series B | 150 | 52 | 52 | 1.125 | 58.81 | 56.56 | 2.69 | 1493.774 | 1436.624 | 68.326
ASME | 16.47 Series B | 150 | 54 | 56 | 1.125 | 61 | 58.75 | 2.75 | 1549.4 | 1492.25 | 69.85
ASME | 16.47 Series B | 150 | 56 | 60 | 1.125 | 63 | 60.75 | 2.82 | 1600.2 | 1543.05 | 71.628
ASME | 16.47 Series B | 150 | 58 | 48 | 1.25 | 65.94 | 63.44 | 2.88 | 1674.876 | 1611.376 | 73.152
ASME | 16.47 Series B | 150 | 60 | 52 | 1.25 | 67.94 | 65.44 | 2.94 | 1725.676 | 1662.176 | 74.676
ASME | 16.47 Series B | 300 | 26 | 32 | 1.25 | 34.12 | 31.62 | 3.44 | 866.648 | 803.148 | 87.376
ASME | 16.47 Series B | 300 | 28 | 36 | 1.25 | 36.25 | 33.75 | 3.44 | 920.75 | 857.25 | 87.376
ASME | 16.47 Series B | 300 | 30 | 36 | 1.375 | 39 | 36.25 | 3.63 | 990.6 | 920.75 | 92.202
ASME | 16.47 Series B | 300 | 32 | 32 | 1.5 | 41.5 | 38.5 | 4 | 1054.1 | 977.9 | 101.6
ASME | 16.47 Series B | 300 | 34 | 36 | 1.5 | 43.62 | 40.62 | 4 | 1107.948 | 1031.748 | 101.6
ASME | 16.47 Series B | 300 | 36 | 32 | 1.625 | 46.12 | 42.88 | 4 | 1171.448 | 1089.152 | 101.6
ASME | 16.47 Series B | 300 | 38 | 36 | 1.625 | 48.12 | 44.88 | 4.31 | 1222.248 | 1139.952 | 109.474
ASME | 16.47 Series B | 300 | 40 | 40 | 1.625 | 50.12 | 46.88 | 4.5 | 1273.048 | 1190.752 | 114.3
ASME | 16.47 Series B | 300 | 42 | 36 | 1.75 | 52.5 | 49 | 4.63 | 1333.5 | 1244.6 | 117.602
ASME | 16.47 Series B | 300 | 44 | 40 | 1.75 | 54.5 | 51 | 4.94 | 1384.3 | 1295.4 | 125.476
ASME | 16.47 Series B | 300 | 46 | 36 | 1.875 | 57.5 | 53.75 | 5 | 1460.5 | 1365.25 | 127
ASME | 16.47 Series B | 300 | 48 | 40 | 1.875 | 59.5 | 55.75 | 5 | 1511.3 | 1416.05 | 127
ASME | 16.47 Series B | 300 | 50 | 44 | 1.875 | 61.5 | 57.75 | 5.38 | 1562.1 | 1466.85 | 136.652
ASME | 16.47 Series B | 300 | 52 | 48 | 1.875 | 63.5 | 59.75 | 5.56 | 1612.9 | 1517.65 | 141.224
ASME | 16.47 Series B | 300 | 54 | 48 | 1.875 | 65.88 | 62.12 | 5.32 | 1673.352 | 1577.848 | 135.128
ASME | 16.47 Series B | 300 | 56 | 36 | 2.25 | 69.5 | 65 | 6 | 1765.3 | 1651 | 152.4
ASME | 16.47 Series B | 300 | 58 | 40 | 2.25 | 71.94 | 67.44 | 6 | 1827.276 | 1712.976 | 152.4
ASME | 16.47 Series B | 300 | 60 | 40 | 2.25 | 73.94 | 69.44 | 5.88 | 1878.076 | 1763.776 | 149.352
ASME | 16.1 | 25 | 4 | 8 | 0.625 | 9 | 7.5 | 0.75 | 228.6 | 190.5 | 19.05
ASME | 16.1 | 25 | 5 | 8 | 0.625 | 10 | 8.5 | 0.75 | 254 | 215.9 | 19.05
ASME | 16.1 | 25 | 6 | 8 | 0.625 | 11 | 9.5 | 0.75 | 279.4 | 241.3 | 19.05
ASME | 16.1 | 25 | 8 | 8 | 0.625 | 13.5 | 11.75 | 0.75 | 342.9 | 298.45 | 19.05
ASME | 16.1 | 25 | 10 | 12 | 0.625 | 16 | 14.25 | 0.88 | 406.4 | 361.95 | 22.352
ASME | 16.1 | 25 | 12 | 12 | 0.625 | 19 | 17 | 1 | 482.6 | 431.8 | 25.4
ASME | 16.1 | 25 | 14 | 12 | 0.75 | 21 | 18.75 | 1.12 | 533.4 | 476.25 | 28.448
ASME | 16.1 | 25 | 16 | 16 | 0.75 | 23.5 | 21.25 | 1.12 | 596.9 | 539.75 | 28.448
ASME | 16.1 | 25 | 18 | 16 | 0.75 | 25 | 22.75 | 1.25 | 635 | 577.85 | 31.75
ASME | 16.1 | 25 | 20 | 20 | 0.75 | 27.5 | 25 | 1.25 | 698.5 | 635 | 31.75
ASME | 16.1 | 25 | 24 | 20 | 0.75 | 32 | 29.5 | 1.38 | 812.8 | 749.3 | 35.052
ASME | 16.1 | 25 | 30 | 28 | 0.875 | 38.75 | 36 | 1.5 | 984.25 | 914.4 | 38.1
ASME | 16.1 | 25 | 36 | 32 | 0.875 | 46 | 42.75 | 1.62 | 1168.4 | 1085.85 | 41.148
ASME | 16.1 | 25 | 42 | 36 | 1 | 53 | 49.5 | 1.75 | 1346.2 | 1257.3 | 44.45
ASME | 16.1 | 25 | 48 | 44 | 1 | 59.5 | 56 | 2 | 1511.3 | 1422.4 | 50.8
ASME | 16.1 | 25 | 54 | 44 | 1 | 66.25 | 62.75 | 2.25 | 1682.75 | 1593.85 | 57.15
ASME | 16.1 | 25 | 60 | 52 | 1.125 | 73 | 69.25 | 2.25 | 1854.2 | 1758.95 | 57.15
ASME | 16.1 | 25 | 72 | 60 | 1.125 | 86.5 | 82.5 | 2.5 | 2197.1 | 2095.5 | 63.5
ASME | 16.1 | 25 | 84 | 64 | 1.25 | 99.75 | 95.5 | 2.75 | 2533.65 | 2425.7 | 69.85
ASME | 16.1 | 25 | 96 | 68 | 1.25 | 113.25 | 108.5 | 3 | 2876.55 | 2755.9 | 76.2
ASME | 16.1 | 125 | 1 | 4 | 0.5 | 4.25 | 3.12 | 0.44 | 107.95 | 79.248 | 11.176
ASME | 16.1 | 125 | 1.25 | 4 | 0.5 | 4.62 | 3.5 | 0.5 | 117.348 | 88.9 | 12.7
ASME | 16.1 | 125 | 1.5 | 4 | 0.5 | 5 | 3.88 | 0.56 | 127 | 98.552 | 14.224
ASME | 16.1 | 125 | 2 | 4 | 0.625 | 6 | 4.75 | 0.62 | 152.4 | 120.65 | 15.748
ASME | 16.1 | 125 | 2.5 | 4 | 0.625 | 7 | 5.5 | 0.69 | 177.8 | 139.7 | 17.526
ASME | 16.1 | 125 | 3 | 4 | 0.625 | 7.5 | 6 | 0.75 | 190.5 | 152.4 | 19.05
ASME | 16.1 | 125 | 3.5 | 8 | 0.625 | 8.5 | 7 | 0.81 | 215.9 | 177.8 | 20.574
ASME | 16.1 | 125 | 4 | 8 | 0.625 | 9 | 7.5 | 0.94 | 228.6 | 190.5 | 23.876
ASME | 16.1 | 125 | 5 | 8 | 0.75 | 10 | 8.5 | 0.94 | 254 | 215.9 | 23.876
ASME | 16.1 | 125 | 6 | 8 | 0.75 | 11 | 9.5 | 1 | 279.4 | 241.3 | 25.4
ASME | 16.1 | 125 | 8 | 8 | 0.75 | 13.5 | 11.75 | 1.12 | 342.9 | 298.45 | 28.448
ASME | 16.1 | 125 | 10 | 12 | 0.875 | 16 | 14.25 | 1.19 | 406.4 | 361.95 | 30.226
ASME | 16.1 | 125 | 12 | 12 | 0.875 | 19 | 17 | 1.25 | 482.6 | 431.8 | 31.75
ASME | 16.1 | 125 | 14 | 12 | 1 | 14 | 18.75 | 1.38 | 355.6 | 476.25 | 35.052
ASME | 16.1 | 125 | 16 | 16 | 1 | 23.5 | 21.25 | 1.44 | 596.9 | 539.75 | 36.576
ASME | 16.1 | 125 | 18 | 16 | 1.125 | 25 | 22.75 | 1.56 | 635 | 577.85 | 39.624
ASME | 16.1 | 125 | 20 | 20 | 1.125 | 27.5 | 25 | 1.69 | 698.5 | 635 | 42.926
ASME | 16.1 | 125 | 24 | 20 | 1.25 | 32 | 29.5 | 1.88 | 812.8 | 749.3 | 47.752
ASME | 16.1 | 125 | 30 | 28 | 1.25 | 38.75 | 36 | 2.12 | 984.25 | 914.4 | 53.848
ASME | 16.1 | 125 | 36 | 32 | 1.5 | 46 | 42.75 | 2.38 | 1168.4 | 1085.85 | 60.452
ASME | 16.1 | 125 | 42 | 36 | 1.5 | 53 | 49.5 | 2.62 | 1346.2 | 1257.3 | 66.548
ASME | 16.1 | 125 | 48 | 44 | 1.5 | 59.5 | 56 | 2.75 | 1511.3 | 1422.4 | 69.85
ASME | 16.1 | 125 | 54 (9) | 44 | 1.75 | 66.25 | 62.75 | 3 | 1682.75 | 1593.85 | 76.2
ASME | 16.1 | 125 | 60 (9) | 52 | 1.75 | 73 | 69.25 | 3.12 | 1854.2 | 1758.95 | 79.248
ASME | 16.1 | 125 | 66 (9) | 52 | 1.75 | 80 | 76 | 3.38 | 2032 | 1930.4 | 85.852
ASME | 16.1 | 125 | 72 (9) | 60 | 1.75 | 86.5 | 82.5 | 3.5 | 2197.1 | 2095.5 | 88.9
ASME | 16.1 | 125 | 78 (9) | 64 | 2 | 93 | 89 | 3.75 | 2362.2 | 2260.6 | 95.25
ASME | 16.1 | 125 | 84 (9) | 64 | 2 | 99.75 | 95.5 | 3.88 | 2533.65 | 2425.7 | 98.552
ASME | 16.1 | 125 | 90 (9) | 68 | 2.25 | 106.5 | 102 | 4.12 | 2705.1 | 2590.8 | 104.648
ASME | 16.1 | 125 | 96 (9) | 68 | 2.25 | 113.25 | 108.5 | 4.25 | 2876.55 | 2755.9 | 107.95
ASME | 16.1 | 250 | 1 | 4 | 0.62 | 4.88 | 3.5 | 0.69 | 123.952 | 88.9 | 17.526
ASME | 16.1 | 250 | 1.25 | 4 | 0.62 | 5.25 | 3.88 | 0.75 | 133.35 | 98.552 | 19.05
ASME | 16.1 | 250 | 1.5 | 4 | 0.75 | 6.12 | 4.5 | 0.81 | 155.448 | 114.3 | 20.574
ASME | 16.1 | 250 | 2 | 8 | 0.62 | 6.5 | 5 | 0.88 | 165.1 | 127 | 22.352
ASME | 16.1 | 250 | 2.5 | 8 | 0.75 | 7.5 | 5.88 | 1 | 190.5 | 149.352 | 25.4
ASME | 16.1 | 250 | 3 | 8 | 0.75 | 8.25 | 6.62 | 1.12 | 209.55 | 168.148 | 28.448
ASME | 16.1 | 250 | 3.5 | 8 | 0.75 | 9 | 7.25 | 1.19 | 228.6 | 184.15 | 30.226
ASME | 16.1 | 250 | 4 | 8 | 0.75 | 10 | 7.88 | 1.25 | 254 | 200.152 | 31.75
ASME | 16.1 | 250 | 5 | 8 | 0.75 | 11 | 9.25 | 1.38 | 279.4 | 234.95 | 35.052
ASME | 16.1 | 250 | 6 | 12 | 0.75 | 12.5 | 10.62 | 1.44 | 317.5 | 269.748 | 36.576
ASME | 16.1 | 250 | 8 | 12 | 0.88 | 15 | 13 | 1.62 | 381 | 330.2 | 41.148
ASME | 16.1 | 250 | 10 | 16 | 1 | 17.5 | 15.25 | 1.88 | 444.5 | 387.35 | 47.752
ASME | 16.1 | 250 | 12 | 16 | 1.12 | 20.5 | 17.75 | 2 | 520.7 | 450.85 | 50.8
ASME | 16.1 | 250 | 14 | 20 | 1.12 | 23 | 20.25 | 2.12 | 584.2 | 514.35 | 53.848
ASME | 16.1 | 250 | 16 | 20 | 1.25 | 25 | 22.5 | 2.25 | 635 | 571.5 | 57.15
ASME | 16.1 | 250 | 18 | 24 | 1.25 | 28 | 24.75 | 2.38 | 711.2 | 628.65 | 60.452
ASME | 16.1 | 250 | 20 | 24 | 1.25 | 30.5 | 27 | 2.5 | 774.7 | 685.8 | 63.5
ASME | 16.1 | 250 | 24 | 24 | 1.5 | 36 | 32 | 2.75 | 914.4 | 812.8 | 69.85
ASME | 16.1 | 250 | 30 | 28 | 1.75 | 43 | 39.25 | 3 | 1092.2 | 996.95 | 76.2
ASME | 16.1 | 250 | 36 (10) | 32 | 2 | 50 | 46 | 3.38 | 1270 | 1168.4 | 85.852
ASME | 16.1 | 250 | 42 (10) | 36 | 2 | 57 | 52.75 | 3.69 | 1447.8 | 1339.85 | 93.726
ASME | 16.1 | 250 | 48 (10) | 40 | 2 | 65 | 60.75 | 4 | 1651 | 1543.05 | 101.6

## For reference only
AWWA C207 | Hub Flange |  | TRUE |  |  |  | TRUE | [5 empty] | TRUE |  |  |  | TRUE |  | TRUE | [33 empty] | TRUE
ASME 16.1 | Raised Face |  | TRUE | [9 empty] | TRUE | [10 empty] | TRUE | [6 empty] | TRUE | [32 empty] | TRUE | TRUE |  | TRUE | TRUE |  |  |  |  | TRUE | TRUE |  | TRUE | TRUE
ASME 16.47 Series A&B (300,150,75) | Raised Face |  | TRUE |  |  |  |  | TRUE |  |  |  |  | TRUE | [10 empty] | TRUE |  | TRUE |  |  |  |  | TRUE | [19 empty] | TRUE |  | TRUE |  | TRUE | TRUE |  | TRUE | TRUE | TRUE |  | TRUE | TRUE
ASME 16.47 Series A&B (400,600,900) | Raised Face |  | TRUE | [9 empty] | TRUE | [10 empty] | TRUE | [6 empty] | TRUE | [18 empty] | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE
ASME 16.5 | Raised Face- Slip On Welding |  | TRUE | [7 empty] | TRUE |  | TRUE |  | TRUE | [8 empty] | TRUE | [19 empty] | TRUE |  |  | TRUE
ASME 16.5 | Raised Face- Threaded |  | TRUE | [7 empty] | TRUE |  | TRUE |  | TRUE |  |  | TRUE | [5 empty] | TRUE |  |  |  |  | TRUE |  | TRUE |  | TRUE |  |  | TRUE | [5 empty] | TRUE | TRUE | TRUE |  |  | TRUE
ASME 16.5 | Raised Face- Socket Welding |  | TRUE | TRUE |  |  |  | TRUE |  | TRUE | TRUE | TRUE | TRUE |  | TRUE |  |  |  | TRUE |  | TRUE |  | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE |  | TRUE | [5 empty] | TRUE |  | TRUE |  | TRUE
ASME 16.5 | Raised Face- Slip On Weld |  | TRUE | TRUE |  |  |  | TRUE |  | TRUE | TRUE | TRUE | TRUE |  | TRUE |  |  |  | TRUE |  |  |  |  | TRUE | TRUE | TRUE |  | TRUE | TRUE |  | TRUE |  | TRUE |  |  |  | TRUE
ASME 16.5 | Raised Face- Threaded |  | TRUE | TRUE |  |  |  | TRUE |  | TRUE | TRUE | TRUE | TRUE |  | TRUE |  |  | TRUE | [5 empty] | TRUE | TRUE | TRUE |  | TRUE | TRUE |  | TRUE |  | TRUE |  |  | TRUE | [5 empty] | TRUE | TRUE
TYPE | Flange Class | Nominal Pipe Size (NPS) | Outside Diameter Flange (O) | Drilling-Diameter Bolt Circle (W) | Drilling-Diameter Bolt Holes | Drilling-Number of Bolts | Drilling-Bolt Diameter | Stud Bolts (L)-Raised Face (0.06 in) | Stud Bolts (L)-Ring Joint | Machine Bolts (L)-Raised Face (0.06in) | Min Thickness Flange (tf) | Min Thickness Lap Joint (tf) | Diameter of Hub (X) | Diameter Beginning Chamfer Welding Neck (Ah) in | Length Through Hub-Threaded Slip on/Socket Welding (Y) in | Length Through Hub- Lapped (Y) in | Length Through Hub Bore Welding Neck (Y) in | Min Thread Length Threaded (T) in | Bore- Min Slip On Socket Weld (B) in | Bore- Min Lapped (B) in | Bore- Weld Neck/Socket Weld (B) in | Corner Bore Radius of Lapped Flange and Pipe (r) in | Depth of socket (D) in | Outside Diameter Flange (O) mm | Diameter Bolt Circle (W) mm | Stud Bolts (L)- 1.5 mm Raised Face | Stud Bolts (L)-Ring Joint mm | Machine Bolts (L)- 1.5mm Raised Face | Min Thickness Flange (tf) mm | Min Thickness Lap Joint (tf) mm | Diameter of Hub (X) mm | Diameter Beginning Chamfer Welding Neck (Ah) mm | Length through Hub-Threaded/Slip-on/Socket Weld (Y) mm | Length Through Hub- Lapped (Y) mm | Length Through Bore- Welding Neck (Y) mm | Min Thread Length Threaded (T) mm | Bore- Min Slip On Socket Weld (B) mm | Bore- Min Lapped (B) mm | Bore- Weld Neck/Socket Weld (B) mm | Corner Bore Radius of Lapped Flange and Pipe (r) mm | Depth of socket (D) mm | Min Counterbore Threaded Flange (in) | Min Counterbore Threaded Flange (mm) | Length Bolts-Raised Face (0.25 in) (L) | Length Bolts-Ring Joint (L) | Length Bolts-Male and Female (L) | Length Bolts-6.4 mm Raised Face (L) | Length Bolts-Ring Joint (L) | Length Bolts-Male and Female (L) | Length of Bolts (L)- Stud Bolt Raised Face (.25 in) | Hub Diameter Top (A) in. | Raised Face Diameter (R) in. | Min Thickness Flange- WNF (tf) in. | Min Thickness Flange- Blind (tf) in. | Length Through Hub (Y) in. | Min Fillet Radius (r1) in. | Length of Bolts- Stud Bolt Raised Face (6.44mm) | Hub Diameter Top (A) mm | Raised Face Diameter (R) mm | Min Thickness Flange (tf)- WNF mm | Min Thickness Flange (tf)-Blind mm | Length Through Hub (Y) mm | Min Fillet Radius (r1) mm | Min Thickness Flange (Q) in. | Raised Face Diameter (W) in. | Bolt Hole- Diameter Bolt Circle in. | Hub- Min Length (Y) in. | Hub- Min Thread Length (T) in. | Blind Flange- Diameter of Port (I) in. | Blind Flange- Wall Thickness (V) in. | Bolting- Length of Bolts in. | Bolting- Length of Stud Bolts in. | Min Thickness Flange (Q) mm | Raised Face Diameter (W) mm | Bolt Hole- Diameter Bolt Circle mm | Hub- Min Length (Y) mm | Hub- Min Thread Length (T) mm | Blind Flange- Diameter of Port (I) mm | Blind Flange- Wall Thickness (V) mm | Bolting- Length of Bolts mm | Bolting- Length of Stud Bolts mm | Flange Thickness in. | Psi | Max Pressure (psi)
ASME 16.5 | 150 | 0.5 | 3.5 | 2.38 | 0.625 | 4 | 0.5 | 2.25 | … | 2 | 0.38 | 0.44 | 1.19 | 0.84 | 0.56 | 0.62 | 1.81 | 0.62 | 0.88 | 0.9 | 0.62 | 0.12 | 0.38 | 89 | 60.5 | 55 | … | 50 | 9.7 | 11.2 | 30 | 21.3 | 14 | 16 | 46 | 16 | 22.4 | 22.9 | 1.7 | 3 | 10 | N/A | N/A
ASME 16.5 | 150 | 0.75 | 3.88 | 2.75 | 0.625 | 4 | 0.5 | 2.5 | … | 2 | 0.44 | 0.5 | 1.5 | 1.05 | 0.56 | 0.62 | 2 | 0.62 | 1.09 | 1.11 | 0.82 | 0.12 | 0.44 | 99 | 69.8 | 65 | … | 50 | 11.2 | 12.7 | 38 | 26.7 | 14 | 16 | 51 | 16 | 27.7 | 28.2 | 20.8 | 3 | 11 | N/A | N/A
ASME 16.5 | 150 | 1 | 4.25 | 3.12 | 0.625 | 4 | 0.5 | 2.5 | 3 | 2.25 | 0.5 | 0.56 | 1.94 | 1.32 | 0.62 | 0.69 | 2.12 | 0.69 | 1.36 | 1.38 | 1.05 | 0.12 | 0.5 | 108 | 79.2 | 65 | 75 | 55 | 12.7 | 14.2 | 49 | 33.5 | 16 | 18 | 54 | 18 | 34.5 | 35.1 | 26.7 | 3 | 13 | N/A | N/A
ASME 16.5 | 150 | 1.25 | 4.62 | 3.5 | 0.625 | 4 | 0.5 | 2.75 | 3.25 | 2.25 | 0.56 | 0.62 | 2.31 | 1.66 | 0.75 | 0.81 | 2.19 | 0.81 | 1.7 | 1.72 | 1.38 | 0.19 | 0.56 | 117 | 88.9 | 70 | 85 | 55 | 14.2 | 15.7 | 59 | 42.2 | 19 | 21 | 56 | 21 | 43.2 | 43.7 | 35.1 | 5 | 14 | N/A | N/A
ASME 16.5 | 150 | 1.5 | 5 | 3.88 | 0.625 | 4 | 0.5 | 2.75 | 3.25 | 2.5 | 0.62 | 0.69 | 2.56 | 1.9 | 0.81 | 0.88 | 2.83 | 0.88 | 1.95 | 1.97 | 1.61 | 0.25 | 0.62 | 127 | 98.6 | 70 | 85 | 65 | 15.9 | 17.5 | 65 | 48.3 | 21 | 22 | 60 | 22 | 49.5 | 50 | 40.9 | 6 | 16 | N/A | N/A
ASME 16.5 | 150 | 2 | 6 | 4.75 | 0.75 | 4 | 0.625 | 3.25 | 3.75 | 2.75 | 0.69 | 0.75 | 3.06 | 2.38 | 0.94 | 1 | 2.44 | 1 | 2.44 | 2.46 | 2.07 | 0.31 | 0.69 | 152 | 120.6 | 85 | 95 | 70 | 17.5 | 19 | 78 | 60.5 | 24 | 25 | 62 | 25 | 61.9 | 62.5 | 52.6 | 8 | 18 | N/A | N/A
ASME 16.5 | 150 | 2.5 | 7 | 5.5 | 0.75 | 4 | 0.625 | 3.5 | 4 | 3 | 0.81 | 0.88 | 3.56 | 2.88 | 1.06 | 1.12 | 2.69 | 1.12 | 2.94 | 2.97 | 2.47 | 0.31 | 0.75 | 178 | 139.7 | 90 | 100 | 75 | 20.6 | 22.4 | 90 | 73.2 | 27 | 28 | 68 | 28 | 74.7 | 75.4 | 62.7 | 8 | 19 | N/A | N/A
ASME 16.5 | 150 | 3 | 7.5 | 6 | 0.75 | 4 | 0.625 | 3.5 | 4 | 3 | 0.88 | 0.94 | 4.25 | 3.5 | 1.12 | 1.19 | 2.69 | 1.19 | 3.57 | 3.6 | 3.07 | 0.38 | 0.81 | 190 | 152.4 | 90 | 100 | 75 | 22.4 | 23.9 | 108 | 88.9 | 28 | 30 | 68 | 30 | 90.7 | 91.4 | 78 | 10 | 21 | N/A | N/A
ASME 16.5 | 150 | 3.5 | 8.5 | 7 | 0.75 | 8 | 0.625 | 3.5 | 4 | 3 | 0.88 | 0.94 | 4.81 | 4 | 1.19 | 1.25 | 2.75 | 1.25 | 4.07 | 4.1 | 3.55 | 0.38 | … | 216 | 177.8 | 90 | 100 | 75 | 22.4 | 23.9 | 122 | 101.6 | 30 | 32 | 70 | 32 | 103.4 | 104.1 | 90.2 | 10 | … | N/A | N/A
ASME 16.5 | 150 | 4 | 9 | 7.5 | 0.75 | 8 | 0.625 | 3.5 | 4 | 3 | 0.88 | 0.94 | 5.31 | 4.5 | 1.25 | 1.31 | 2.94 | 1.31 | 4.57 | 4.6 | 4.03 | 0.44 | … | 229 | 190.5 | 90 | 100 | 75 | 22.4 | 23.9 | 135 | 114.3 | 32 | 33 | 75 | 33 | 116.1 | 116.8 | 102.4 | 11 | … | N/A | N/A
ASME 16.5 | 150 | 5 | 10 | 8.5 | 0.875 | 8 | 0.75 | 3.75 | 4.25 | 3.25 | 0.88 | 0.94 | 6.44 | 5.56 | 1.38 | 1.44 | 3.44 | 1.44 | 5.66 | 5.69 | 5.05 | 0.44 | … | 254 | 215.9 | 95 | 110 | 85 | 22.4 | 23.9 | 164 | 141.2 | 35 | 37 | 87 | 37 | 143.8 | 144.5 | 128.3 | 11 | … | N/A | N/A
ASME 16.5 | 150 | 6 | 11 | 9.5 | 0.875 | 8 | 0.75 | 4 | 4.5 | 3.25 | 0.94 | 1 | 7.56 | 6.63 | 1.5 | 1.56 | 3.44 | 1.56 | 6.72 | 6.75 | 6.07 | 0.5 | … | 279 | 241.3 | 100 | 115 | 85 | 23.9 | 25.4 | 192 | 168.4 | 38 | 40 | 87 | 40 | 170.7 | 171.4 | 154.2 | 13 | … | N/A | N/A
ASME 16.5 | 150 | 8 | 13.5 | 11.75 | 0.875 | 8 | 0.75 | 4.25 | 4.75 | 3.5 | 1.06 | 1.12 | 9.69 | 8.63 | 1.69 | 1.75 | 3.94 | 1.75 | 8.72 | 8.75 | 7.98 | 0.5 | … | 343 | 298.4 | 110 | 120 | 90 | 26.9 | 28.4 | 246 | 219.2 | 43 | 44 | 100 | 44 | 221.5 | 222.2 | 202.7 | 13 | … | N/A | N/A
ASME 16.5 | 150 | 10 | 16 | 14.25 | 1 | 12 | 0.875 | 4.5 | 5 | 4 | 1.12 | 1.19 | 12 | 10.75 | 1.88 | 1.94 | 3.94 | 1.94 | 10.88 | 10.92 | 10.02 | 0.5 | … | 406 | 362 | 115 | 125 | 100 | 28.4 | 30.2 | 305 | 273 | 48 | 49 | 100 | 49 | 276.4 | 277.4 | 254.5 | 13 | … | N/A | N/A
ASME 16.5 | 150 | 12 | 19 | 17 | 1 | 12 | 0.875 | 4.75 | 5.25 | 4 | 1.19 | 1.25 | 14.38 | 12.75 | 2.12 | 2.19 | 4.44 | 2.19 | 12.88 | 12.92 | 12 | 0.5 | … | 483 | 431.8 | 120 | 135 | 100 | 30.2 | 31.8 | 365 | 323.8 | 54 | 56 | 113 | 56 | 327.2 | 328.2 | 304.8 | 13 | … | N/A | N/A
ASME 16.5 | 150 | 14 | 21 | 18.75 | 1.125 | 12 | 1 | 5.25 | 5.75 | 4.5 | 1.31 | 1.38 | 15.75 | 14 | 2.19 | 3.12 | 4.94 | 2.25 | 14.14 | 14.18 | (8) | 0.5 | … | 533 | 476.2 | 135 | 145 | 115 | 33.3 | 35.1 | 400 | 355.6 | 56 | 79 | 125 | 57 | 359.2 | 360.2 | (8) | 13 | … | N/A | N/A
ASME 16.5 | 150 | 16 | 23.5 | 21.25 | 1.125 | 16 | 1 | 5.25 | 5.75 | 4.5 | 1.38 | 1.44 | 18 | 16 | 2.44 | 3.44 | 4.94 | 2.5 | 16.16 | 16.19 | (8) | 0.5 | … | 597 | 539.8 | 135 | 145 | 115 | 35.1 | 36.6 | 457 | 406.4 | 62 | 87 | 125 | 64 | 410.5 | 411.2 | (8) | 13 | … | N/A | N/A
ASME 16.5 | 150 | 18 | 25 | 22.75 | 1.25 | 16 | 1.125 | 5.75 | 6.25 | 5 | 1.5 | 1.56 | 19.88 | 18 | 2.62 | 3.81 | 5.44 | 2.69 | 18.18 | 18.2 | (8) | 0.5 | … | 635 | 577.8 | 145 | 160 | 125 | 38.1 | 39.6 | 505 | 457.2 | 67 | 97 | 138 | 68 | 461.8 | 462.3 | (8) | 13 | … | N/A | N/A
ASME 16.5 | 150 | 20 | 27.5 | 25 | 1.25 | 20 | 1.125 | 6.25 | 6.75 | 5.5 | 1.62 | 1.69 | 22 | 20 | 2.81 | 4.06 | 5.62 | 2.88 | 20.2 | 20.25 | (8) | 0.5 | … | 693 | 635 | 160 | 170 | 140 | 41.1 | 42.9 | 559 | 508 | 71 | 103 | 143 | 73 | 513.1 | 514.4 | (8) | 13 | … | N/A | N/A
ASME 16.5 | 150 | 22 | 29.5 | 27.25 | 1.375 | 20 | 1.25 | 6.75 | 7.25 | 6 | 1.75 | 1.81 | 24 | 22 | 3.06 | 4.25 | 5.82 | … | 22.22 | 22.25 | (8) | 0.5 | … | 749 | 692.2 | 170 | 185 | 150 | 44.4 | 46 | 610 | 558.8 | 78 | 108 | 148 | … | 564.4 | 565.2 | (8) | 13 | … | N/A | N/A
ASME 16.5 | 150 | 24 | 32 | 29.5 | 1.375 | 20 | 1.25 | 6.75 | 7.25 | 6 | 1.81 | 1.88 | 26.12 | 24 | 3.19 | 4.38 | 5.94 | 3.25 | 24.25 | 24.25 | (8) | 0.5 | … | 813 | 749.3 | 170 | 185 | 150 | 46 | 47.8 | 663 | 609.6 | 81 | 111 | 151 | 83 | 616 | 616 | (8) | 13 | … | N/A | N/A
ASME 16.5 | 300 | 0.5 | 3.75 | 2.62 | 0.625 | 4 | 0.5 | 2.5 | 3 | 2.25 | 0.5 | 0.56 | 1.5 | 0.84 | 0.81 | 0.88 | 2 | 0.62 | 0.88 | 0.9 | 0.62 | 0.12 | 0.38 | 95 | 66.5 | 65 | 75 | 55 | 12.7 | 14.2 | 38 | 21.3 | 21 | 22 | 51 | 16 | 22.4 | 22.9 | 15.7 | 3 | 10 | 0.93 | 23.6
ASME 16.5 | 300 | 0.75 | 4.62 | 3.25 | 0.75 | 4 | 0.625 | 3 | 3.5 | 2.5 | 0.56 | 0.62 | 1.88 | 1.05 | 0.94 | 1 | 2.19 | 0.62 | 1.09 | 1.11 | 0.82 | 0.12 | 0.44 | 117 | 82.6 | 75 | 90 | 65 | 14.2 | 15.7 | 48 | 26.7 | 24 | 25 | 56 | 16 | 27.7 | 28.2 | 20.8 | 3 | 11 | 1.14 | 29
ASME 16.5 | 300 | 1 | 4.88 | 3.5 | 0.75 | 4 | 0.625 | 3 | 3.5 | 2.5 | 0.62 | 0.69 | 2.12 | 1.32 | 1 | 1.06 | 2.38 | 0.69 | 1.36 | 1.38 | 1.05 | 0.12 | 0.5 | 124 | 88.9 | 75 | 90 | 65 | 15.7 | 17.5 | 54 | 33.5 | 25 | 27 | 60 | 18 | 34.5 | 35.1 | 26.7 | 3 | 13 | 1.41 | 35.8
ASME 16.5 | 300 | 1.25 | 5.25 | 3.88 | 0.75 | 4 | 0.625 | 3.25 | 3.75 | 2.75 | 0.69 | 0.75 | 2.5 | 1.66 | 1 | 1.06 | 2.5 | 0.81 | 1.7 | 1.72 | 1.38 | 0.19 | 0.56 | 133 | 98.6 | 85 | 95 | 70 | 17.5 | 19 | 64 | 42.2 | 25 | 27 | 64 | 21 | 43.2 | 43.7 | 35.1 | 5 | 14 | 1.75 | 44.4
ASME 16.5 | 300 | 1.5 | 6.12 | 4.5 | 0.875 | 4 | 0.75 | 3.5 | 4 | 3 | 0.75 | 0.81 | 2.75 | 1.9 | 1.13 | 1.16 | 2.63 | 0.88 | 1.95 | 1.97 | 1.61 | 0.25 | 0.62 | 155 | 114.3 | 90 | 100 | 75 | 19 | 20.6 | 70 | 48.3 | 29 | 30 | 67 | 22 | 49.5 | 50 | 40.9 | 6 | 16 | 1.98 | 50.3
ASME 16.5 | 300 | 2 | 6.5 | 5 | 0.75 | 8 | 0.625 | 3.5 | 4 | 3 | 0.81 | 0.88 | 3.31 | 2.38 | 1.25 | 1.31 | 2.69 | 1.12 | 2.44 | 2.46 | 2.07 | 0.31 | 0.69 | 165 | 127 | 90 | 100 | 75 | 20.6 | 22.4 | 84 | 60.5 | 32 | 33 | 68 | 28 | 62 | 62.5 | 52.6 | 8 | 17 | 2.5 | 63.5
ASME 16.5 | 300 | 2.5 | 7.5 | 5.88 | 0.875 | 8 | 0.75 | 4 | 4.5 | 3.25 | 0.94 | 1 | 3.94 | 2.88 | 1.44 | 1.5 | 2.94 | 1.25 | 2.94 | 2.97 | 2.47 | 0.31 | 0.75 | 190 | 149.4 | 100 | 115 | 85 | 23.9 | 25.4 | 100 | 73.2 | 37 | 38 | 75 | 32 | 74.7 | 75.4 | 62.7 | 8 | 19 | 3 | 76.2
ASME 16.5 | 300 | 3 | 8.25 | 6.62 | 0.875 | 8 | 0.75 | 4.25 | 4.75 | 3.5 | 1.06 | 1.12 | 4.62 | 3.5 | 1.63 | 1.69 | 3.06 | 1.25 | 3.57 | 3.6 | 3.07 | 0.38 | 0.81 | 210 | 168.1 | 110 | 120 | 90 | 26.9 | 28.4 | 117 | 88.9 | 41 | 43 | 78 | 32 | 90.7 | 91.4 | 78 | 10 | 21 | 3.63 | 92.2
ASME 16.5 | 300 | 3.5 | 9 | 7.25 | 0.875 | 8 | 0.75 | 4.25 | 5 | 3.75 | 1.12 | 1.19 | 5.25 | 4 | 1.69 | 1.75 | 3.13 | 1.44 | 4.07 | 4.1 | 3.55 | 0.38 | … | 229 | 184.2 | 110 | 125 | 95 | 28.4 | 30.2 | 133 | 101.6 | 43 | 44 | 80 | 37 | 103.4 | 104.1 | 90.2 | 10 | … | 4.13 | 104.9
ASME 16.5 | 300 | 4 | 10 | 7.88 | 0.875 | 8 | 0.75 | 4.5 | 5 | 3.75 | 1.19 | 1.25 | 5.75 | 4.5 | 1.82 | 1.88 | 3.32 | 1.44 | 4.57 | 4.6 | 4.03 | 0.44 | … | 254 | 200.2 | 115 | 125 | 95 | 30.2 | 31.8 | 146 | 114.3 | 46 | 48 | 84 | 37 | 116.1 | 116.8 | 102.4 | 11 | … | 4.63 | 117.6
ASME 16.5 | 300 | 5 | 11 | 9.25 | 0.875 | 8 | 0.75 | 4.75 | 5.25 | 4.25 | 1.31 | 1.38 | 7 | 5.56 | 1.94 | 2 | 3.82 | 1.69 | 5.66 | 5.69 | 5.05 | 0.44 | … | 279 | 235 | 120 | 135 | 110 | 33.3 | 35.1 | 178 | 141.2 | 49 | 51 | 97 | 43 | 143.8 | 144.5 | 128.3 | 11 | … | 5.69 | 144.5
ASME 16.5 | 300 | 6 | 12.5 | 10.62 | 0.875 | 12 | 0.75 | 4.75 | 5.5 | 4.25 | 1.38 | 1.44 | 8.12 | 6.63 | 2 | 2.06 | 3.82 | 1.81 | 6.72 | 6.75 | 6.07 | 0.5 | … | 318 | 269.7 | 120 | 140 | 110 | 35.1 | 36.6 | 206 | 168.4 | 51 | 52 | 97 | 46 | 170.7 | 171.4 | 154.2 | 13 | … | 6.75 | 171.4
ASME 16.5 | 300 | 8 | 15 | 13 | 1 | 12 | 0.875 | 5.5 | 6 | 4.75 | 1.56 | 1.62 | 10.25 | 8.63 | 2.38 | 2.44 | 4.32 | 2 | 8.72 | 8.75 | 7.98 | 0.5 | … | 381 | 330.2 | 140 | 150 | 120 | 39.6 | 41.1 | 260 | 219.2 | 60 | 62 | 110 | 51 | 221.5 | 222.2 | 202.7 | 13 | … | 8.75 | 222.2
ASME 16.5 | 300 | 10 | 17.5 | 15.25 | 1.125 | 16 | 1 | 6.25 | 6.75 | 5.5 | 1.81 | 1.88 | 12.62 | 10.75 | 2.56 | 3.75 | 4.56 | 2.19 | 10.88 | 10.92 | 10.02 | 0.5 | … | 444 | 387.4 | 160 | 170 | 140 | 46 | 47.8 | 321 | 273 | 65 | 95 | 116 | 56 | 276.4 | 277.4 | 254.5 | 13 | … | 10.88 | 276.4
ASME 16.5 | 300 | 12 | 20.5 | 17.75 | 1.25 | 16 | 1.125 | 6.75 | 7.25 | 5.75 | 1.94 | 2 | 14.75 | 12.75 | 2.82 | 4 | 5.06 | 2.38 | 12.88 | 12.92 | 12 | 0.5 | … | 521 | 450.8 | 170 | 185 | 145 | 49.3 | 50.8 | 375 | 323.8 | 72 | 102 | 129 | 60 | 327.2 | 328.2 | 304.8 | 13 | … | 12.94 | 328.7
ASME 16.5 | 300 | 14 | 23 | 20.25 | 1.25 | 20 | 1.125 | 7 | 7.5 | 6.25 | 2.06 | 2.12 | 16.75 | 14 | 2.94 | 4.38 | 5.56 | 2.5 | 14.14 | 14.18 | (7) | 0.5 | … | 584 | 514.4 | 180 | 190 | 160 | 52.3 | 53.8 | 425 | 355.6 | 75 | 111 | 141 | 64 | 359.2 | 360.2 | (7) | 13 | … | 14.19 | 360.4
ASME 16.5 | 300 | 16 | 25.5 | 22.5 | 1.375 | 20 | 1.25 | 7.5 | 8 | 6.5 | 2.19 | 2.25 | 19 | 16 | 3.19 | 4.75 | 5.69 | 2.69 | 16.16 | 16.19 | (7) | 0.5 | … | 648 | 571.5 | 190 | 205 | 165 | 55.6 | 57.2 | 483 | 406.4 | 81 | 121 | 145 | 68 | 410.5 | 411.2 | (7) | 13 | … | 16.19 | 411.2
ASME 16.5 | 300 | 18 | 28 | 24.75 | 1.375 | 24 | 1.25 | 7.75 | 8.25 | 6.75 | 2.31 | 2.38 | 21 | 18 | 3.44 | 5.12 | 6.19 | 2.75 | 18.18 | 18.2 | (7) | 0.5 | … | 711 | 628.6 | 195 | 210 | 170 | 58.7 | 60.5 | 533 | 457.2 | 87 | 130 | 157 | 70 | 461.8 | 462.3 | (7) | 13 | … | 18.19 | 462
ASME 16.5 | 300 | 20 | 30.5 | 27 | 1.375 | 24 | 1.25 | 8 | 8.75 | 7.25 | 2.44 | 2.5 | 23.12 | 20 | 3.69 | 5.5 | 6.32 | 2.88 | 20.2 | 20.25 | (7) | 0.5 | … | 775 | 685.8 | 205 | 220 | 185 | 62 | 63.5 | 587 | 508 | 94 | 140 | 161 | 73 | 513.1 | 514.4 | (7) | 13 | … | 20.19 | 512.8
ASME 16.5 | 300 | 22 | 33 | 29.25 | 1.625 | 24 | 1.5 | 9 | 10 | 8 | 2.56 | 2.62 | 25.25 | 22 | 3.94 | 5.69 | 6.44 | … | 22.22 | 22.25 | (7) | 0.5 | … | 838 | 743 | 230 | 255 | 205 | 65 | 66.5 | 641 | 558.8 | 100 | 145 | 164 | … | 564.4 | 565.2 | (7) | 13 | … | … | …
ASME 16.5 | 300 | 24 | 36 | 32 | 1.625 | 24 | 1.5 | 9 | 10 | 8 | 2.69 | 2.75 | 27.62 | 24 | 4.13 | 6 | 6.56 | 3.25 | 24.25 | 24.25 | (7) | 0.5 | … | 914 | 812.8 | 230 | 255 | 205 | 68.3 | 68.8 | 702 | 609.6 | 105 | 152 | 167 | 83 | 616 | 616 | (7) | 13 | … | 24.19 | 614.4
ASME 16.5 | 400 | 0.5 | (5) | (5) | (5) | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5) | (5) | (5)
ASME 16.5 | 400 | 0.75 | (5) | (5) | (5) | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5) | (5) | (5)
ASME 16.5 | 400 | 1 | (5) | (5) | (5) | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5) | (5) | (5)
ASME 16.5 | 400 | 1.25 | (5) | (5) | (5) | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5) | (5) | (5)
ASME 16.5 | 400 | 1.5 | (5) | (5) | (5) | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5) | (5) | (5)
ASME 16.5 | 400 | 2 | (5) | (5) | (5) | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5) | (5) | (5)
ASME 16.5 | 400 | 2.5 | (5) | (5) | (5) | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5) | (5) | (5)
ASME 16.5 | 400 | 3 | (5) | (5) | (5) | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5) | (5) | (5)
ASME 16.5 | 400 | 3.5 | (5) | (5) | (5) | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5) | (5) | (5)
ASME 16.5 | 400 | 4 | 10 | 7.88 | 1 | 8 | 0.875 |  |  |  | 1.38 | N/A | 5.75 | 4.5 | 2 | 2 | 3.5 | 1.44 | 4.57 | 4.63 | (5) | 0.44 | N/A | 254 | 200.2 |  |  |  | 35.1 | N/A | 146 | 114.3 | 51 | 51 | 89 | 37 | 116.1 | 116.8 | (5) | 11 | N/A | 4.63 | 117.6 | 5.5 | 5.5 | 5.25 | 140 | 140 | 135
ASME 16.5 | 400 | 5 | 11 | 9.25 | 1 | 8 | 0.875 |  |  |  | 1.5 | N/A | 7 | 5.56 | 2.12 | 2.12 | 4 | 1.69 | 5.66 | 5.69 | (5) | 0.44 | N/A | 279 | 235 |  |  |  | 38.1 | N/A | 178 | 141.2 | 54 | 54 | 102 | 43 | 143.8 | 144.5 | (5) | 11 | N/A | 5.69 | 144.5 | 5.75 | 5.75 | 5.25 | 145 | 145 | 135
ASME 16.5 | 400 | 6 | 12.5 | 10.62 | 1 | 12 | 0.875 |  |  |  | 1.62 | N/A | 8.12 | 6.63 | 2.25 | 2.25 | 4.06 | 1.81 | 6.72 | 6.75 | (5) | 0.5 | N/A | 318 | 269.7 |  |  |  | 41.1 | N/A | 206 | 168.4 | 57 | 57 | 103 | 46 | 170.7 | 171.4 | (5) | 13 | N/A | 6.75 | 171.4 | 6 | 6 | 5.75 | 150 | 150 | 145
ASME 16.5 | 400 | 8 | 15 | 13 | 1.125 | 12 | 1 |  |  |  | 1.88 | N/A | 10.25 | 8.63 | 2.69 | 2.69 | 4.62 | 2 | 8.72 | 8.75 | (5) | 0.5 | N/A | 381 | 330.2 |  |  |  | 47.8 | N/A | 260 | 219.2 | 68 | 68 | 117 | 51 | 221.5 | 222.2 | (5) | 13 | N/A | 8.75 | 222.2 | 6.75 | 6.75 | 6.5 | 170 | 170 | 165
ASME 16.5 | 400 | 10 | 17.5 | 15.25 | 1.25 | 16 | 1.125 |  |  |  | 2.12 | N/A | 12.62 | 10.75 | 2.88 | 4 | 4.88 | 2.19 | 10.88 | 10.92 | (5) | 0.5 | N/A | 444 | 387.4 |  |  |  | 53.8 | N/A | 321 | 273 | 73 | 102 | 124 | 56 | 276.4 | 277.4 | (5) | 13 | N/A | 10.88 | 276.4 | 7.5 | 7.5 | 7.25 | 190 | 190 | 185
ASME 16.5 | 400 | 12 | 20.5 | 17.75 | 1.375 | 16 | 1.25 |  |  |  | 2.25 | N/A | 14.75 | 12.75 | 3.12 | 4.25 | 5.38 | 2.38 | 12.88 | 12.92 | (5) | 0.5 | N/A | 521 | 450.8 |  |  |  | 57.2 | N/A | 375 | 323.8 | 79 | 108 | 137 | 60 | 327.2 | 328.2 | (5) | 13 | N/A | 12.94 | 328.7 | 8 | 8 | 7.75 | 205 | 205 | 195
ASME 16.5 | 400 | 14 | 23 | 20.25 | 1.375 | 20 | 1.25 |  |  |  | 2.38 | N/A | 16.75 | 14 | 3.31 | 4.62 | 5.88 | 2.5 | 14.14 | 14.18 | (5) | 0.5 | N/A | 584 | 514.4 |  |  |  | 60.5 | N/A | 425 | 355.6 | 84 | 117 | 149 | 64 | 359.2 | 360.2 | (5) | 13 | N/A | 14.19 | 360.4 | 8.25 | 8.25 | 8 | 210 | 210 | 205
ASME 16.5 | 400 | 16 | 25.5 | 23 | 1.5 | 20 | 1.375 |  |  |  | 2.5 | N/A | 19 | 16 | 3.69 | 5 | 6 | 2.69 | 16.16 | 16.19 | (5) | 0.5 | N/A | 648 | 571.5 |  |  |  | 63.5 | N/A | 483 | 406.4 | 94 | 127 | 152 | 68 | 410.5 | 411.2 | (5) | 13 | N/A | 16.19 | 411.2 | 8.75 | 8.75 | 8.5 | 220 | 220 | 215
ASME 16.5 | 400 | 18 | 28 | 24.75 | 1.5 | 24 | 1.375 |  |  |  | 2.62 | N/A | 21 | 18 | 3.88 | 5.38 | 6.5 | 2.75 | 18.18 | 18.2 | (5) | 0.5 | N/A | 711 | 628.6 |  |  |  | 66.5 | N/A | 533 | 457.2 | 99 | 137 | 165 | 70 | 461.8 | 462.3 | (5) | 13 | N/A | 18.19 | 462 | 9 | 9 | 8.75 | 230 | 230 | 220
ASME 16.5 | 400 | 20 | 30.5 | 27 | 1.625 | 24 | 1.5 |  |  |  | 2.75 | N/A | 23.12 | 20 | 4 | 5.75 | 6.62 | 2.88 | 20.2 | 20.25 | (5) | 0.5 | N/A | 775 | 685.8 |  |  |  | 69.8 | N/A | 587 | 508 | 102 | 146 | 168 | 73 | 513.1 | 514.4 | (5) | 13 | N/A | 20.19 | 512.8 | 9.5 | 9.75 | 9.25 | 240 | 250 | 235
ASME 16.5 | 400 | 22 | 33 | 29.25 | 1.75 | 24 | 1.625 |  |  |  | 2.88 | N/A | 25.25 | 22 | 4.25 | 6 | 6.75 | … | 22.22 | 22.25 | (5) | 0.5 | N/A | 838 | 743 |  |  |  | 73.2 | N/A | 641 | 558.8 | 108 | 152 | 171 | … | 564.4 | 565.2 | (5) | 13 | N/A | … | … | 10 | 10.25 | 9.75 | 255 | 260 | 250
ASME 16.5 | 400 | 24 | 36 | 32 | 1.875 | 24 | 1.75 |  |  |  | 3 | N/A | 27.62 | 24 | 4.5 | 6.25 | 6.88 | 3.25 | 24.25 | 24.25 | (5) | 0.5 | N/A | 914 | 812.8 |  |  |  | 76.2 | N/A | 702 | 609.6 | 114 | 159 | 175 | 83 | 616 | 616 | (5) | 13 | N/A | 24.19 | 614.4 | 10.5 | 11 | 10.25 | 265 | 280 | 260
ASME 16.5 | 600 | 0.5 | 3.75 | 2.62 | 0.625 | 4 | 0.5 |  |  |  | 0.56 | N/A | 1.5 | 0.84 | 0.88 | 0.88 | 2.06 | 0.62 | 0.88 | 0.9 | (4) | 0.12 | 0.38 | 95 | 66.5 |  |  |  | 14.2 | N/A | 38 | 21.3 | 22 | 22 | 52 | 16 | 22.4 | 22.9 | (4) | 3 | 10 | 0.93 | 23.6 | 3 | 3 | 2.75 | 75 | 75 | 70
ASME 16.5 | 600 | 0.75 | 4.62 | 3.25 | 0.75 | 4 | 0.625 |  |  |  | 0.62 | N/A | 1.88 | 1.05 | 1 | 1 | 2.25 | 0.62 | 1.09 | 1.11 | (4) | 0.12 | 0.44 | 117 | 82.6 |  |  |  | 15.7 | N/A | 48 | 26.7 | 25 | 25 | 57 | 16 | 27.7 | 28.2 | (4) | 3 | 11 | 1.14 | 29 | 3.5 | 3.5 | 3.25 | 90 | 90 | 85
ASME 16.5 | 600 | 1 | 4.88 | 3.5 | 0.75 | 4 | 0.625 |  |  |  | 0.69 | N/A | 2.12 | 1.32 | 1.06 | 1.06 | 2.44 | 0.69 | 1.36 | 1.38 | (4) | 0.12 | 0.5 | 124 | 88.9 |  |  |  | 17.5 | N/A | 54 | 33.5 | 27 | 27 | 62 | 18 | 34.5 | 35.1 | (4) | 3 | 13 | 1.41 | 35.8 | 3.5 | 3.5 | 3.25 | 90 | 90 | 85
ASME 16.5 | 600 | 1.25 | 5.25 | 3.88 | 0.75 | 4 | 0.625 |  |  |  | 0.81 | N/A | 2.5 | 1.66 | 1.12 | 1.12 | 2.62 | 0.81 | 1.7 | 1.72 | (4) | 0.19 | 0.56 | 133 | 98.6 |  |  |  | 20.3 | N/A | 64 | 42.2 | 28 | 28 | 67 | 21 | 43.2 | 43.7 | (4) | 5 | 14 | 1.75 | 44.4 | 3.75 | 3.75 | 3.5 | 95 | 95 | 90
ASME 16.5 | 600 | 1.5 | 6.12 | 4.5 | 0.875 | 4 | 0.75 |  |  |  | 0.88 | N/A | 2.75 | 1.9 | 1.25 | 1.25 | 2.75 | 0.88 | 1.95 | 1.97 | (4) | 0.25 | 0.62 | 155 | 114.3 |  |  |  | 22.4 | N/A | 70 | 48.3 | 32 | 32 | 70 | 22 | 49.5 | 50 | (4) | 6 | 16 | 1.99 | 50.5 | 4.25 | 4.25 | 4 | 110 | 110 | 100
ASME 16.5 | 600 | 2 | 6.5 | 5 | 0.75 | 8 | 0.625 |  |  |  | 1 | N/A | 3.31 | 2.38 | 1.44 | 1.44 | 2.88 | 1.12 | 2.44 | 2.46 | (4) | 0.31 | 0.69 | 165 | 127 |  |  |  | 25.4 | N/A | 84 | 60.5 | 37 | 37 | 73 | 28 | 62 | 62.5 | (4) | 8 | 18 | 0.25 | 63.5 | 4.25 | 4.25 | 4 | 110 | 110 | 100
ASME 16.5 | 600 | 2.5 | 7.5 | 5.88 | 0.875 | 8 | 0.75 |  |  |  | 1.12 | N/A | 3.94 | 2.88 | 1.62 | 1.62 | 3.12 | 1.25 | 2.94 | 2.97 | (4) | 0.31 | 0.75 | 190 | 149.4 |  |  |  | 28.4 | N/A | 100 | 73.2 | 41 | 41 | 79 | 32 | 74.7 | 75.4 | (4) | 8 | 19 | 3 | 76.2 | 4.75 | 4.75 | 4.5 | 120 | 120 | 115
ASME 16.5 | 600 | 3 | 8.25 | 6.62 | 0.875 | 8 | 0.75 |  |  |  | 1.25 | N/A | 4.62 | 3.5 | 1.81 | 1.81 | 3.25 | 1.38 | 3.57 | 3.6 | (4) | 0.38 | 0.81 | 210 | 168.1 |  |  |  | 31.8 | N/A | 117 | 88.9 | 46 | 46 | 83 | 35 | 90.7 | 91.4 | (4) | 10 | 21 | 3.63 | 92.2 | 5 | 5 | 4.75 | 125 | 125 | 120
ASME 16.5 | 600 | 3.5 | 9 | 7.25 | 1 | 8 | 0.875 |  |  |  | 1.38 | N/A | 5.25 | 4 | 1.94 | 1.94 | 3.38 | 1.56 | 4.07 | 4.1 | (4) | 0.38 | … | 229 | 184.2 |  |  |  | 35.1 | N/A | 133 | 101.6 | 49 | 49 | 86 | 40 | 103.4 | 104.1 | (4) | 10 | … | 4.13 | 104.9 | 5.5 | 5.5 | 5.25 | 140 | 140 | 135
ASME 16.5 | 600 | 4 | 10.75 | 8.5 | 1 | 8 | 0.875 |  |  |  | 1.5 | N/A | 6 | 4.5 | 2.12 | 2.12 | 4 | 1.62 | 4.57 | 4.6 | (4) | 0.44 | … | 273 | 215.9 |  |  |  | 38.1 | N/A | 152 | 114.3 | 54 | 54 | 102 | 41 | 116.1 | 116.8 | (4) | 11 | … | 4.63 | 117.6 | 5.75 | 5.75 | 5.5 | 145 | 145 | 140
ASME 16.5 | 600 | 5 | 13 | 10.5 | 1.125 | 8 | 1 |  |  |  | 1.75 | N/A | 7.44 | 5.56 | 2.38 | 2.38 | 4.5 | 1.88 | 5.66 | 5.69 | (4) | 0.44 | … | 330 | 266.7 |  |  |  | 44.4 | N/A | 189 | 141.2 | 60 | 60 | 114 | 48 | 143.8 | 144.5 | (4) | 11 | … | 5.69 | 144.5 | 6.5 | 6.5 | 6.25 | 165 | 165 | 160
ASME 16.5 | 600 | 6 | 14 | 11.5 | 1.125 | 12 | 1 |  |  |  | 1.88 | N/A | 8.75 | 6.63 | 2.62 | 2.62 | 4.62 | 2 | 6.72 | 6.75 | (4) | 0.5 | … | 356 | 292.1 |  |  |  | 47.8 | N/A | 222 | 168.4 | 67 | 67 | 117 | 51 | 170.7 | 171.4 | (4) | 13 | … | 6.75 | 171.4 | 6.75 | 6.75 | 6.5 | 170 | 170 | 165
ASME 16.5 | 600 | 8 | 16.5 | 13.75 | 1.25 | 12 | 1.125 |  |  |  | 2.19 | N/A | 10.75 | 8.63 | 3 | 3 | 5.25 | 2.25 | 8.72 | 8.75 | (4) | 0.5 | … | 419 | 349.2 |  |  |  | 55.6 | N/A | 273 | 219.2 | 76 | 76 | 133 | 57 | 221.5 | 222.2 | (4) | 13 | … | 8.75 | 222.2 | 7.5 | 7.75 | 7.25 | 190 | 195 | 185
ASME 16.5 | 600 | 10 | 20 | 17 | 1.375 | 16 | 1.25 |  |  |  | 2.5 | N/A | 13.5 | 10.75 | 3.38 | 4.38 | 6 | 2.56 | 10.88 | 10.92 | (4) | 0.5 | … | 508 | 431.8 |  |  |  | 63.5 | N/A | 343 | 273 | 86 | 111 | 152 | 65 | 276.2 | 277.4 | (4) | 13 | … | 10.88 | 276.4 | 8.5 | 8.5 | 8.25 | 215 | 215 | 210
ASME 16.5 | 600 | 12 | 22 | 19.25 | 1.375 | 20 | 1.25 |  |  |  | 2.62 | N/A | 15.75 | 12.75 | 3.62 | 4.62 | 6.12 | 2.75 | 12.88 | 12.92 | (4) | 0.5 | … | 559 | 489 |  |  |  | 66.5 | N/A | 400 | 323.8 | 92 | 117 | 155 | 70 | 327 | 328.2 | (4) | 13 | … | 12.94 | 328.7 | 8.75 | 8.75 | 8.5 | 220 | 220 | 215
ASME 16.5 | 600 | 14 | 23.75 | 20.75 | 1.5 | 20 | 1.375 |  |  |  | 2.75 | N/A | 17 | 14 | 3.69 | 5 | 6.5 | 2.88 | 14.14 | 14.18 | (4) | 0.5 | … | 603 | 527 |  |  |  | 69.8 | N/A | 432 | 355.6 | 94 | 127 | 165 | 73 | 359.2 | 360.2 | (4) | 13 | … | 14.19 | 360.4 | 9.25 | 9.25 | 9 | 235 | 235 | 230
ASME 16.5 | 600 | 16 | 27 | 23.75 | 1.625 | 20 | 1.5 |  |  |  | 3 | N/A | 19.5 | 16 | 4.19 | 5.5 | 7 | 3.06 | 16.16 | 16.19 | (4) | 0.5 | … | 686 | 603.2 |  |  |  | 76.2 | N/A | 495 | 406.4 | 106 | 140 | 178 | 78 | 410.5 | 411.2 | (4) | 13 | … | 16.19 | 411.2 | 10 | 10 | 9.75 | 255 | 255 | 250
ASME 16.5 | 600 | 18 | 29.25 | 25.75 | 1.75 | 20 | 1.625 |  |  |  | 3.25 | N/A | 21.5 | 18 | 4.62 | 6 | 7.25 | 3.12 | 18.18 | 18.2 | (4) | 0.5 | … | 743 | 654 |  |  |  | 82.6 | N/A | 546 | 457.2 | 117 | 152 | 184 | 79 | 461.8 | 462.3 | (4) | 13 | … | 18.19 | 462 | 10.75 | 10.75 | 10.5 | 275 | 275 | 265
ASME 16.5 | 600 | 20 | 32 | 28.5 | 1.75 | 24 | 1.625 |  |  |  | 3.5 | N/A | 24 | 20 | 5 | 6.5 | 7.5 | 3.25 | 20.2 | 20.25 | (4) | 0.5 | … | 813 | 723.9 |  |  |  | 88.9 | N/A | 610 | 508 | 127 | 165 | 190 | 83 | 513.1 | 514.4 | (4) | 13 | … | 20.19 | 512.8 | 11.25 | 11.5 | 11 | 285 | 290 | 280
ASME 16.5 | 600 | 22 | 34.25 | 30.62 | 1.875 | 24 | 1.75 |  |  |  | 3.75 | N/A | 26.25 | 22 | 5.25 | 6.88 | 7.75 | … | 22.22 | 22.25 | (4) | 0.5 | … | 870 | 777.7 |  |  |  | 95.2 | N/A | 663 | 558.8 | 133 | 175 | 197 | … | 564.4 | 565.2 | (4) | 13 | … | … | … | 12 | 12.25 | … | 305 | 310 | …
ASME 16.5 | 600 | 24 | 37 | 33 | 2 | 24 | 1.875 |  |  |  | 4 | N/A | 28.25 | 24 | 5.5 | 7.25 | 8 | 3.62 | 24.25 | 24.25 | (4) | 0.5 | … | 940 | 838.2 |  |  |  | 101.6 | N/A | 718 | 609.6 | 140 | 184 | 203 | 92 | 616 | 616 | (4) | 13 | … | 24.19 | 614.4 | 13 | 13.25 | 12.75 | 330 | 335 | 325
ASME 16.5 | 900 | 0.5 | (5) | (5) | (5) | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5) | (5) | (5)
ASME 16.5 | 900 | 0.75 | (5) | (5) | (5) | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5) | (5) | (5)
ASME 16.5 | 900 | 1 | (5) | (5) | (5) | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5) | (5) | (5)
ASME 16.5 | 900 | 1.25 | (5) | (5) | (5) | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5) | (5) | (5)
ASME 16.5 | 900 | 1.5 | (5) | (5) | (5) | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5) | (5) | (5)
ASME 16.5 | 900 | 2 | (5) | (5) | (5) | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5) | (5) | (5)
ASME 16.5 | 900 | 2.5 | (5) | (5) | (5) | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5) | (5) | (5)
ASME 16.5 | 900 | 3 | 9.5 | 7.5 | 1 | 8 | 0.875 |  |  |  | 1.5 | N/A | 5 | 3.5 | 2.12 | 2.12 | 4 | 1.62 | 3.57 | 3.6 | (5) | 0.38 | N/A | 241 | 190.5 |  |  |  | 38.1 | N/A | 127 | 88.9 | 54 | 54 | 102 | 41 | 90.7 | 91.4 | (5) | 10 | N/A | 3.63 | 92.2 | 5.75 | 5.5 | 5.75 | 145 | 140 | 145
ASME 16.5 | 900 | 4 | 11.5 | 9.25 | 1.25 | 8 | 1.125 |  |  |  | 1.75 | N/A | 6.25 | 4.5 | 2.75 | 2.75 | 4.5 | 1.88 | 4.57 | 4.6 | (5) | 0.44 | N/A | 292 | 235 |  |  |  | 44.5 | N/A | 159 | 114.3 | 70 | 70 | 114 | 48 | 116.1 | 116.8 | (5) | 11 | N/A | 4.63 | 117.6 | 6.75 | 6.5 | 6.75 | 170 | 165 | 170
ASME 16.5 | 900 | 5 | 13.75 | 11 | 1.375 | 8 | 1.25 |  |  |  | 2 | N/A | 7.5 | 5.56 | 3.12 | 3.12 | 5 | 2.12 | 5.66 | 5.69 | (5) | 0.44 | N/A | 349 | 279.4 |  |  |  | 50.8 | N/A | 190 | 141.2 | 79 | 79 | 127 | 54 | 143.8 | 144.5 | (5) | 11 | N/A | 5.69 | 144.5 | 7.5 | 7.25 | 7.5 | 190 | 185 | 190
ASME 16.5 | 900 | 6 | 15 | 12.5 | 1.25 | 12 | 1.125 |  |  |  | 2.19 | N/A | 9.25 | 6.63 | 3.38 | 3.38 | 5.5 | 2.25 | 6.72 | 6.75 | (5) | 0.5 | N/A | 381 | 317.5 |  |  |  | 55.6 | N/A | 235 | 168.4 | 86 | 86 | 140 | 57 | 170.7 | 171.4 | (5) | 13 | N/A | 6.75 | 171.4 | 7.5 | 7.25 | 7.75 | 190 | 185 | 195
ASME 16.5 | 900 | 8 | 18.5 | 15.5 | 1.5 | 12 | 1.375 |  |  |  | 2.5 | N/A | 11.75 | 8.63 | 4 | 4.5 | 6.38 | 2.5 | 8.72 | 8.75 | (5) | 0.5 | N/A | 470 | 393.7 |  |  |  | 63.5 | N/A | 298 | 219.2 | 102 | 114 | 162 | 64 | 221.5 | 222.2 | (5) | 13 | N/A | 8.75 | 222.2 | 8.75 | 8.5 | 8.75 | 220 | 215 | 220
ASME 16.5 | 900 | 10 | 21.5 | 18.5 | 1.5 | 16 | 1.375 |  |  |  | 2.75 | N/A | 14.5 | 10.75 | 4.25 | 5 | 7.25 | 2.81 | 10.88 | 10.92 | (5) | 0.5 | N/A | 546 | 469.9 |  |  |  | 69.8 | N/A | 368 | 273 | 108 | 127 | 184 | 71 | 276.4 | 277.4 | (5) | 13 | N/A | 10.88 | 276.4 | 9.25 | 9 | 9.25 | 235 | 230 | 235
ASME 16.5 | 900 | 12 | 24 | 21 | 1.5 | 20 | 1.375 |  |  |  | 3.12 | N/A | 16.5 | 12.75 | 4.62 | 5.62 | 7.88 | 3 | 12.88 | 12.92 | (5) | 0.5 | N/A | 610 | 533.4 |  |  |  | 79.2 | N/A | 419 | 323.8 | 117 | 143 | 200 | 76 | 327.2 | 328.2 | (5) | 13 | N/A | 12.94 | 328.7 | 10 | 9.75 | 10 | 255 | 250 | 255
ASME 16.5 | 900 | 14 | 25.25 | 22 | 1.625 | 20 | 1.5 |  |  |  | 3.38 | N/A | 17.75 | 14 | 5.12 | 6.12 | 8.38 | 3.25 | 14.14 | 14.18 | (5) | 0.5 | N/A | 641 | 558.8 |  |  |  | 85.9 | N/A | 451 | 355.6 | 130 | 155 | 213 | 83 | 359.2 | 360.2 | (5) | 13 | N/A | 14.19 | 360.4 | 10.75 | 10.5 | 11 | 275 | 265 | 280
ASME 16.5 | 900 | 16 | 27.75 | 24.25 | 1.75 | 20 | 1.625 |  |  |  | 3.5 | N/A | 20 | 16 | 5.25 | 6.5 | 8.5 | 3.38 | 16.16 | 16.19 | (5) | 0.5 | N/A | 705 | 616 |  |  |  | 88.9 | N/A | 508 | 406.4 | 133 | 165 | 216 | 86 | 410.5 | 411.2 | (5) | 13 | N/A | 16.19 | 411.2 | 11.25 | 11 | 11.5 | 285 | 280 | 290
ASME 16.5 | 900 | 18 | 31 | 27 | 2 | 20 | 1.875 |  |  |  | 4 | N/A | 22.25 | 18 | 6 | 7.5 | 9 | 3.5 | 18.18 | 18.2 | (5) | 0.5 | N/A | 787 | 685.8 |  |  |  | 101.6 | N/A | 565 | 457.2 | 152 | 190 | 229 | 89 | 461.8 | 462.3 | (5) | 13 | N/A | 18.19 | 462 | 12.75 | 12.5 | 13.25 | 325 | 320 | 335
ASME 16.5 | 900 | 20 | 33.75 | 29.5 | 2.125 | 20 | 2 |  |  |  | 4.25 | N/A | 24.5 | 20 | 6.25 | 8.25 | 9.75 | 3.62 | 20.2 | 20.25 | (5) | 0.5 | N/A | 857 | 749.3 |  |  |  | 108 | N/A | 622 | 508 | 159 | 210 | 248 | 92 | 513.1 | 514.4 | (5) | 13 | N/A | 20.19 | 512.8 | 13.75 | 13.5 | 14.25 | 350 | 345 | 360
ASME 16.5 | 900 | 24 | 41 | 35.5 | 2.625 | 20 | 2.5 |  |  |  | 5.5 | N/A | 29.5 | 24 | 8 | 10.5 | 11.5 | 4 | 24.25 | 24.25 | (5) | 0.5 | N/A | 1041 | 901.7 |  |  |  | 139.7 | N/A | 749 | 609.6 | 203 | 267 | 292 | 102 | 616 | 616 | (5) | 13 | N/A | 24.19 | 614.4 | 17.25 | 17 | 18 | 440 | 430 | 455
ASME 16.5 | 1500 | 0.5 | 4.75 | 3.25 | 0.875 | 4 | 0.75 |  |  |  | 0.88 | N/A | 1.5 | 0.84 | 1.25 | 1.25 | 2.28 | 0.88 | 0.88 | 0.9 | (4) | 0.12 | 0.38 | 121 | 82.6 |  |  |  | 22.4 | N/A | 38 | 21.3 | 32 | 32 | 60 | 22 | 22.4 | 22.9 | (4) | 3 | 10 | 0.93 | 23.6 | 4.25 | 4.25 | 4 | 110 | 110 | 100
ASME 16.5 | 1500 | 0.75 | 5.12 | 3.5 | 0.875 | 4 | 0.75 |  |  |  | 1 | N/A | 1.75 | 1.05 | 1.38 | 1.38 | 2.75 | 1 | 1.09 | 1.11 | (4) | 0.12 | 0.44 | 130 | 88.9 |  |  |  | 25.4 | N/A | 44 | 26.7 | 35 | 35 | 70 | 25 | 27.7 | 28.2 | (4) | 3 | 11 | 1.14 | 29 | 4.5 | 4.5 | 4.25 | 115 | 115 | 110
ASME 16.5 | 1500 | 1 | 5.88 | 4 | 1 | 4 | 0.875 |  |  |  | 1.12 | N/A | 2.06 | 1.32 | 1.62 | 1.62 | 2.88 | 1.12 | 1.36 | 1.38 | (4) | 0.12 | 0.5 | 149 | 101.6 |  |  |  | 28.4 | N/A | 52 | 33.5 | 41 | 41 | 73 | 28 | 34.5 | 35.4 | (4) | 3 | 13 | 1.41 | 35.8 | 5 | 5 | 4.75 | 125 | 125 | 120
ASME 16.5 | 1500 | 1.25 | 6.25 | 4.38 | 1 | 4 | 0.875 |  |  |  | 1.12 | N/A | 2.5 | 1.66 | 1.62 | 1.62 | 2.88 | 1.19 | 1.7 | 1.72 | (4) | 0.19 | 0.56 | 159 | 111.1 |  |  |  | 28.4 | N/A | 64 | 42.2 | 41 | 41 | 73 | 30 | 43.2 | 43.7 | (4) | 5 | 14 | 1.75 | 44.4 | 5 | 5 | 4.75 | 125 | 125 | 120
ASME 16.5 | 1500 | 1.5 | 7 | 4.88 | 1.125 | 4 | 1 |  |  |  | 1.25 | N/A | 2.75 | 1.9 | 1.75 | 1.75 | 3.25 | 1.25 | 1.95 | 1.97 | (4) | 0.25 | 0.62 | 178 | 124 |  |  |  | 31.8 | N/A | 70 | 48.3 | 44 | 44 | 83 | 32 | 49.5 | 50 | (4) | 6 | 16 | 1.99 | 50.5 | 5.5 | 5.5 | 5.25 | 140 | 140 | 135
ASME 16.5 | 1500 | 2 | 8.5 | 6.5 | 1 | 8 | 0.875 |  |  |  | 1.5 | N/A | 4.12 | 2.38 | 2.25 | 2.25 | 4 | 1.5 | 2.44 | 2.46 | (4) | 0.31 | 0.69 | 216 | 165.1 |  |  |  | 38.1 | N/A | 105 | 60.5 | 57 | 57 | 102 | 38 | 62 | 62.5 | (4) | 8 | 18 | 2.5 | 63.5 | 5.75 | 5.75 | 5.5 | 145 | 145 | 140
ASME 16.5 | 1500 | 2.5 | 9.62 | 7.5 | 1.125 | 8 | 1 |  |  |  | 1.62 | N/A | 4.88 | 2.88 | 2.5 | 2.5 | 4.12 | 1.88 | 2.94 | 2.97 | (4) | 0.31 | 0.75 | 244 | 190.5 |  |  |  | 41.1 | N/A | 124 | 73.2 | 64 | 64 | 105 | 48 | 74.7 | 75.4 | (4) | 8 | 19 | 3 | 76.2 | 6.25 | 6.25 | 6 | 160 | 160 | 150
ASME 16.5 | 1500 | 3 | 10.5 | 8 | 1.125 | 8 | 1.125 |  |  |  | 1.88 | N/A | 5.25 | 3.5 | … | 2.88 | 4.62 | … | … | 3.6 | (4) | 0.38 | … | 267 | 203.2 |  |  |  | 47.8 | N/A | 133 | 88.9 | … | 73 | 117 | … | … | 91.4 | (4) | 10 | … | … | … | 7 | 7 | 6.75 | 180 | 180 | 170
ASME 16.5 | 1500 | 4 | 12.25 | 9.5 | 1.375 | 8 | 1.25 |  |  |  | 2.12 | N/A | 6.38 | 4.5 | … | 3.56 | 4.88 | … | … | 4.6 | (4) | 0.44 | … | 311 | 241.3 |  |  |  | 53.8 | N/A | 162 | 114.3 | … | 90 | 124 | … | … | 116.8 | (4) | 11 | … | … | … | 7.75 | 7.75 | 7.5 | 195 | 195 | 190
ASME 16.5 | 1500 | 5 | 14.75 | 11.5 | 1.625 | 8 | 1.5 |  |  |  | 2.88 | N/A | 7.75 | 5.56 | … | 4.12 | 6.12 | … | … | 5.69 | (4) | 0.44 | … | 375 | 292.1 |  |  |  | 73.2 | N/A | 197 | 141.2 | … | 105 | 155 | … | … | 144.5 | (4) | 11 | … | … | … | 9.75 | 9.75 | 9.5 | 250 | 250 | 240
ASME 16.5 | 1500 | 6 | 15.5 | 12.5 | 1.5 | 12 | 1.375 |  |  |  | 3.25 | N/A | 9 | 6.63 | … | 4.69 | 6.75 | … | … | 6.75 | (4) | 0.5 | … | 394 | 317.5 |  |  |  | 82.6 | N/A | 229 | 168.4 | … | 119 | 171 | … | … | 171.4 | (4) | 13 | … | … | … | 10.25 | 10.5 | 10 | 260 | 265 | 255
ASME 16.5 | 1500 | 8 | 19 | 15.5 | 1.75 | 12 | 1.625 |  |  |  | 3.62 | N/A | 11.5 | 8.63 | … | 5.62 | 8.38 | … | … | 8.75 | (4) | 0.5 | … | 483 | 393.7 |  |  |  | 91.9 | N/A | 292 | 219.2 | … | 143 | 213 | … | … | 222.2 | (4) | 13 | … | … | … | 11.5 | 11.75 | 11.25 | 290 | 300 | 285
ASME 16.5 | 1500 | 10 | 23 | 19 | 2 | 12 | 1.875 |  |  |  | 4.25 | N/A | 14.5 | 10.75 | … | 7 | 10 | … | … | 10.92 | (4) | 0.5 | … | 584 | 482.6 |  |  |  | 108 | N/A | 368 | 273 | … | 178 | 254 | … | … | 277.4 | (4) | 13 | … | … | … | 13.25 | 13.5 | 13 | 335 | 345 | 330
ASME 16.5 | 1500 | 12 | 26.5 | 22.5 | 2.125 | 16 | 2 |  |  |  | 4.88 | N/A | 17.75 | 12.75 | … | 8.62 | 11.12 | … | … | 12.92 | (4) | 0.5 | … | 673 | 571.5 |  |  |  | 124 | N/A | 451 | 323.8 | … | 219 | 282 | … | … | 328.2 | (4) | 13 | … | … | … | 14.75 | 15.25 | 14.5 | 375 | 385 | 370
ASME 16.5 | 1500 | 14 | 29.5 | 25 | 2.375 | 16 | 2.25 |  |  |  | 5.25 | N/A | 19.5 | 14 | … | 9.5 | 11.75 | … | … | 14.18 | (4) | 0.5 | … | 749 | 635 |  |  |  | 133.4 | N/A | 495 | 355.6 | … | 241 | 298 | … | … | 360.2 | (4) | 13 | … | … | … | 16 | 16.75 | 15.75 | 405 | 425 | 400
ASME 16.5 | 1500 | 16 | 32.5 | 27.75 | 2.625 | 16 | 2.5 |  |  |  | 5.75 | N/A | 21.75 | 16 | … | 10.25 | 12.25 | … | … | 16.19 | (4) | 0.5 | … | 826 | 704.8 |  |  |  | 146 | N/A | 552 | 406.4 | … | 260 | 311 | … | … | 411.2 | (4) | 13 | … | … | … | 17.5 | 18.5 | 17.25 | 445 | 470 | 440
ASME 16.5 | 1500 | 18 | 36 | 30.5 | 2.875 | 16 | 2.75 |  |  |  | 6.38 | N/A | 23.5 | 18 | … | 10.88 | 12.88 | … | … | 18.2 | (4) | 0.5 | … | 914 | 774.7 |  |  |  | 162.1 | N/A | 597 | 457.2 | … | 276 | 327 | … | … | 462.3 | (4) | 13 | … | … | … | 19.5 | 20.75 | 19.25 | 495 | 525 | 490
ASME 16.5 | 1500 | 20 | 38.75 | 32.75 | 3.125 | 16 | 3 |  |  |  | 7 | N/A | 25.25 | 20 | … | 11.5 | 14 | … | … | 20.25 | (4) | 0.5 | … | 984 | 831.8 |  |  |  | 177.8 | N/A | 641 | 508 | … | 292 | 356 | … | … | 514.4 | (4) | 13 | … | … | … | 21.25 | 22.25 | 21 | 540 | 565 | 535
ASME 16.5 | 1500 | 24 | 46 | 39 | 3.625 | 16 | 3 |  |  |  | 8 | N/A | 30 | 24 | … | 13 | 16 | … | … | 24.25 | (4) | 0.5 | … | 1168 | 990.6 |  |  |  | 203.2 | N/A | 762 | 609.6 | … | 330 | 406 | … | … | 616 | (4) | 13 | … | … | … | 24.25 | 25.5 | 24 | 615 | 650 | 610
ASME 16.5 | 2500 | 0.5 | 5.25 | 3.5 | 0.875 | 4 | 0.75 |  |  |  | 1.19 | N/A | 1.69 | 0.84 | 1.56 | 1.56 | 2.88 | 1.12 | N/A | 0.9 | (4) | 0.12 | N/A | 133 | 88.9 |  |  |  | 30.2 | N/A | 43 | 21.3 | 40 | 40 | 73 | 28 | N/A | 22.9 | (4) | 3 | N/A | 0.93 | 23.6 | 4.75 | 4.75 | 4.5 | 120 | 120 | 115
ASME 16.5 | 2500 | 0.75 | 5.5 | 3.75 | 0.875 | 4 | 0.75 |  |  |  | 1.25 | N/A | 2 | 1.05 | 1.69 | 1.69 | 3.12 | 1.25 | N/A | 1.11 | (4) | 0.12 | N/A | 140 | 95.2 |  |  |  | 31.8 | N/A | 51 | 26.7 | 43 | 43 | 79 | 32 | N/A | 28.2 | (4) | 3 | N/A | 1.14 | 29 | 5 | 5 | 4.75 | 125 | 125 | 120
ASME 16.5 | 2500 | 1 | 6.25 | 4.25 | 1 | 4 | 0.875 |  |  |  | 1.38 | N/A | 2.25 | 1.32 | 1.88 | 1.88 | 3.5 | 1.38 | N/A | 1.38 | (4) | 0.12 | N/A | 159 | 108 |  |  |  | 35.1 | N/A | 57 | 33.5 | 52 | 48 | 89 | 35 | N/A | 35.1 | (4) | 3 | N/A | 1.41 | 35.8 | 5.5 | 5.5 | 5.25 | 140 | 140 | 135
ASME 16.5 | 2500 | 1.25 | 7.25 | 5.12 | 1.125 | 4 | 1 |  |  |  | 1.5 | N/A | 2.88 | 1.66 | 2.06 | 2.06 | 3.75 | 1.5 | N/A | 1.72 | (4) | 0.19 | N/A | 184 | 130 |  |  |  | 38.1 | N/A | 73 | 42.2 | 60 | 52 | 95 | 38 | N/A | 43.7 | (4) | 5 | N/A | 1.75 | 44.4 | 6 | 6 | 5.75 | 150 | 150 | 145
ASME 16.5 | 2500 | 1.5 | 8 | 5.75 | 1.25 | 4 | 1.125 |  |  |  | 1.75 | N/A | 3.12 | 1.9 | 2.38 | 2.38 | 4.38 | 1.75 | N/A | 1.97 | (4) | 0.25 | N/A | 203 | 146 |  |  |  | 44.4 | N/A | 79 | 48.3 | 70 | 60 | 111 | 44 | N/A | 50 | (4) | 6 | N/A | 1.99 | 50.5 | 6.75 | 6.75 | 6.5 | 170 | 170 | 165
ASME 16.5 | 2500 | 2 | 9.25 | 6.75 | 1.125 | 8 | 1 |  |  |  | 2 | N/A | 3.75 | 2.38 | 2.75 | 2.75 | 5 | 2 | N/A | 2.46 | (4) | 0.31 | N/A | 235 | 171.4 |  |  |  | 50.8 | N/A | 95 | 60.5 | 79 | 70 | 127 | 51 | N/A | 62.5 | (4) | 8 | N/A | 2.5 | 63.5 | 7 | 7 | 6.75 | 180 | 180 | 170
ASME 16.5 | 2500 | 2.5 | 10.5 | 7.75 | 1.25 | 8 | 1.125 |  |  |  | 2.25 | N/A | 4.5 | 2.88 | 3.12 | 3.12 | 5.62 | 2.25 | N/A | 2.97 | (4) | 0.31 | N/A | 267 | 196.8 |  |  |  | 57.2 | N/A | 114 | 73.2 | … | 79 | 143 | 57 | N/A | 75.4 | (4) | 8 | N/A | 3 | 76.2 | 7.75 | 8 | 7.5 | 195 | 205 | 190
ASME 16.5 | 2500 | 3 | 12 | 9 | 1.375 | 8 | 1.25 |  |  |  | 2.62 | N/A | 5.25 | 3.5 | … | 3.62 | 6.62 | … | N/A | 3.6 | (4) | 0.38 | N/A | 305 | 228.6 |  |  |  | 66.5 | N/A | 133 | 88.9 | … | 92 | 168 | … | N/A | 91.4 | (4) | 10 | N/A | … | … | 8.75 | 9 | 8.5 | 220 | 230 | 215
ASME 16.5 | 2500 | 4 | 14 | 10.75 | 1.625 | 8 | 1.5 |  |  |  | 3 | N/A | 6.5 | 4.5 | … | 4.25 | 7.5 | … | N/A | 4.6 | (4) | 0.44 | N/A | 356 | 273 |  |  |  | 76.2 | N/A | 165 | 114.3 | … | 108 | 190 | … | N/A | 116.8 | (4) | 11 | N/A | … | … | 10 | 10.25 | 9.75 | 255 | 260 | 250
ASME 16.5 | 2500 | 5 | 16.5 | 12.75 | 1.875 | 8 | 1.75 |  |  |  | 3.62 | N/A | 8 | 5.56 | … | 5.12 | 9 | … | N/A | 5.69 | (4) | 0.44 | N/A | 419 | 323.8 |  |  |  | 91.9 | N/A | 203 | 141.2 | … | 130 | 229 | … | N/A | 144.5 | (4) | 11 | N/A | … | … | 11.75 | 12.25 | 11.5 | 300 | 310 | 290
ASME 16.5 | 2500 | 6 | 19 | 14.5 | 2.125 | 8 | 2 |  |  |  | 4.25 | N/A | 9.25 | 6.63 | … | 6 | 10.75 | … | N/A | 6.75 | (4) | 0.5 | N/A | 483 | 368.3 |  |  |  | 108 | N/A | 235 | 168.4 | … | 152 | 273 | … | N/A | 171.4 | (4) | 13 | N/A | … | … | 13.5 | 14 | 13.25 | 345 | 355 | 335
ASME 16.5 | 2500 | 8 | 21.75 | 17.25 | 2.125 | 12 | 2 |  |  |  | 5 | N/A | 12 | 8.63 | … | 7 | 12.5 | … | N/A | 8.75 | (4) | 0.5 | N/A | 552 | 438.2 |  |  |  | 127 | N/A | 605 | 219.2 | … | 178 | 318 | … | N/A | 222.2 | (4) | 13 | N/A | … | … | 15 | 15.5 | 14.75 | 380 | 395 | 375
ASME 16.5 | 2500 | 10 | 26.5 | 21.25 | 2.625 | 12 | 2.5 |  |  |  | 6.5 | N/A | 14.75 | 10.75 | … | 9 | 16.5 | … | N/A | 10.92 | (4) | 0.5 | N/A | 673 | 539.8 |  |  |  | 165.1 | N/A | 375 | 273 | … | 229 | 419 | … | N/A | 277.4 | (4) | 13 | N/A | … | … | 19.25 | 20 | 19 | 490 | 510 | 485
ASME 16.5 | 2500 | 12 | 30 | 24.38 | 2.875 | 12 | 2.75 |  |  |  | 7.25 | N/A | 17.38 | 12.75 | … | 10 | 18.25 | … | N/A | 12.92 | (4) | 0.5 | N/A | 762 | 619.3 |  |  |  | 184.2 | N/A | 441 | 323.8 | … | 2543 | 464 | … | N/A | 328.2 | (4) | 13 | N/A | … | … | 21.25 | 22 | 21 | 540 | 560 | 535
ASME 16.47 Series A | 400 | 26 | 38.25 | 34.5 | 1.875 | 28 | 1.75 |  | 12.5 |  |  |  | 28.62 | [10 empty] | 972 | 876.3 |  | 320 |  |  |  | 727 | [18 empty] | 12 | 26 | 29.5 | 3.5 | 3.88 | 7.62 | 0.44 | 310 | 660.4 | 749 | 88.9 | 98.6 | 194 | 11
ASME 16.47 Series A | 400 | 28 | 40.75 | 37 | 2 | 28 | 1.875 |  | 13.5 |  |  |  | 30.81 | [10 empty] | 1035 | 939.8 |  | 340 |  |  |  | 783 | [18 empty] | 13 | 28 | 31.5 | 3.75 | 4.12 | 8.12 | 0.5 | 330 | 711.2 | 800 | 95.2 | 104.6 | 206 | 13
ASME 16.47 Series A | 400 | 30 | 43 | 39.25 | 2.125 | 28 | 2 |  | 14 |  |  |  | 32.94 | [10 empty] | 1092 | 997 |  | 360 |  |  |  | 837 | [18 empty] | 13.5 | 30 | 33.75 | 4 | 4.38 | 8.62 | 0.5 | 345 | 762 | 857 | 101.6 | 111.3 | 219 | 13
ASME 16.47 Series A | 400 | 32 | 45.25 | 41.5 | 2.125 | 28 | 2 |  | 14.75 |  |  |  | 35 | [10 empty] | 1149 | 1054.1 |  | 375 |  |  |  | 339 | [18 empty] | 14 | 32 | 36 | 4.25 | 4.56 | 9.12 | 0.5 | 360 | 812.8 | 914 | 108 | 115.8 | 232 | 13
ASME 16.47 Series A | 400 | 34 | 47.5 | 43.5 | 2.125 | 28 | 2 |  | 15 |  |  |  | 37.19 | [10 empty] | 1206 | 1104.9 |  | 380 |  |  |  | 945 | [18 empty] | 14.5 | 34 | 38 | 4.38 | 4.81 | 9.5 | 0.56 | 365 | 863.6 | 965 | 111.3 | 122.2 | 241 | 14
ASME 16.47 Series A | 400 | 36 | 50 | 46 | 2.125 | 32 | 2 |  | 15.25 |  |  |  | 39.38 | [10 empty] | 1270 | 1168.4 |  | 385 |  |  |  | 1000 | [18 empty] | 14.5 | 36 | 40.25 | 4.5 | 5.06 | 9.88 | 0.56 | 375 | 914.4 | 1022 | 114.3 | 128.5 | 251 | 14
ASME 16.47 Series A | 400 | 38 | 47.5 | 44 | 1.875 | 32 | 1.75 |  | … |  |  |  | 39.5 | [10 empty] | 1206 | 1117.6 |  | … |  |  |  | 1003 | [18 empty] | 15 | 38 | 40.75 | 4.88 | 4.88 | 8.12 | 0.56 | 380 | 965.2 | 1035 | 124 | 124 | 206 | 14
ASME 16.47 Series A | 400 | 40 | 50 | 46.25 | 2 | 32 | 1.875 |  | … |  |  |  | 41.5 | [10 empty] | 1270 | 1174.8 |  | … |  |  |  | 1054 | [18 empty] | 15.5 | 40 | 43 | 5.12 | 5.12 | 8.5 | 0.56 | 405 | 1016 | 1092 | 130 | 130 | 216 | 14
ASME 16.47 Series A | 400 | 42 | 52 | 48.25 | 2 | 32 | 1.875 |  | … |  |  |  | 43.62 | [10 empty] | 1321 | 1225.6 |  | … |  |  |  | 1108 | [18 empty] | 16 | 42 | 45 | 5.25 | 5.25 | 8.81 | 0.56 | 405 | 1066.8 | 1143 | 133.4 | 133.4 | 224 | 14
ASME 16.47 Series A | 400 | 44 | 54.5 | 50.5 | 2.125 | 32 | 2 |  | … |  |  |  | 45.62 | [10 empty] | 1384 | 1282.7 |  | … |  |  |  | 1159 | [18 empty] | 16.5 | 44 | 47.25 | 5.5 | 5.5 | 9.18 | 0.56 | 425 | 1117.6 | 1200 | 139.7 | 139.7 | 233 | 14
ASME 16.47 Series A | 400 | 46 | 56.75 | 52.75 | 2.125 | 36 | 2 |  | … |  |  |  | 47.75 | [10 empty] | 1441 | 1339.8 |  | … |  |  |  | 1213 | [18 empty] | 17 | 46 | 49.5 | 5.75 | 5.75 | 9.62 | 0.56 | 435 | 1168.4 | 1257 | 146 | 146 | 244 | 14
ASME 16.47 Series A | 400 | 48 | 59.5 | 55.25 | 2.375 | 28 | 2.25 |  | … |  |  |  | 49.88 | [10 empty] | 1511 | 1403.4 |  | … |  |  |  | 1267 | [18 empty] | 18 | 48 | 51.5 | 6 | 6 | 10.12 | 0.56 | 460 | 1219.2 | 1308 | 152.4 | 152.4 | 257 | 14
ASME 16.47 Series A | 400 | 50 | 61.75 | 57.5 | 2.375 | 32 | 2.25 |  | … |  |  |  | 52 | [10 empty] | 1568 | 1460.5 |  | … |  |  |  | 1321 | [18 empty] | 18.5 | 50 | 53.62 | 6.19 | 6.25 | 10.56 | 0.56 | 470 | 1270 | 1362 | 157.2 | 158.8 | 268 | 14
ASME 16.47 Series A | 400 | 52 | 63.75 | 59.5 | 2.375 | 32 | 2.25 |  | … |  |  |  | 54 | [10 empty] | 1619 | 1511.3 |  | … |  |  |  | 1372 | [18 empty] | 19 | 52 | 55.62 | 6.38 | 6.44 | 10.88 | 0.56 | 480 | 1320.8 | 1413 | 162.1 | 163.6 | 276 | 14
ASME 16.47 Series A | 400 | 54 | 67 | 62.25 | 2.625 | 28 | 2.5 |  | … |  |  |  | 56.12 | [10 empty] | 1702 | 1581.2 |  | … |  |  |  | 1425 | [18 empty] | 20 | 54 | 57.88 | 6.69 | 6.75 | 11.38 | 0.56 | 510 | 1371.6 | 1470 | 169.9 | 171.4 | 289 | 14
ASME 16.47 Series A | 400 | 56 | 69 | 64.25 | 2.625 | 32 | 2.5 |  | … |  |  |  | 58.25 | [10 empty] | 1753 | 1632 |  | … |  |  |  | 1480 | [18 empty] | 20.5 | 56 | 60.12 | 6.88 | 6.94 | 11.75 | 0.56 | 520 | 1422.4 | 1527 | 174.8 | 176.3 | 298 | 14
ASME 16.47 Series A | 400 | 58 | 71 | 66.25 | 2.625 | 32 | 2.5 |  | … |  |  |  | 60.25 | [10 empty] | 1803 | 1682.8 |  | … |  |  |  | 1530 | [18 empty] | 20.75 | 58 | 62.12 | 7 | 7.12 | 12.06 | 0.56 | 530 | 1473.2 | 1578 | 177.8 | 180.8 | 306 | 14
ASME 16.47 Series A | 400 | 60 | 74.25 | 69 | 2.875 | 32 | 2.75 |  | … |  |  |  | 62.38 | [10 empty] | 1886 | 1752.6 |  | … |  |  |  | 1584 | [18 empty] | 21.75 | 60 | 64.38 | 7.31 | 7.44 | 12.56 | 0.56 | 560 | 1524 | 1635 | 185.7 | 189 | 319 | 14
ASME 16.47 Series A | 600 | 26 | 40 | 36 | 2 | 28 | 1.875 |  | 14.25 |  |  |  | 29.44 | [10 empty] | 1016 | 914.4 |  | 365 |  |  |  | 748 | [18 empty] | 14 | 26 | 29.5 | 4.25 | 4.94 | 8.75 | 0.5 | 355 | 660.4 | 749 | 108 | 125.5 | 222 | 13
ASME 16.47 Series A | 600 | 28 | 42.25 | 38 | 2.125 | 28 | 2 |  | 15 |  |  |  | 31.62 | [10 empty] | 1073 | 965.2 |  | 375 |  |  |  | 803 | [18 empty] | 14.5 | 28 | 31.5 | 4.38 | 5.19 | 9.25 | 0.5 | 365 | 711.2 | 800 | 111.3 | 131.8 | 235 | 13
ASME 16.47 Series A | 600 | 30 | 44.5 | 40.25 | 2.375 | 28 | 2 |  | 15 |  |  |  | 33.94 | [10 empty] | 1130 | 1022.4 |  | 385 |  |  |  | 862 | [18 empty] | 14.5 | 30 | 33.75 | 4.5 | 5.5 | 9.75 | 0.5 | 375 | 762 | 857 | 114.3 | 139.7 | 248 | 13
ASME 16.47 Series A | 600 | 32 | 47 | 42.5 | 2.375 | 28 | 2.25 |  | 16 |  |  |  | 36.12 | [10 empty] | 1194 | 1079.5 |  | 405 |  |  |  | 917 | [18 empty] | 15.25 | 32 | 36 | 4.62 | 5.81 | 10.25 | 0.56 | 390 | 812.8 | 914 | 117.3 | 147.6 | 260 | 13
ASME 16.47 Series A | 600 | 34 | 49 | 44.5 | 2.625 | 28 | 2.25 |  | 16.25 |  |  |  | 38.31 | [10 empty] | 1245 | 1130.3 |  | 410 |  |  |  | 973 | [18 empty] | 15.5 | 34 | 38 | 4.75 | 6.06 | 10.62 | 0.56 | 400 | 863.6 | 965 | 120.6 | 153.9 | 270 | 14
ASME 16.47 Series A | 600 | 36 | 51.75 | 47 | 2.375 | 28 | 2.5 |  | 17 |  |  |  | 40.62 | [10 empty] | 1314 | 1193.8 |  | 430 |  |  |  | 1032 | [18 empty] | 16.5 | 36 | 40.25 | 4.88 | 6.38 | 11.12 | 0.56 | 415 | 914.4 | 1022 | 124 | 162.1 | 282 | 14
ASME 16.47 Series A | 600 | 38 | 50 | 45.75 | 2.375 | 28 | 2.25 |  | … |  |  |  | 40.25 | [10 empty] | 1270 | 1162 |  | … |  |  |  | 1022 | [18 empty] | 18.25 | 38 | 41.5 | 6 | 6.12 | 10 | 0.56 | 465 | 965.2 | 1054 | 152.4 | 155.4 | 254 | 14
ASME 16.47 Series A | 600 | 40 | 52 | 47.75 | 2.625 | 32 | 2.25 |  | … |  |  |  | 42.25 | [10 empty] | 1321 | 1212.8 |  | … |  |  |  | 1073 | [18 empty] | 18.75 | 40 | 43.75 | 6.25 | 6.38 | 10.38 | 0.56 | 480 | 1016 | 1111 | 158.8 | 162.1 | 264 | 14
ASME 16.47 Series A | 600 | 42 | 55.25 | 50.5 | 2.625 | 28 | 2.5 |  | … |  |  |  | 44.38 | [10 empty] | 1403 | 1282.7 |  | … |  |  |  | 1127 | [18 empty] | 20 | 42 | 46 | 6.62 | 6.75 | 11 | 0.56 | 510 | 1066.8 | 1168 | 168.1 | 171.4 | 279 | 14
ASME 16.47 Series A | 600 | 44 | 57.25 | 52.5 | 2.625 | 32 | 2.5 |  | … |  |  |  | 46.5 | [10 empty] | 1454 | 1333.5 |  | … |  |  |  | 1181 | [18 empty] | 20.25 | 44 | 48.25 | 6.81 | 7 | 11.38 | 0.56 | 520 | 1117.6 | 1226 | 173 | 177.8 | 289 | 14
ASME 16.47 Series A | 600 | 46 | 59.5 | 54.75 | 2.875 | 32 | 2.5 |  | … |  |  |  | 48.62 | [10 empty] | 1511 | 1390.6 |  | … |  |  |  | 1235 | [18 empty] | 20.75 | 46 | 50.25 | 7.06 | 7.31 | 11.81 | 0.56 | 530 | 1168.4 | 1276 | 179.3 | 185.7 | 300 | 14
ASME 16.47 Series A | 600 | 48 | 62.75 | 57.5 | 3.125 | 32 | 2.75 |  | … |  |  |  | 50.75 | [10 empty] | 15.94 | 1460.5 |  | … |  |  |  | 1289 | [18 empty] | 22 | 48 | 52.5 | 7.44 | 7.69 | 12.44 | 0.56 | 565 | 1219.2 | 1334 | 189 | 195.3 | 316 | 14
ASME 16.47 Series A | 600 | 50 | 65.75 | 60 | 3.125 | 28 | 3 |  | … |  |  |  | 52.88 | [10 empty] | 1670 | 1524 |  | … |  |  |  | 1343 | [18 empty] | 23.25 | 50 | 54.5 | 7.75 | 8 | 12.94 | 0.56 | 595 | 1270 | 1384 | 196.8 | 203.2 | 329 | 14
ASME 16.47 Series A | 600 | 52 | 67.75 | 62 | 3.125 | 32 | 3 |  | … |  |  |  | 54.88 | [10 empty] | 1721 | 1574.8 |  | … |  |  |  | 1394 | [18 empty] | 23.75 | 52 | 56.5 | 8 | 8.25 | 13.25 | 0.56 | 605 | 1320.8 | 1435 | 203.2 | 209.6 | 337 | 14
ASME 16.47 Series A | 600 | 54 | 70 | 64.25 | 3.125 | 32 | 3 |  | … |  |  |  | 57 | [10 empty] | 1778 | 1632 |  | … |  |  |  | 1448 | [18 empty] | 2425 | 54 | 58.75 | 8.25 | 8.56 | 13.75 | 0.56 | 620 | 1371.6 | 1492 | 209.6 | 217.4 | 349 | 14
ASME 16.47 Series A | 600 | 56 | 73 | 66.75 | 3.375 | 32 | 3.25 |  | … |  |  |  | 59.12 | [10 empty] | 1854 | 1695.4 |  | … |  |  |  | 1502 | [18 empty] | 25.5 | 56 | 60.75 | 8.56 | 8.88 | 14.25 | 0.62 | 645 | 1422.4 | 1543 | 217.4 | 225.6 | 362 | 16
ASME 16.47 Series A | 600 | 58 | 75 | 68.75 | 3.375 | 32 | 3.25 |  | … |  |  |  | 61.12 | [10 empty] | 1905 | 1746.2 |  | … |  |  |  | 1553 | [18 empty] | 25.75 | 58 | 63 | 8.75 | 9.12 | 14.53 | 0.62 | 655 | 1473.2 | 1600 | 222.2 | 231.6 | 370 | 16
ASME 16.47 Series A | 600 | 60 | 78.5 | 71.75 | 3.625 | 28 | 3.5 |  | … |  |  |  | 63.38 | [10 empty] | 1994 | 1822.4 |  | … |  |  |  | 1610 | [18 empty] | 27.25 | 60 | 65.25 | 9.19 | 9.56 | 15.31 | 0.69 | 690 | 1524 | 1657 | 233.4 | 242.8 | 389 | 17
ASME 16.47 Series A | 900 | 26 | 42.75 | 37.5 | 2.875 | 20 | 2.75 |  | 19 |  |  |  | 30.5 | [10 empty] | 1086 | 952.5 |  | 485 |  |  |  | 775 | [18 empty] | 18.25 | 26 | 29.5 | 5.5 | 6.31 | 11.25 | 0.44 | 465 | 660.4 | 749 | 139.7 | 160.3 | 286 | 11
ASME 16.47 Series A | 900 | 28 | 46 | 40.25 | 3.125 | 20 | 3 |  | 19.75 |  |  |  | 32.75 | [10 empty] | 1168 | 1022.4 |  | 505 |  |  |  | 832 | [18 empty] | 19 | 28 | 31.5 | 5.62 | 6.753 | 11.75 | 0.5 | 485 | 711.2 | 800 | 142.7 | 171.4 | 298 | 13
ASME 16.47 Series A | 900 | 30 | 48.5 | 42.75 | 3.125 | 20 | 3 |  | 20.25 |  |  |  | 35 | [10 empty] | 1232 | 1085.8 |  | 520 |  |  |  | 889 | [18 empty] | 19.5 | 30 | 33.75 | 5.88 | 7.18 | 12.25 | 0.5 | 495 | 762 | 857 | 129.4 | 182.4 | 311 | 13
ASME 16.47 Series A | 900 | 32 | 51.75 | 45.5 | 3.375 | 20 | 3.25 |  | 21.5 |  |  |  | 37.25 | [10 empty] | 1314 | 1155.7 |  | 550 |  |  |  | 946 | [18 empty] | 20.75 | 32 | 36 | 6.25 | 7.62 | 13 | 0.5 | 530 | 812.8 | 914 | 158.8 | 193.5 | 330 | 13
ASME 16.47 Series A | 900 | 34 | 55 | 48.25 | 3.625 | 20 | 3.5 |  | 22.75 |  |  |  | 39.62 | [10 empty] | 1397 | 1225.6 |  | 580 |  |  |  | 1006 | [18 empty] | 21.75 | 34 | 38 | 6.5 | 8.06 | 13.75 | 0.56 | 555 | 863.6 | 965 | 165.1 | 204.7 | 349 | 14
ASME 16.47 Series A | 900 | 36 | 57.5 | 50.75 | 3.625 | 20 | 3.5 |  | 23.25 |  |  |  | 41.88 | [10 empty] | 1460 | 1289 |  | 595 |  |  |  | 1064 | [18 empty] | 22.25 | 36 | 40.25 | 6.75 | 8.44 | 14.25 | 0.56 | 565 | 914.4 | 1022 | 171.4 | 214.4 | 362 | 14
ASME 16.47 Series A | 900 | 38 | 57.5 | 50.75 | 3.625 | 20 | 3.5 |  | … |  |  |  | 42.25 | [10 empty] | 1460 | 1289 |  | … |  |  |  | 1073 | [18 empty] | 23.75 | 38 | 43.25 | 7.5 | 8.5 | 13.88 | 0.75 | 605 | 965.2 | 1099 | 190.5 | 215.9 | 353 | 19
ASME 16.47 Series A | 900 | 40 | 59.5 | 52.75 | 3.625 | 24 | 3.5 |  | … |  |  |  | 44.38 | [10 empty] | 1511 | 1339.8 |  | … |  |  |  | 1127 | [18 empty] | 24.5 | 40 | 45.75 | 7.75 | 8.81 | 14.31 | 0.81 | 620 | 1016 | 1162 | 196.8 | 223.8 | 363 | 21
ASME 16.47 Series A | 900 | 42 | 61.5 | 54.75 | 3.625 | 24 | 3.5 |  | … |  |  |  | 46.31 | [10 empty] | 1562 | 1390.6 |  | … |  |  |  | 1176 | [18 empty] | 25 | 42 | 47.75 | 8.12 | 9.12 | 14.62 | 0.81 | 635 | 1066.8 | 1213 | 206.2 | 231.6 | 371 | 21
ASME 16.47 Series A | 900 | 44 | 64.88 | 57.75 | 3.875 | 24 | 3.75 |  | … |  |  |  | 48.62 | [10 empty] | 1648 | 1463.5 |  | … |  |  |  | 1235 | [18 empty] | 26 | 44 | 50 | 8.44 | 9.56 | 15.38 | 0.88 | 665 | 1117.6 | 1270 | 214.4 | 242.8 | 391 | 22
ASME 16.47 Series A | 900 | 46 | 68.25 | 60.5 | 4.125 | 24 | 4 |  | … |  |  |  | 50.88 | [10 empty] | 1734 | 1536.7 |  | … |  |  |  | 1292 | [18 empty] | 27.5 | 46 | 52.5 | 8.88 | 10.06 | 16.18 | 0.88 | 7000 | 1168.4 | 1334 | 225.6 | 255.5 | 411 | 22
ASME 16.47 Series A | 900 | 48 | 70.25 | 62.5 | 4.125 | 24 | 4 |  | … |  |  |  | 52.88 | [10 empty] | 1784 | 1587.5 |  | … |  |  |  | 1343 | [18 empty] | 28 | 48 | 54.5 | 9.19 | 10.38 | 16.5 | 0.94 | 715 | 1219.2 | 1384 | 233.4 | 263.7 | 419 | 24
ASME 16.47 Series A | 900 | 50 | … | … | … | … | … |  | … |  |  |  | … | [10 empty] | … | … |  | … |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series A | 900 | 52 | … | … | … | … | … |  | … |  |  |  | … | [10 empty] | … | … |  | … |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series A | 900 | 54 | … | … | … | … | … |  | … |  |  |  | … | [10 empty] | … | … |  | … |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series A | 900 | 56 | … | … | … | … | … |  | … |  |  |  | … | [10 empty] | … | … |  | … |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series A | 900 | 58 | … | … | … | … | … |  | … |  |  |  | … | [10 empty] | … | … |  | … |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series A | 900 | 60 | … | … | … | … | … |  | … |  |  |  | … | [10 empty] | … | … |  | … |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 400 | 26 | 33.5 | 30.75 | 1.5 | 28 | 1.375 |  | N/A |  |  |  | 27.12 | [10 empty] | 851 | 781 |  | N/A |  |  |  | 689 | [18 empty] | 14.25 | 26 | 28 | 3.5 | 3.5 | 5.88 | 0.44 | 290 | 660.4 | 711 | 88.9 | 88.9 | 149 | 11
ASME 16.47 Series B | 400 | 28 | 36 | 33 | 1.625 | 24 | 1.5 |  | N/A |  |  |  | 29.12 | [10 empty] | 914 | 838.2 |  | N/A |  |  |  | 740 | [18 empty] | 14.75 | 28 | 30 | 3.75 | 3.75 | 6.25 | 0.5 | 310 | 711.2 | 762 | 95.2 | 95.2 | 159 | 13
ASME 16.47 Series B | 400 | 30 | 38.25 | 35.25 | 1.625 | 28 | 1.5 |  | N/A |  |  |  | 31.25 | [10 empty] | 972 | 895.4 |  | N/A |  |  |  | 794 | [18 empty] | 15.5 | 30 | 32.25 | 4 | 4 | 6.69 | 0.5 | 320 | 768 | 819 | 101.6 | 101.6 | 170 | 13
ASME 16.47 Series B | 400 | 32 | 40.75 | 37.25 | 1.75 | 28 | 1.625 |  | N/A |  |  |  | 33.25 | [10 empty] | 1035 | 952.5 |  | N/A |  |  |  | 845 | [18 empty] | 16.25 | 32 | 34.38 | 4.25 | 4.25 | 7.06 | 0.5 | 345 | 812.8 | 873 | 108 | 108 | 179 | 13
ASME 16.47 Series B | 400 | 34 | 42.75 | 39.5 | 1.75 | 32 | 1.625 |  | N/A |  |  |  | 35.38 | [10 empty] | 1086 | 1003.3 |  | N/A |  |  |  | 899 | [18 empty] | 17.25 | 34 | 36.5 | 4.38 | 4.38 | 7.38 | 0.56 | 345 | 863.6 | 927 | 111.3 | 111.3 | 187 | 14
ASME 16.47 Series B | 400 | 36 | 45.5 | 42 | 1.875 | 28 | 1.75 |  | N/A |  |  |  | 37.5 | [10 empty] | 1156 | 1066.8 |  | N/A |  |  |  | 952 | [18 empty] | 18 | 36 | 38.62 | 4.69 | 4.69 | 7.88 | 0.56 | 370 | 914.4 | 981 | 119.1 | 119.1 | 200 | 14
ASME 16.47 Series B | 400 | 38 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 400 | 40 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 400 | 42 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 400 | 44 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 400 | 46 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 400 | 48 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 400 | 50 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 400 | 52 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 400 | 54 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 400 | 56 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 400 | 58 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 400 | 60 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 600 | 26 | 35 | 31.75 | 1.75 | 28 | 1.625 |  | N/A |  |  |  | 27.5 | [10 empty] | 889 | 806.4 |  | N/A |  |  |  | 698 | [18 empty] | 14.25 | 26 | 28.62 | 4.38 | 4.38 | 7.12 | 0.5 | 360 | 660.4 | 727 | 111.3 | 111.3 | 181 | 13
ASME 16.47 Series B | 600 | 28 | 37.5 | 34 | 1.875 | 28 | 1.75 |  | N/A |  |  |  | 29.62 | [10 empty] | 952 | 863.6 |  | N/A |  |  |  | 752 | [18 empty] | 14.75 | 28 | 30.88 | 4.56 | 4.56 | 7.5 | 0.5 | 375 | 711.2 | 784 | 115.8 | 115.8 | 190 | 13
ASME 16.47 Series B | 600 | 30 | 40.25 | 36.5 | 2 | 28 | 1.875 |  | N/A |  |  |  | 31.75 | [10 empty] | 1022 | 927.1 |  | N/A |  |  |  | 806 | [18 empty] | 15.5 | 30 | 33.12 | 4.94 | 5 | 8.06 | 0.5 | 395 | 762 | 841 | 125.5 | 127 | 205 | 13
ASME 16.47 Series B | 600 | 32 | 42.75 | 38.75 | 2.125 | 28 | 2 |  | N/A |  |  |  | 33.88 | [10 empty] | 1086 | 984.2 |  | N/A |  |  |  | 861 | [18 empty] | 16.25 | 32 | 35.25 | 5.12 | 5.31 | 8.5 | 0.5 | 415 | 812.8 | 895 | 130 | 134.9 | 216 | 13
ASME 16.47 Series B | 600 | 34 | 45.75 | 41.5 | 2.375 | 24 | 2.25 |  | N/A |  |  |  | 36 | [10 empty] | 1162 | 1054.1 |  | N/A |  |  |  | 914 | [18 empty] | 17.25 | 34 | 37.5 | 5.56 | 5.68 | 9.19 | 0.56 | 440 | 863.6 | 952 | 141.2 | 144.3 | 233 | 14
ASME 16.47 Series B | 600 | 36 | 47.75 | 43.5 | 2.375 | 28 | 2.25 |  | N/A |  |  |  | 38.12 | [10 empty] | 1213 | 1104.9 |  | N/A |  |  |  | 968 | [18 empty] | 18 | 36 | 39.75 | 5.75 | 5.94 | 9.56 | 0.56 | 460 | 914.4 | 1010 | 146 | 150.9 | 243 | 14
ASME 16.47 Series B | 600 | 38 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 600 | 40 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 600 | 42 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 600 | 44 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 600 | 46 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 600 | 48 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 600 | 50 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 600 | 52 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 600 | 54 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 600 | 56 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 600 | 58 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 600 | 60 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 900 | 26 | 40.25 | 35.5 | 2.625 | 20 | 2.5 |  | N/A |  |  |  | 29.25 | [10 empty] | 1022 | 901.7 |  | N/A |  |  |  | 743 | [18 empty] | 17.75 | 26 | 30 | 5.31 | 6.06 | 10.19 | 0.44 | 450 | 660.4 | 762 | 134.9 | 153.9 | 259 | 11
ASME 16.47 Series B | 900 | 28 | 43.5 | 38.25 | 2.875 | 20 | 2.75 |  | N/A |  |  |  | 31.38 | [10 empty] | 1105 | 971.6 |  | N/A |  |  |  | 797 | [18 empty] | 19.25 | 28 | 32.25 | 5.81 | 6.56 | 10.88 | 0.5 | 495 | 711.2 | 819 | 147.6 | 166.6 | 276 | 13
ASME 16.47 Series B | 900 | 30 | 46.5 | 40.75 | 3.125 | 20 | 3 |  | N/A |  |  |  | 33.5 | [10 empty] | 1181 | 1035 |  | N/A |  |  |  | 851 | [18 empty] | 20 | 30 | 34.5 | 6.12 | 6.93 | 11.38 | 0.5 | 510 | 762 | 876 | 155.4 | 176 | 289 | 13
ASME 16.47 Series B | 900 | 32 | 48.75 | 43 | 3.125 | 20 | 3 |  | N/A |  |  |  | 35.75 | [10 empty] | 1238 | 1092.2 |  | N/A |  |  |  | 908 | [18 empty] | 20.75 | 32 | 36.5 | 6.31 | 7.31 | 11.94 | 0.5 | 530 | 812.8 | 927 | 160.3 | 185.7 | 303 | 13
ASME 16.47 Series B | 900 | 34 | 51.75 | 45.5 | 3.375 | 20 | 3.25 |  | N/A |  |  |  | 37.88 | [10 empty] | 1314 | 1155.7 |  | N/A |  |  |  | 962 | [18 empty] | 22.25 | 34 | 39 | 6.75 | 7.68 | 12.56 | 0.56 | 565 | 863.6 | 991 | 171.4 | 195 | 319 | 14
ASME 16.47 Series B | 900 | 36 | 53 | 47.25 | 3.125 | 24 | 3 |  | N/A |  |  |  | 40 | [10 empty] | 1346 | 1200.2 |  | N/A |  |  |  | 1016 | [18 empty] | 22.5 | 36 | 40.5 | 6.81 | 7.94 | 12.81 | 0.56 | 570 | 914.4 | 1029 | 173 | 201.7 | 325 | 14
ASME 16.47 Series B | 900 | 38 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 900 | 40 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 900 | 42 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 900 | 44 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 900 | 46 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 900 | 48 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 900 | 50 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 900 | 52 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 900 | 54 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 900 | 56 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 900 | 58 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series B | 900 | 60 | … | … | … | … | … |  | N/A |  |  |  | … | [10 empty] | … | … |  | N/A |  |  |  | … | [18 empty] | … | … | … | … | … | … | … | … | … | … | … | … | … | …
ASME 16.47 Series A | 300 | 26 | 38.25 | 34.5 | 1.75 | 28 | 1.625 | 10.5 | 11.5 |  |  |  | 28.38 | [10 empty] | 972 | 876.3 | 270 | 290 |  |  |  | 721 | [19 empty] | 26 | 29.5 | 3.07 | 3.25 | 7.19 | 0.38 |  | 660.4 | 749 | 78 | 82.6 | 183 | 10
ASME 16.47 Series A | 300 | 28 | 40.75 | 37 | 1.75 | 28 | 1.625 | 11 | 12 |  |  |  | 30.5 | [10 empty] | 1035 | 939.8 | 280 | 300 |  |  |  | 775 | [19 empty] | 28 | 31.5 | 3.32 | 3.5 | 7.69 | 0.44 |  | 711.2 | 800 | 84.3 | 88.9 | 195 | 11
ASME 16.47 Series A | 300 | 30 | 43 | 39.25 | 1.875 | 28 | 1.75 | 11.75 | 12.75 |  |  |  | 32.56 | [10 empty] | 1092 | 997 | 300 | 320 |  |  |  | 827 | [19 empty] | 30 | 33.75 | 3.57 | 3.69 | 8.19 | 0.44 |  | 762 | 857 | 90.7 | 93.7 | 208 | 11
ASME 16.47 Series A | 300 | 32 | 45.25 | 41.5 | 2 | 28 | 1.875 | 12.75 | 13.75 |  |  |  | 34.69 | [10 empty] | 1149 | 1054.1 | 320 | 345 |  |  |  | 881 | [19 empty] | 32 | 36 | 3.82 | 3.88 | 8.69 | 0.44 |  | 812.8 | 914 | 97 | 98.6 | 221 | 11
ASME 16.47 Series A | 300 | 34 | 47.5 | 43.5 | 2 | 28 | 1.875 | 13 | 13.75 |  |  |  | 36.88 | [10 empty] | 1206 | 1104.9 | 330 | 350 |  |  |  | 937 | [19 empty] | 34 | 38 | 3.94 | 4.07 | 9.07 | 0.5 |  | 863.6 | 965 | 100.1 | 103.4 | 230 | 13
ASME 16.47 Series A | 300 | 36 | 50 | 46 | 2.125 | 32 | 2 | 13.5 | 14.25 |  |  |  | 39 | [10 empty] | 1270 | 1168.4 | 340 | 365 |  |  |  | 991 | [19 empty] | 36 | 40.25 | 4.07 | 4.32 | 9.44 | 0.5 |  | 914.4 | 1022 | 103.4 | 109.7 | 240 | 13
ASME 16.47 Series A | 300 | 38 | 46 | 43 | 1.625 | 32 | 1.5 | 12.5 | … |  |  |  | 39.12 | [10 empty] | 1168 | 1092.2 | 32 | … |  |  |  | 994 | [19 empty] | 38 | 40.5 | 4.19 | 4.19 | 7.06 | 0.5 |  | 965.2 | 1029 | 106.4 | 106.4 | 179 | 13
ASME 16.47 Series A | 300 | 40 | 48.75 | 45.5 | 1.75 | 32 | 1.625 | 13.25 | … |  |  |  | 41.25 | [10 empty] | 1238 | 1155.7 | 340 | … |  |  |  | 1048 | [19 empty] | 40 | 42.75 | 4.44 | 4.44 | 7.56 | 0.5 |  | 1016 | 1086 | 112.8 | 112.8 | 192 | 13
ASME 16.47 Series A | 300 | 42 | 50.75 | 47.5 | 1.75 | 32 | 1.625 | 13.75 | … |  |  |  | 43.25 | [10 empty] | 1289 | 1206.5 | 350 | … |  |  |  | 1099 | [19 empty] | 42 | 44.75 | 4.63 | 4.63 | 7.82 | 0.5 |  | 1066.8 | 1137 | 117.6 | 117.6 | 199 | 13
ASME 16.47 Series A | 300 | 44 | 53.25 | 49.75 | 1.875 | 32 | 1.75 | 14.5 | … |  |  |  | 45.25 | [10 empty] | 1353 | 1263.6 | 365 | … |  |  |  | 1149 | [19 empty] | 44 | 47 | 4.82 | 4.82 | 8.06 | 0.5 |  | 1117.6 | 1194 | 122.4 | 122.4 | 205 | 13
ASME 16.47 Series A | 300 | 46 | 55.75 | 52 | 2 | 28 | 1.875 | 15 | … |  |  |  | 47.38 | [10 empty] | 1416 | 1320.8 | 380 | … |  |  |  | 1203 | [19 empty] | 46 | 49 | 5 | 5 | 8.44 | 0.5 |  | 1168.4 | 1245 | 127 | 127 | 214 | 13
ASME 16.47 Series A | 300 | 48 | 57.75 | 54 | 2 | 32 | 1.875 | 15.5 | … |  |  |  | 49.38 | [10 empty] | 1467 | 1371.6 | 390 | … |  |  |  | 1254 | [19 empty] | 48 | 51.25 | 5.19 | 5.19 | 8.75 | 0.5 |  | 1219.2 | 1302 | 131.8 | 131.8 | 222 | 13
ASME 16.47 Series A | 300 | 50 | 60.25 | 56.25 | 2.125 | 32 | 2 | 16 | … |  |  |  | 51.38 | [10 empty] | 1530 | 1428.8 | 410 | … |  |  |  | 1305 | [19 empty] | 50 | 53.5 | 5.44 | 5.44 | 9.07 | 0.5 |  | 1270 | 1359 | 138.2 | 138.2 | 230 | 13
ASME 16.47 Series A | 300 | 52 | 62.25 | 58.25 | 2.125 | 32 | 2 | 16.5 | … |  |  |  | 53.38 | [10 empty] | 1581 | 1479.6 | 420 | … |  |  |  | 1356 | [19 empty] | 52 | 55.5 | 5.63 | 5.63 | 9.32 | 0.5 |  | 1320.8 | 1410 | 143 | 143 | 237 | 13
ASME 16.47 Series A | 300 | 54 | 65.25 | 61 | 2.375 | 28 | 2.25 | 17.5 | … |  |  |  | 55.5 | [10 empty] | 1657 | 1549.4 | 450 | … |  |  |  | 1410 | [19 empty] | 54 | 57.75 | 5.94 | 5.94 | 9.88 | 0.5 |  | 1371.6 | 1467 | 150.9 | 150.9 | 251 | 13
ASME 16.47 Series A | 300 | 56 | 67.25 | 63 | 2.375 | 28 | 2.25 | 17.75 | … |  |  |  | 57.62 | [10 empty] | 1708 | 1600.2 | 450 | … |  |  |  | 1464 | [19 empty] | 56 | 59.75 | 6 | 6 | 10.19 | 0.5 |  | 1422.4 | 1518 | 152.4 | 152.4 | 259 | 13
ASME 16.47 Series A | 300 | 58 | 69.25 | 65 | 2.375 | 32 | 2.25 | 18.25 | … |  |  |  | 59.62 | [10 empty] | 1759 | 1651 | 465 | … |  |  |  | 1514 | [19 empty] | 58 | 62 | 6.19 | 6.19 | 10.44 | 0.5 |  | 1473.2 | 1575 | 157.2 | 157.2 | 265 | 13
ASME 16.47 Series A | 300 | 60 | 71.25 | 67 | 2.375 | 32 | 1.25 | 18.75 | … |  |  |  | 61.62 | [10 empty] | 1810 | 1701.8 | 475 | … |  |  |  | 1565 | [19 empty] | 60 | 64 | 6.38 | 6.38 | 10.69 | 0.5 |  | 1524 | 1626 | 160.1 | 160.1 | 272 | 13
ASME 16.47 Series A | 150 | 26 | 34.25 | 31.75 | 1.375 | 24 | 1.25 | 8.75 | N/A |  |  |  | 26.62 | [10 empty] | 870 | 806.4 | 225 | N/A |  |  |  | 676 | [19 empty] | 26 | 29.5 | 2.63 | 2.63 | 4.69 | 0.38 |  | 660.4 | 749 | 66.8 | 66.8 | 119 | 10
ASME 16.47 Series A | 150 | 28 | 36.5 | 34 | 1.375 | 28 | 1.25 | 9 | N/A |  |  |  | 28.62 | [10 empty] | 927 | 863.6 | 230 | N/A |  |  |  | 727 | [19 empty] | 28 | 31.5 | 2.75 | 2.75 | 4.88 | 0.44 |  | 711.2 | 800 | 69.8 | 69.8 | 124 | 11
ASME 16.47 Series A | 150 | 30 | 38.75 | 36 | 1.375 | 28 | 1.25 | 9.25 | N/A |  |  |  | 30.75 | [10 empty] | 984 | 914.4 | 235 | N/A |  |  |  | 781 | [19 empty] | 30 | 33.75 | 2.88 | 2.88 | 5.32 | 0.44 |  | 762 | 857 | 73.2 | 73.2 | 135 | 11
ASME 16.47 Series A | 150 | 32 | 41.75 | 38.5 | 1.625 | 28 | 1.5 | 10.5 | N/A |  |  |  | 32.75 | [10 empty] | 1060 | 977.9 | 265 | N/A |  |  |  | 832 | [19 empty] | 32 | 36 | 3.13 | 3.13 | 5.63 | 0.44 |  | 812.8 | 914 | 79.5 | 79.5 | 143 | 11
ASME 16.47 Series A | 150 | 34 | 43.75 | 40.5 | 1.625 | 32 | 1.5 | 10.5 | N/A |  |  |  | 34.75 | [10 empty] | 1111 | 1028.7 | 270 | N/A |  |  |  | 883 | [19 empty] | 34 | 38 | 3.19 | 3.19 | 5.82 | 0.5 |  | 863.6 | 965 | 81 | 81 | 148 | 13
ASME 16.47 Series A | 150 | 36 | 46 | 42.75 | 1.625 | 32 | 1.5 | 11.25 | N/A |  |  |  | 36.75 | [10 empty] | 1168 | 1085.8 | 285 | N/A |  |  |  | 933 | [19 empty] | 36 | 40.25 | 3.5 | 3.5 | 6.13 | 0.5 |  | 914.4 | 1022 | 88.9 | 88.9 | 156 | 13
ASME 16.47 Series A | 150 | 38 | 48.75 | 45.25 | 1.625 | 32 | 1.5 | 11 | N/A |  |  |  | 39 | [10 empty] | 1238 | 1149.4 | 280 | N/A |  |  |  | 991 | [19 empty] | 38 | 42.25 | 3.38 | 3.38 | 6.13 | 0.5 |  | 965.2 | 1073 | 85.9 | 85.9 | 156 | 13
ASME 16.47 Series A | 150 | 40 | 50.75 | 47.25 | 1.625 | 36 | 1.5 | 11.25 | N/A |  |  |  | 41 | [10 empty] | 1289 | 1200.2 | 285 | N/A |  |  |  | 1041 | [19 empty] | 40 | 44.25 | 3.5 | 3.5 | 6.38 | 0.5 |  | 1016 | 1124 | 88.9 | 88.9 | 162 | 13
ASME 16.47 Series A | 150 | 42 | 53 | 49.5 | 1.625 | 36 | 1.5 | 11.75 | N/A |  |  |  | 43 | [10 empty] | 1346 | 1257.3 | 300 | N/A |  |  |  | 1092 | [19 empty] | 42 | 47 | 3.75 | 3.75 | 6.69 | 0.5 |  | 1066.8 | 1194 | 95.2 | 95.2 | 170 | 13
ASME 16.47 Series A | 150 | 44 | 55.25 | 51.75 | 1.625 | 40 | 1.5 | 12 | N/A |  |  |  | 45 | [10 empty] | 1403 | 1314.4 | 305 | N/A |  |  |  | 1143 | [19 empty] | 44 | 49 | 3.94 | 3.94 | 6.94 | 0.5 |  | 1117.6 | 1245 | 100.1 | 100.1 | 176 | 13
ASME 16.47 Series A | 150 | 46 | 57.25 | 53.75 | 1.625 | 40 | 1.5 | 12.25 | N/A |  |  |  | 47.12 | [10 empty] | 1454 | 1365.2 | 310 | N/A |  |  |  | 1197 | [19 empty] | 46 | 51 | 4 | 4 | 7.25 | 0.5 |  | 1168.4 | 1295 | 101.6 | 101.6 | 184 | 13
ASME 16.47 Series A | 150 | 48 | 59.5 | 56 | 1.625 | 44 | 1.5 | 12.5 | N/A |  |  |  | 49.12 | [10 empty] | 1511 | 1422.4 | 320 | N/A |  |  |  | 1248 | [19 empty] | 48 | 52.5 | 4.19 | 4.19 | 7.5 | 0.5 |  | 1219.2 | 1359 | 106.4 | 106.4 | 191 | 13
ASME 16.47 Series A | 150 | 50 | 67.75 | 58.25 | 1.875 | 44 | 1.75 | 13.5 | N/A |  |  |  | 51.25 | [10 empty] | 1568 | 1479.6 | 340 | N/A |  |  |  | 1302 | [19 empty] | 50 | 55.5 | 4.32 | 4.32 | 7.94 | 0.5 |  | 1270 | 1410 | 109.7 | 109.7 | 202 | 13
ASME 16.47 Series A | 150 | 52 | 64 | 60.5 | 1.875 | 44 | 1.75 | 13.75 | N/A |  |  |  | 53.25 | [10 empty] | 1626 | 1536.7 | 350 | N/A |  |  |  | 1353 | [19 empty] | 52 | 57.5 | 4.5 | 4.5 | 8.19 | 0.5 |  | 1320.8 | 1431 | 114.3 | 114.3 | 208 | 13
ASME 16.47 Series A | 150 | 54 | 66.25 | 62.75 | 1.875 | 44 | 1.75 | 14 | N/A |  |  |  | 55.25 | [10 empty] | 1683 | 1593.8 | 360 | N/A |  |  |  | 1403 | [19 empty] | 54 | 59.5 | 4.69 | 4.69 | 8.44 | 0.5 |  | 1371.6 | 15111 | 119.1 | 119.1 | 214 | 13
ASME 16.47 Series A | 150 | 56 | 68.75 | 65 | 1.875 | 48 | 1.75 | 14.5 | N/A |  |  |  | 57.38 | [10 empty] | 1746 | 1651 | 365 | N/A |  |  |  | 1457 | [19 empty] | 56 | 62 | 4.82 | 4.82 | 8.94 | 0.5 |  | 1422.4 | 1575 | 122.4 | 122.4 | 227 | 13
ASME 16.47 Series A | 150 | 58 | 71 | 67.25 | 1.875 | 48 | 1.75 | 14.75 | N/A |  |  |  | 59.38 | [10 empty] | 1803 | 1708.2 | 380 | N/A |  |  |  | 1508 | [19 empty] | 58 | 64 | 5 | 5 | 9.19 | 0.5 |  | 1473.2 | 1626 | 127 | 127 | 233 | 13
ASME 16.47 Series A | 150 | 60 | 73 | 69.25 | 1.875 | 52 | 1.75 | 15 | N/A |  |  |  | 61.38 | [10 empty] | 1854 | 1759 | 380 | N/A |  |  |  | 1559 | [19 empty] | 60 | 66 | 5.13 | 5.13 | 9.38 | 0.5 |  | 1524 | 1676 | 130.3 | 130.3 | 238 | 13
ASME 16.47 Series B | 75 | 26 | 30 | 28.5 | 0.75 | 36 | 0.625 | 4.5 | N/A |  |  |  | 26.62 | [10 empty] | 760 | 723.9 | 115 | N/A |  |  |  | 676 | [19 empty] | 26.06 | 27.75 | 1.25 | 1.25 | 2.25 | 0.31 |  | 661.9 | 705 | 31.8 | 31.8 | 57 | 8
ASME 16.47 Series B | 75 | 28 | 32 | 30.5 | 0.75 | 40 | 0.625 | 4.5 | N/A |  |  |  | 28.62 | [10 empty] | 813 | 774.7 | 115 | N/A |  |  |  | 727 | [19 empty] | 28.06 | 29.75 | 1.25 | 1.25 | 2.38 | 0.31 |  | 712.7 | 756 | 31.8 | 31.8 | 60 | 8
ASME 16.47 Series B | 75 | 30 | 34 | 32.5 | 0.75 | 44 | 0.625 | 4.75 | N/A |  |  |  | 30.62 | [10 empty] | 864 | 825.5 | 115 | N/A |  |  |  | 778 | [19 empty] | 30.06 | 31.75 | 1.25 | 1.25 | 2.5 | 0.31 |  | 763.5 | 806 | 31.8 | 31.8 | 64 | 8
ASME 16.47 Series B | 75 | 32 | 36 | 34.5 | 0.75 | 48 | 0.625 | 4.75 | N/A |  |  |  | 32.62 | [10 empty] | 914 | 876.3 | 120 | N/A |  |  |  | 829 | [19 empty] | 32.06 | 33.75 | 1.32 | 1.38 | 2.69 | 0.31 |  | 814.3 | 857 | 33.5 | 35.1 | 68 | 8
ASME 16.47 Series B | 75 | 34 | 38 | 36.5 | 0.75 | 52 | 0.625 | 4.75 | N/A |  |  |  | 34.62 | [10 empty] | 965 | 927.1 | 120 | N/A |  |  |  | 879 | [19 empty] | 34.06 | 35.75 | 1.32 | 1.44 | 2.82 | 0.31 |  | 865.1 | 908 | 33.5 | 36.6 | 72 | 8
ASME 16.47 Series B | 75 | 36 | 40.69 | 39.06 | 0.875 | 40 | 0.75 | 5 | N/A |  |  |  | 36.81 | [10 empty] | 1034 | 992.1 | 130 | N/A |  |  |  | 935 | [19 empty] | 36.06 | 38 | 1.38 | 1.61 | 3.32 | 0.38 |  | 915.9 | 965 | 35.1 | 40.9 | 84 | 10
ASME 16.47 Series B | 75 | 38 | 42.69 | 41.06 | 0.875 | 40 | 0.75 | 5.25 | N/A |  |  |  | 38.81 | [10 empty] | 1084 | 1042.9 | 130 | N/A |  |  |  | 986 | [19 empty] | 38.06 | 40 | 1.44 | 1.69 | 3.44 | 0.38 |  | 966.7 | 1016 | 36.6 | 42.9 | 87 | 10
ASME 16.47 Series B | 75 | 40 | 44.69 | 43.06 | 0.875 | 44 | 0.75 | 5.25 | N/A |  |  |  | 40.81 | [10 empty] | 1135 | 1093.7 | 130 | N/A |  |  |  | 1037 | [19 empty] | 40.06 | 42 | 1.44 | 1.69 | 3.57 | 0.38 |  | 1017.5 | 1067 | 36.6 | 42.9 | 91 | 110
ASME 16.47 Series B | 75 | 42 | 46.69 | 45.06 | 0.875 | 48 | 0.75 | 5.25 | N/A |  |  |  | 42.81 | [10 empty] | 1186 | 1144.5 | 135 | N/A |  |  |  | 1087 | [19 empty] | 42.06 | 44 | 1.5 | 1.82 | 3.69 | 0.38 |  | 1068.3 | 1118 | 38.1 | 46.2 | 94 | 10
ASME 16.47 Series B | 75 | 44 | 49.25 | 47.38 | 1 | 36 | 0.875 | 5.75 | N/A |  |  |  | 44.88 | [10 empty] | 1251 | 1203.5 | 150 | N/A |  |  |  | 1140 | [19 empty] | 44.06 | 46.25 | 1.63 | 1.88 | 4.07 | 0.38 |  | 1119.1 | 1175 | 41.4 | 47.8 | 103 | 10
ASME 16.47 Series B | 75 | 46 | 51.25 | 49.38 | 1 | 40 | 0.875 | 6 | N/A |  |  |  | 46.88 | [10 empty] | 1302 | 1254.3 | 150 | N/A |  |  |  | 1191 | [19 empty] | 46.06 | 48.25 | 1.69 | 1.94 | 4.19 | 0.38 |  | 1169.9 | 1226 | 42.9 | 49.3 | 106 | 10
ASME 16.47 Series B | 75 | 48 | 53.25 | 51.38 | 1 | 44 | 0.875 | 6 | N/A |  |  |  | 48.88 | [10 empty] | 1353 | 1305.1 | 160 | N/A |  |  |  | 1242 | [19 empty] | 48.06 | 50.25 | 1.75 | 2.07 | 4.32 | 0.38 |  | 1220.7 | 1276 | 44.6 | 52.6 | 110 | 10
ASME 16.47 Series B | 75 | 50 | 55.25 | 53.38 | 1 | 44 | 0.875 | 6.25 | N/A |  |  |  | 50.94 | [10 empty] | 1403 | 1355.9 | 160 | N/A |  |  |  | 1294 | [19 empty] | 50.06 | 52.25 | 1.82 | 2.13 | 4.5 | 0.38 |  | 1271.5 | 1327 | 46.2 | 54.1 | 114 | 10
ASME 16.47 Series B | 75 | 52 | 57.38 | 55.5 | 1 | 48 | 0.875 | 6.25 | N/A |  |  |  | 52.94 | [10 empty] | 1457 | 1409.7 | 16 | N/A |  |  |  | 1345 | [19 empty] | 52.06 | 54.25 | 1.82 | 2.19 | 4.69 | 0.38 |  | 1322.3 | 1378 | 46.2 | 55.6 | 119 | 10
ASME 16.47 Series B | 75 | 54 | 59.38 | 57.5 | 1 | 48 | 0.875 | 6.25 | N/A |  |  |  | 55 | [10 empty] | 1508 | 1460.5 | 160 | N/A |  |  |  | 1397 | [19 empty] | 54.06 | 56.25 | 1.88 | 2.32 | 4.88 | 0.38 |  | 1373.1 | 1429 | 47.8 | 58.9 | 124 | 10
ASME 16.47 Series B | 75 | 56 | 62 | 59.88 | 1.125 | 40 | 1 | 6.75 | N/A |  |  |  | 57.12 | [10 empty] | 1575 | 1521 | 170 | N/A |  |  |  | 1451 | [19 empty] | 56.06 | 58.5 | 1.94 | 2.38 | 5.25 | 0.44 |  | 1423.9 | 1486 | 49.3 | 60.5 | 133 | 11
ASME 16.47 Series B | 75 | 58 | 64 | 61.88 | 1.125 | 44 | 1 | 7 | N/A |  |  |  | 59.12 | [10 empty] | 1626 | 1571.8 | 180 | N/A |  |  |  | 1502 | [19 empty] | 58.06 | 60.5 | 2 | 2.44 | 5.38 | 0.44 |  | 1474.7 | 1537 | 50.8 | 62 | 137 | 11
ASME 16.47 Series B | 75 | 60 | 66 | 63.88 | 1.125 | 44 | 1 | 7.25 | N/A |  |  |  | 61.12 | [10 empty] | 1676 | 1622.6 | 185 | N/A |  |  |  | 1553 | [19 empty] | 60.06 | 62.5 | 2.13 | 2.57 | 5.63 | 0.44 |  | 1525.5 | 1588 | 54.1 | 65.3 | 143 | 11
ASME 16.47 Series B | 150 | 26 | 30.94 | 29.31 | 0.875 | 36 | 0.75 | 5.5 | N/A |  |  |  | 26.94 | [10 empty] | 786 | 744.5 | 140 | N/A |  |  |  | 683 | [19 empty] | 26.06 | 28 | 1.57 | 1.69 | 3.44 | 0.38 |  | 661.9 | 711 | 39.9 | 42.9 | 87 | 10
ASME 16.47 Series B | 150 | 28 | 32.94 | 31.31 | 0.875 | 40 | 0.75 | 5.75 | N/A |  |  |  | 28.94 | [10 empty] | 837 | 795.3 | 145 | N/A |  |  |  | 735 | [19 empty] | 28.06 | 30 | 1.69 | 1.82 | 3.69 | 0.38 |  | 712.7 | 762 | 42.9 | 46.2 | 94 | 10
ASME 16.47 Series B | 150 | 30 | 34.94 | 33.31 | 0.875 | 44 | 0.75 | 5.75 | N/A |  |  |  | 31 | [10 empty] | 887 | 846.1 | 145 | N/A |  |  |  | 787 | [19 empty] | 30.06 | 32 | 1.69 | 1.94 | 3.88 | 0.38 |  | 763.5 | 813 | 42.9 | 49.3 | 98 | 10
ASME 16.47 Series B | 150 | 32 | 37.06 | 35.44 | 0.875 | 48 | 0.75 | 5.75 | N/A |  |  |  | 33.06 | [10 empty] | 941 | 900.2 | 150 | N/A |  |  |  | 840 | [19 empty] | 32.06 | 34 | 1.75 | 2.07 | 4.19 | 0.38 |  | 814.3 | 864 | 44.4 | 52.6 | 106 | 10
ASME 16.47 Series B | 150 | 34 | 39.56 | 37.69 | 1 | 40 | 0.875 | 6.25 | N/A |  |  |  | 35.12 | [10 empty] | 1005 | 957.3 | 165 | N/A |  |  |  | 892 | [19 empty] | 34.06 | 36.25 | 1.88 | 2.19 | 4.28 | 0.38 |  | 865.1 | 921 | 47.8 | 55.6 | 109 | 10
ASME 16.47 Series B | 150 | 36 | 41.62 | 39.75 | 1 | 44 | 0.875 | 6.5 | N/A |  |  |  | 37.19 | [10 empty] | 1057 | 1009.6 | 165 | N/A |  |  |  | 945 | [19 empty] | 36.06 | 38.25 | 2 | 2.25 | 4.57 | 0.38 |  | 915.9 | 972 | 50.8 | 57.2 | 116 | 10
ASME 16.47 Series B | 150 | 38 | 44.25 | 42.12 | 1.125 | 40 | 1 | 7.25 | N/A |  |  |  | 39.25 | [10 empty] | 1124 | 1069.8 | 185 | N/A |  |  |  | 997 | [19 empty] | 38.12 | 40.25 | 2.07 | 2.44 | 4.82 | 0.38 |  | 968.2 | 1022 | 52.6 | 62 | 122 | 10
ASME 16.47 Series B | 150 | 40 | 46.25 | 44.12 | 1.125 | 44 | 1 | 7.25 | N/A |  |  |  | 41.31 | [10 empty] | 1175 | 1120.6 | 185 | N/A |  |  |  | 1049 | [19 empty] | 40.12 | 42.5 | 2.13 | 2.57 | 5 | 0.38 |  | 1019 | 1080 | 54.1 | 65.3 | 127 | 10
ASME 16.47 Series B | 150 | 42 | 48.25 | 46.12 | 1.125 | 48 | 1 | 7.5 | N/A |  |  |  | 43.38 | [10 empty] | 1226 | 1171.4 | 190 | N/A |  |  |  | 1102 | [19 empty] | 42.12 | 44.5 | 2.25 | 2.63 | 5.19 | 0.44 |  | 1069.8 | 1130 | 57.2 | 66.8 | 132 | 11
ASME 16.47 Series B | 150 | 44 | 50.25 | 48.12 | 1.125 | 52 | 1 | 7.75 | N/A |  |  |  | 445.38 | [10 empty] | 1276 | 1222.2 | 195 | N/A |  |  |  | 1153 | [19 empty] | 44.12 | 46.5 | 2.32 | 2.75 | 5.32 | 0.44 |  | 1120.6 | 1181 | 58.9 | 69.8 | 135 | 11
ASME 16.47 Series B | 150 | 46 | 52.81 | 50.56 | 1.25 | 40 | 1.125 | 8 | N/A |  |  |  | 47.44 | [10 empty] | 1341 | 1284.2 | 205 | N/A |  |  |  | 1205 | [19 empty] | 46.12 | 48.62 | 2.38 | 2.88 | 5.63 | 0.44 |  | 1171.4 | 1235 | 60.5 | 73.2 | 143 | 11
ASME 16.47 Series B | 150 | 48 | 54.81 | 52.56 | 1.25 | 44 | 1.125 | 8.25 | N/A |  |  |  | 49.5 | [10 empty] | 1392 | 1335 | 210 | N/A |  |  |  | 1257 | [19 empty] | 48.12 | 50.75 | 2.5 | 3 | 5.82 | 0.44 |  | 1222.2 | 1289 | 63.5 | 76.2 | 148 | 11
ASME 16.47 Series B | 150 | 50 | 56.81 | 54.56 | 1.25 | 48 | 1.125 | 8.5 | N/A |  |  |  | 51.5 | [10 empty] | 1443 | 1385.8 | 215 | N/A |  |  |  | 1308 | [19 empty] | 50.12 | 52.75 | 2.63 | 3.13 | 6 | 0.44 |  | 1273 | 1340 | 66.8 | 79.5 | 152 | 11
ASME 16.47 Series B | 150 | 52 | 58.81 | 56.56 | 1.25 | 52 | 1.125 | 8.75 | N/A |  |  |  | 53.56 | [10 empty] | 1494 | 1436.6 | 220 | N/A |  |  |  | 1360 | [19 empty] | 52.12 | 54.75 | 2.69 | 3.25 | 6.13 | 0.44 |  | 1323.8 | 1391 | 68.3 | 82.6 | 156 | 11
ASME 16.47 Series B | 150 | 54 | 61 | 58.75 | 1.25 | 56 | 1.125 | 8.75 | N/A |  |  |  | 55.62 | [10 empty] | 1549 | 1492.2 | 225 | N/A |  |  |  | 1413 | [19 empty] | 54.12 | 56.75 | 2.75 | 3.38 | 6.32 | 0.44 |  | 1374.6 | 1441 | 69.8 | 85.9 | 161 | 11
ASME 16.47 Series B | 150 | 56 | 63 | 60.75 | 1.25 | 60 | 1.125 | 9 | N/A |  |  |  | 57.62 | [10 empty] | 1600 | 1543 | 225 | N/A |  |  |  | 1465 | [19 empty] | 56.12 | 58.75 | 2.82 | 3.5 | 6.5 | 0.56 |  | 1425.4 | 1492 | 71.6 | 88.9 | 165 | 14
ASME 16.47 Series B | 150 | 58 | 65.94 | 63.44 | 1.375 | 48 | 1.25 | 9.25 | N/A |  |  |  | 59.69 | [10 empty] | 1675 | 1611.4 | 235 | N/A |  |  |  | 1516 | [19 empty] | 58.12 | 60.75 | 2.88 | 3.62 | 6.82 | 0.56 |  | 1476.2 | 1543 | 73.2 | 91.9 | 173 | 14
ASME 16.47 Series B | 150 | 60 | 67.94 | 65.44 | 1.375 | 52 | 1.25 | 9.5 | N/A |  |  |  | 61.81 | [10 empty] | 1726 | 1662.2 | 240 | N/A |  |  |  | 1570 | [19 empty] | 60.12 | 63 | 2.94 | 3.75 | 7 | 0.56 |  | 1527 | 1600 | 74.7 | 95.2 | 178 | 14
ASME 16.47 Series B | 300 | 26 | 34.12 | 31.62 | 1.375 | 32 | 1.25 | 10.5 | N/A |  |  |  | 27.62 | [10 empty] | 867 | 803.1 | 270 | N/A |  |  |  | 702 | [19 empty] | 26.19 | 29 | 3.44 | 3.44 | 5.63 | 0.56 |  | 665.2 | 737 | 87.4 | 87.4 | 143 | 14
ASME 16.47 Series B | 300 | 28 | 36.25 | 33.75 | 1.375 | 36 | 1.25 | 10.5 | N/A |  |  |  | 29.75 | [10 empty] | 921 | 857.2 | 270 | N/A |  |  |  | 756 | [19 empty] | 28.19 | 31 | 3.44 | 3.44 | 5.81 | 0.56 |  | 716 | 787 | 87.4 | 87.4 | 148 | 14
ASME 16.47 Series B | 300 | 30 | 39 | 36.25 | 1.5 | 36 | 1.375 | 11.25 | N/A |  |  |  | 32 | [10 empty] | 991 | 920.8 | 285 | N/A |  |  |  | 813 | [19 empty] | 30.25 | 33.25 | 3.63 | 3.63 | 6.16 | 0.56 |  | 768.4 | 845 | 92.2 | 92.2 | 156 | 14
ASME 16.47 Series B | 300 | 32 | 41.5 | 38.5 | 1.625 | 32 | 1.5 | 12.25 | N/A |  |  |  | 34 | [10 empty] | 1054 | 977.9 | 310 | N/A |  |  |  | 864 | [19 empty] | 32.25 | 35.5 | 4 | 4 | 6.56 | 0.62 |  | 819.2 | 902 | 101.6 | 101.6 | 167 | 16
ASME 16.47 Series B | 300 | 34 | 43.62 | 40.62 | 1.625 | 36 | 1.5 | 12.25 | N/A |  |  |  | 36.12 | [10 empty] | 1108 | 1031.7 | 310 | N/A |  |  |  | 917 | [19 empty] | 34.25 | 37.5 | 4 | 4 | 6.75 | 0.62 |  | 870 | 952 | 101.6 | 101.6 | 171 | 16
ASME 16.47 Series B | 300 | 36 | 46.12 | 42.88 | 1.75 | 32 | 1.625 | 12.5 | N/A |  |  |  | 38 | [10 empty] | 1171 | 1089.2 | 320 | N/A |  |  |  | 965 | [19 empty] | 36.25 | 39.75 | 4 | 4 | 7.06 | 0.62 |  | 920.8 | 1010 | 101.6 | 101.6 | 179 | 16
ASME 16.47 Series B | 300 | 38 | 48.12 | 44.88 | 1.75 | 36 | 1.625 | 13 | N/A |  |  |  | 40 | [10 empty] | 1222 | 1140 | 335 | N/A |  |  |  | 1016 | [19 empty] | 38.25 | 41.75 | 4.31 | 4.31 | 7.5 | 0.62 |  | 971.6 | 1060 | 109.5 | 109.5 | 190 | 16
ASME 16.47 Series B | 300 | 40 | 50.12 | 46.88 | 1.75 | 40 | 1.625 | 13.5 | N/A |  |  |  | 42 | [10 empty] | 1273 | 1190.8 | 345 | N/A |  |  |  | 1067 | [19 empty] | 40.25 | 43.88 | 4.5 | 4.5 | 7.75 | 0.62 |  | 1022.4 | 1115 | 114.3 | 114.3 | 197 | 16
ASME 16.47 Series B | 300 | 42 | 52.5 | 49 | 1.875 | 36 | 1.75 | 14 | N/A |  |  |  | 44 | [10 empty] | 1334 | 1244.6 | 355 | N/A |  |  |  | 1118 | [19 empty] | 42.31 | 46 | 4.63 | 4.63 | 8 | 0.62 |  | 1074.7 | 1168 | 117.6 | 117.6 | 203 | 16
ASME 16.47 Series B | 300 | 44 | 54.5 | 51 | 1.875 | 40 | 1.75 | 14.5 | N/A |  |  |  | 46.19 | [10 empty] | 1384 | 1295.4 | 370 | N/A |  |  |  | 1173 | [19 empty] | 44.31 | 48 | 4.94 | 4.94 | 8.38 | 0.62 |  | 1125.5 | 1219 | 125.5 | 125.5 | 213 | 16
ASME 16.47 Series B | 300 | 46 | 57.5 | 53.75 | 2 | 36 | 1.875 | 15 | N/A |  |  |  | 48.38 | [10 empty] | 1460 | 1365.2 | 380 | N/A |  |  |  | 1229 | [19 empty] | 46.31 | 50 | 5 | 5.06 | 8.69 | 0.62 |  | 1176.3 | 1270 | 127 | 128.5 | 221 | 16
ASME 16.47 Series B | 300 | 48 | 59.5 | 55.75 | 2 | 40 | 1.875 | 15 | N/A |  |  |  | 50.31 | [10 empty] | 1511 | 1416 | 380 | N/A |  |  |  | 1278 | [19 empty] | 48.31 | 52.25 | 5 | 5.25 | 8.75 | 0.62 |  | 1227.1 | 1327 | 127 | 133.4 | 222 | 16
ASME 16.47 Series B | 300 | 50 | 61.5 | 57.75 | 2 | 44 | 1.875 | 15.75 | N/A |  |  |  | 52.38 | [10 empty] | 1562 | 1466.8 | 400 | N/A |  |  |  | 1330 | [19 empty] | 50.31 | 54.25 | 5.38 | 5.44 | 9.19 | 0.62 |  | 1277.9 | 1378 | 136.7 | 138.2 | 233 | 16
ASME 16.47 Series B | 300 | 52 | 63.5 | 59.75 | 2 | 48 | 1.875 | 16 | N/A |  |  |  | 54.44 | [10 empty] | 1613 | 1517.6 | 410 | N/A |  |  |  | 1383 | [19 empty] | 52.31 | 56.25 | 5.56 | 5.61 | 9.5 | 0.62 |  | 1328.7 | 1429 | 141.2 | 142.5 | 241 | 16
ASME 16.47 Series B | 300 | 54 | 65.88 | 62.12 | 2 | 48 | 1.875 | 15.75 | N/A |  |  |  | 56.5 | [10 empty] | 1673 | 1577.8 | 400 | N/A |  |  |  | 1435 | [19 empty] | 54.31 | 58.25 | 5.32 | 5.81 | 9.38 | 0.62 |  | 1379.5 | 1480 | 135.1 | 147.6 | 238 | 16
ASME 16.47 Series B | 300 | 56 | 69.5 | 65 | 2.375 | 36 | 2.25 | 17.75 | N/A |  |  |  | 58.81 | [10 empty] | 1765 | 1651 | 450 | N/A |  |  |  | 1494 | [19 empty] | 56.31 | 60.5 | 6 | 6.12 | 10.5 | 0.69 |  | 14300.3 | 1537 | 152.4 | 155.4 | 267 | 17
ASME 16.47 Series B | 300 | 58 | 71.94 | 67.44 | 2.375 | 40 | 2.25 | 17.75 | N/A |  |  |  | 60.94 | [10 empty] | 1827 | 1713 | 450 | N/A |  |  |  | 1548 | [19 empty] | 58.31 | 62.75 | 6 | 6.31 | 10.75 | 0.69 |  | 1481.1 | 1594 | 152.4 | 160.3 | 273 | 17
ASME 16.47 Series B | 300 | 60 | 73.94 | 69.44 | 2.375 | 40 | 2.25 | 17.5 | N/A |  |  |  | 62.94 | [10 empty] | 1878 | 1763.8 | 450 | N/A |  |  |  | 1599 | [19 empty] | 60.31 | 65 | 5.88 | 6.5 | 10.63 | 0.69 |  | 1531.9 | 1651 | 149.4 | 165.1 | 270 | 17
ASME 16.1 | 25 | 4 | 9 |  | 0.75 | 8 | 0.625 | [5 empty] | 5.31 | [10 empty] | 230 | [6 empty] | 135 | [32 empty] | 0.75 | N/A | 7.5 | 1.31 | N/A | N/A | N/A | 2.5 | N/A | 19 | N/A | 191 | 33 | N/A | N/A | N/A | 64 | N/A
ASME 16.1 | 25 | 5 | 10 |  | 0.75 | 8 | 0.625 | [5 empty] | 6.44 | [10 empty] | 255 | [6 empty] | 164 | [32 empty] | 0.75 | N/A | 8.5 | 1.44 | N/A | N/A | N/A | 2.5 | N/A | 19 | N/A | 216 | 37 | N/A | N/A | N/A | 64 | N/A
ASME 16.1 | 25 | 6 | 11 |  | 0.75 | 8 | 0.625 | [5 empty] | 7.56 | [10 empty] | 280 | [6 empty] | 192 | [32 empty] | 0.75 | N/A | 9.5 | 1.56 | N/A | N/A | N/A | 2.5 | N/A | 19 | N/A | 241 | 40 | N/A | N/A | N/A | 64 | N/A
ASME 16.1 | 25 | 8 | 13.5 |  | 0.75 | 8 | 0.625 | [5 empty] | 9.69 | [10 empty] | 345 | [6 empty] | 246 | [32 empty] | 0.75 | N/A | 11.75 | 1.75 | N/A | N/A | N/A | 2.5 | N/A | 19 | N/A | 299 | 45 | N/A | N/A | N/A | 64 | N/A
ASME 16.1 | 25 | 10 | 16 |  | 0.75 | 12 | 0.625 | [5 empty] | 11.94 | [10 empty] | 405 | [6 empty] | 303 | [32 empty] | 0.88 | N/A | 14.25 | 1.94 | N/A | N/A | N/A | 3 | N/A | 22.2 | N/A | 368 | 49 | N/A | N/A | N/A | 70 | N/A
ASME 16.1 | 25 | 12 | 19 |  | 0.75 | 12 | 0.625 | [5 empty] | 14.06 | [10 empty] | 485 | [6 empty] | 357 | [32 empty] | 1 | N/A | 17 | 2.19 | N/A | N/A | N/A | 3 | N/A | 25.4 | N/A | 432 | 56 | N/A | N/A | N/A | 76 | N/A
ASME 16.1 | 25 | 14 | 21 |  | 0.875 | 12 | 0.75 | [5 empty] | 15.37 | [10 empty] | 535 | [6 empty] | 391 | [32 empty] | 1.12 | N/A | 18.75 | 2.25 | N/A | N/A | N/A | 3.5 | N/A | 28.6 | N/A | 476 | 57 | N/A | N/A | N/A | 89 | N/A
ASME 16.1 | 25 | 16 | 23.5 |  | 0.875 | 16 | 0.75 | [5 empty] | 17.5 | [10 empty] | 595 | [6 empty] | 445 | [32 empty] | 1.12 | N/A | 21.25 | 2.5 | N/A | N/A | N/A | 3.5 | N/A | 28.6 | N/A | 540 | 64 | N/A | N/A | N/A | 89 | N/A
ASME 16.1 | 25 | 18 | 25 |  | 0.875 | 16 | 0.75 | [5 empty] | 19.62 | [10 empty] | 635 | [6 empty] | 498 | [32 empty] | 1.25 | N/A | 22.75 | 2.69 | N/A | N/A | N/A | 4 | N/A | 31.8 | N/A | 578 | 68 | N/A | N/A | N/A | 95 | N/A
ASME 16.1 | 25 | 20 | 27.5 |  | 0.875 | 20 | 0.75 | [5 empty] | 21.75 | [10 empty] | 700 | [6 empty] | 552 | [32 empty] | 1.25 | N/A | 25 | 2.88 | N/A | N/A | N/A | 4 | N/A | 31.8 | N/A | 635 | 78 | N/A | N/A | N/A | 95 | N/A
ASME 16.1 | 25 | 24 | 32 |  | 0.875 | 20 | 0.75 | [5 empty] | 26 | [10 empty] | 815 | [6 empty] | 560 | [32 empty] | 1.38 | N/A | 29.5 | 3.25 | N/A | N/A | N/A | 4 | N/A | 34.9 | N/A | 749 | 83 | N/A | N/A | N/A | 102 | N/A
ASME 16.1 | 25 | 30 | 38.75 |  | 1 | 28 | 0.875 | [5 empty] | … | [10 empty] | 985 | [6 empty] | … | [32 empty] | 1.5 | N/A | 36 | … | N/A | N/A | N/A | 4.5 | N/A | 38.1 | N/A | 914 | … | N/A | N/A | N/A | 114 | N/A
ASME 16.1 | 25 | 36 | 46 |  | 1 | 32 | 0.875 | [5 empty] | … | [10 empty] | 1170 | [6 empty] | … | [32 empty] | 1.62 | N/A | 42.75 | … | N/A | N/A | N/A | 5 | N/A | 41.3 | N/A | 1085 | … | N/A | N/A | N/A | 121 | N/A
ASME 16.1 | 25 | 42 | 53 |  | 1.125 | 36 | 1 | [5 empty] | … | [10 empty] | 1345 | [6 empty] | … | [32 empty] | 1.75 | N/A | 49.5 | … | N/A | N/A | N/A | 5.5 | N/A | 44.5 | N/A | 1257 | … | N/A | N/A | N/A | 133 | N/A
ASME 16.1 | 25 | 48 | 59.5 |  | 1.125 | 44 | 1 | [5 empty] | … | [10 empty] | 1510 | [6 empty] | … | [32 empty] | 2 | N/A | 56 | … | N/A | N/A | N/A | 6 | N/A | 50.8 | N/A | 1422 | … | N/A | N/A | N/A | 146 | N/A
ASME 16.1 | 25 | 54 | 66.25 |  | 1.125 | 44 | 1 | [5 empty] | … | [10 empty] | 1685 | [6 empty] | … | [32 empty] | 2.25 | N/A | 62.75 | … | N/A | N/A | N/A | 6.5 | N/A | 57.2 | N/A | 1594 | … | N/A | N/A | N/A | 159 | N/A
ASME 16.1 | 25 | 60 | 73 |  | 1.25 | 52 | 1.125 | [5 empty] | … | [10 empty] | 1855 | [6 empty] | … | [32 empty] | 2.25 | N/A | 69.25 | … | N/A | N/A | N/A | 6.5 | N/A | 57.2 | N/A | 1759 | … | N/A | N/A | N/A | 159 | N/A
ASME 16.1 | 25 | 72 | 86.5 |  | 1.25 | 60 | 1.125 | [5 empty] | … | [10 empty] | 2195 | [6 empty] | … | [32 empty] | 2.5 | N/A | 82.5 | … | N/A | N/A | N/A | 7 | N/A | 63.5 | N/A | 2095 | … | N/A | N/A | N/A | 172 | N/A
ASME 16.1 | 25 | 84 | 99.75 |  | 1.375 | 64 | 1.25 | [5 empty] | … | [10 empty] | 2535 | [6 empty] | … | [32 empty] | 2.75 | N/A | 95.5 | … | N/A | N/A | N/A | 7.5 | N/A | 69.9 | N/A | 2425 | … | N/A | N/A | N/A | 191 | N/A
ASME 16.1 | 25 | 96 | 113.25 |  | 1.375 | 68 | 1.25 | [5 empty] | … | [10 empty] | 2875 | [6 empty] | … | [32 empty] | 3 | N/A | 108.5 | … | N/A | N/A | N/A | 8 | N/A | 76.2 | N/A | 2756 | … | N/A | N/A | N/A | 203 | N/A
ASME 16.1 | 125 | 1 | 4.25 |  | 0.625 | 4 | 0.5 | [5 empty] | 1.94 | [10 empty] | 110 | [6 empty] | 49 | [32 empty] | 0.44 | N/A | 3.12 | 0.69 | N/A | 1 | 0.38 | 2 | … | 11.1 | N/A | 79 | 18 | N/A | 25 | 9.6 | 45 | …
ASME 16.1 | 125 | 1.25 | 4.62 |  | 0.625 | 4 | 0.5 | [5 empty] | 2.31 | [10 empty] | 115 | [6 empty] | 59 | [32 empty] | 0.5 | N/A | 3.5 | 0.81 | N/A | 1.25 | 0.44 | 2 | … | 12.7 | N/A | 89 | 21 | N/A | 32 | 11.1 | 51 | …
ASME 16.1 | 125 | 1.5 | 5 |  | 0.625 | 4 | 0.5 | [5 empty] | 2.56 | [10 empty] | 125 | [6 empty] | 65 | [32 empty] | 0.56 | N/A | 3.88 | 0.88 | N/A | 1.5 | 0.5 | 2 | … | 14.3 | N/A | 98 | 22 | N/A | 38 | 12.7 | 51 | …
ASME 16.1 | 125 | 2 | 6 |  | 0.75 | 4 | 0.625 | [5 empty] | 3.06 | [10 empty] | 150 | [6 empty] | 78 | [32 empty] | 0.62 | N/A | 4.75 | 1 | N/A | 2 | 0.56 | 2.5 | … | 15.9 | N/A | 121 | 25 | N/A | 51 | 14.3 | 57 | …
ASME 16.1 | 125 | 2.5 | 7 |  | 0.75 | 4 | 0.625 | [5 empty] | 3.56 | [10 empty] | 180 | [6 empty] | 91 | [32 empty] | 0.69 | N/A | 5.5 | 1.12 | N/A | 2.5 | 0.63 | 2.5 | … | 17.5 | N/A | 140 | 29 | N/A | 64 | 15.9 | 64 | …
ASME 16.1 | 125 | 3 | 7.5 |  | 0.75 | 4 | 0.625 | [5 empty] | 4.25 | [10 empty] | 190 | [6 empty] | 108 | [32 empty] | 0.75 | N/A | 6 | 1.19 | N/A | 3 | 0.69 | 2.5 | … | 19 | N/A | 152 | 30 | N/A | 76 | 17.5 | 64 | …
ASME 16.1 | 125 | 3.5 | 8.5 |  | 0.75 | 8 | 0.625 | [5 empty] | 4.81 | [10 empty] | 215 | [6 empty] | 122 | [32 empty] | 0.81 | N/A | 7 | 1.25 | N/A | 3.5 | 0.75 | 3 | … | 20.6 | N/A | 178 | 32 | N/A | 89 | 19 | 70 | …
ASME 16.1 | 125 | 4 | 9 |  | 0.75 | 8 | 0.625 | [5 empty] | 5.31 | [10 empty] | 230 | [6 empty] | 135 | [32 empty] | 0.94 | N/A | 7.5 | 1.31 | N/A | 4 | 0.88 | 3 | … | 23.8 | N/A | 191 | 33 | N/A | 102 | 22.2 | 76 | …
ASME 16.1 | 125 | 5 | 10 |  | 0.875 | 8 | 0.75 | [5 empty] | 6.44 | [10 empty] | 255 | [6 empty] | 164 | [32 empty] | 0.94 | N/A | 8.5 | 1.44 | N/A | 5 | 0.88 | 3 | … | 23.8 | N/A | 216 | 37 | N/A | 125 | 22.2 | 76 | …
ASME 16.1 | 125 | 6 | 11 |  | 0.875 | 8 | 0.75 | [5 empty] | 7.56 | [10 empty] | 280 | [6 empty] | 192 | [32 empty] | 1 | N/A | 9.5 | 1.56 | N/A | 6 | 0.94 | 3.5 | … | 25.4 | N/A | 241 | 40 | N/A | 152 | 23.8 | 83 | …
ASME 16.1 | 125 | 8 | 13.5 |  | 0.875 | 8 | 0.75 | [5 empty] | 9.69 | [10 empty] | 345 | [6 empty] | 246 | [32 empty] | 1.12 | N/A | 11.75 | 1.75 | N/A | 8 | 1.06 | 3.5 | … | 28.6 | N/A | 299 | 45 | N/A | 203 | 27 | 89 | …
ASME 16.1 | 125 | 10 | 16 |  | 1 | 12 | 0.875 | [5 empty] | 11.94 | [10 empty] | 405 | [6 empty] | 303 | [32 empty] | 1.19 | N/A | 14.25 | 1.94 | N/A | 10 | 1.12 | 4 | … | 30.2 | N/A | 362 | 49 | N/A | 254 | 28.6 | 95 | …
ASME 16.1 | 125 | 12 | 19 |  | 1 | 12 | 0.875 | [5 empty] | 14.06 | [10 empty] | 485 | [6 empty] | 357 | [32 empty] | 1.25 | N/A | 17 | 2.19 | N/A | 12 | 0.81 | 4 | … | 31.8 | N/A | 432 | 56 | N/A | 305 | 20.6 | 95 | …
ASME 16.1 | 125 | 14 | 14 |  | 1.125 | 12 | 1 | [5 empty] | 15.38 | [10 empty] | 535 | [6 empty] | 391 | [32 empty] | 1.38 | N/A | 18.75 | 2.25 | N/A | 14 | 0.88 | 4.5 | … | 35.1 | N/A | 476 | 57 | N/A | 356 | 22.2 | 108 | …
ASME 16.1 | 125 | 16 | 23.5 |  | 1.125 | 16 | 1 | [5 empty] | 17.5 | [10 empty] | 595 | [6 empty] | 445 | [32 empty] | 1.44 | N/A | 21.25 | 2.5 | N/A | 16 | 1 | 4.5 | … | 36.5 | N/A | 540 | 64 | N/A | 406 | 25.4 | 114 | …
ASME 16.1 | 125 | 18 | 25 |  | 1.25 | 16 | 1.125 | [5 empty] | 19.62 | [10 empty] | 635 | [6 empty] | 499 | [32 empty] | 1.56 | N/A | 22.75 | 2.69 | N/A | 18 | 1.06 | 5 | … | 39.7 | N/A | 578 | 68 | N/A | 457 | 27 | 121 | …
ASME 16.1 | 125 | 20 | 27.5 |  | 1.25 | 20 | 1.125 | [5 empty] | 21.75 | [10 empty] | 700 | [6 empty] | 553 | [32 empty] | 1.69 | N/A | 25 | 2.88 | N/A | 20 | 1.12 | 5 | … | 42.9 | N/A | 635 | 73 | N/A | 508 | 28.6 | 127 | …
ASME 16.1 | 125 | 24 | 32 |  | 1.375 | 20 | 1.25 | [5 empty] | 26 | [10 empty] | 815 | [6 empty] | 660 | [32 empty] | 1.88 | N/A | 29.5 | 3.25 | N/A | 24 | 1.25 | 5.5 | … | 47.6 | N/A | 749 | 83 | N/A | 610 | 31.8 | 140 | …
ASME 16.1 | 125 | 30 | 38.75 |  | 1.375 | 28 | 1.25 | [5 empty] | … | [10 empty] | 985 | [6 empty] | … | [32 empty] | 2.12 | N/A | 36 | … | N/A | 30 | 1.44 | 6.5 | … | 54 | N/A | 914 | … | N/A | 762 | 36.6 | 159 | …
ASME 16.1 | 125 | 36 | 46 |  | 1.625 | 32 | 1.5 | [5 empty] | … | [10 empty] | 1170 | [6 empty] | … | [32 empty] | 2.38 | N/A | 42.75 | … | N/A | 36 | 1.62 | 7 | 9 | 60.3 | N/A | 1086 | … | N/A | 914 | 41.3 | 178 | 222
ASME 16.1 | 125 | 42 | 53 |  | 1.625 | 36 | 1.5 | [5 empty] | … | [10 empty] | 1345 | [6 empty] | … | [32 empty] | 2.62 | N/A | 49.5 | … | N/A | 42 | 1.81 | 7.5 | 9.5 | 66.7 | N/A | 1257 | … | N/A | 1066 | 46 | 191 | 235
ASME 16.1 | 125 | 48 | 59.5 |  | 1.625 | 44 | 1.5 | [5 empty] | … | [10 empty] | 1510 | [6 empty] | … | [32 empty] | 2.75 | N/A | 56 | … | N/A | 48 | 2 | 8 | 9.5 | 69.9 | N/A | 1422 | … | N/A | 1219 | 50.8 | 197 | 242
ASME 16.1 | 125 | 54 (9) | 66.25 |  | 2 | 44 | 1.75 | [5 empty] | … | [10 empty] | 1685 | [6 empty] | … | [32 empty] | 3 | N/A | 62.75 | … | N/A | … | … | 8.5 | 10.5 | 76.2 | N/A | 1594 | … | N/A | … | … | 216 | 267
ASME 16.1 | 125 | 60 (9) | 73 |  | 2 | 52 | 1.75 | [5 empty] | … | [10 empty] | 1855 | [6 empty] | … | [32 empty] | 3.12 | N/A | 69.25 | … | N/A | … | … | 9 | 11 | 79.4 | N/A | 1759 | … | N/A | … | … | 222 | 273
ASME 16.1 | 125 | 66 (9) | 80 |  | 2 | 52 | 1.75 | [5 empty] | … | [10 empty] | 2032 | [6 empty] | … | [32 empty] | 3.38 | N/A | 76 | … | N/A | … | … | 9.5 | 11.5 | 85.7 | N/A | 1930 | … | N/A | … | … | 241 | 292
ASME 16.1 | 125 | 72 (9) | 86.5 |  | 2 | 60 | 1.75 | [5 empty] | … | [10 empty] | 2195 | [6 empty] | … | [32 empty] | 3.5 | N/A | 82.5 | … | N/A | … | … | 9.5 | 11.5 | 88.9 | N/A | 2096 | … | N/A | … | … | 241 | 292
ASME 16.1 | 125 | 78 (9) | 93 |  | 2.25 | 64 | 2 | [5 empty] | … | [10 empty] | 2365 | [6 empty] | … | [32 empty] | 3.75 | N/A | 89 | … | N/A | … | … | 10.5 | 12.5 | 95.3 | N/A | 2261 | … | N/A | … | … | 267 | 318
ASME 16.1 | 125 | 84 (9) | 99.75 |  | 2.25 | 64 | 2 | [5 empty] | … | [10 empty] | 2535 | [6 empty] | … | [32 empty] | 3.88 | N/A | 95.5 | … | N/A | … | … | 10.5 | 13 | 98.4 | N/A | 2426 | … | N/A | … | … | 267 | 324
ASME 16.1 | 125 | 90 (9) | 106.5 |  | 2.5 | 68 | 2.25 | [5 empty] | … | [10 empty] | 2720 | [6 empty] | … | [32 empty] | 4.12 | N/A | 102 | … | N/A | … | … | 11.5 | 14 | 104.6 | N/A | 2591 | … | N/A | … | … | 292 | 357
ASME 16.1 | 125 | 96 (9) | 113.25 |  | 2.5 | 68 | 2.25 | [5 empty] | … | [10 empty] | 2875 | [6 empty] | … | [32 empty] | 4.25 | N/A | 108.5 | … | N/A | … | … | 11.5 | 14 | 108 | N/A | 2756 | … | N/A | … | … | 292 | 356
ASME 16.1 | 250 | 1 | 4.88 |  | 0.75 | 4 | 0.62 | [5 empty] | 2.06 | [10 empty] | 125 | [6 empty] | 52 | [32 empty] | 0.69 | 2.69 | 3.5 | 0.88 | 0.68 | 1 | … | 2.5 | … | 17.5 | 68 | 89 | 22 | 18 | 25 | … | 64 | …
ASME 16.1 | 250 | 1.25 | 5.25 |  | 0.75 | 4 | 0.62 | [5 empty] | 2.5 | [10 empty] | 135 | [6 empty] | 64 | [32 empty] | 0.75 | 3.06 | 3.88 | 1 | 0.81 | 1.25 | … | 2.5 | … | 19 | 78 | 98 | 25 | 19 | 32 | … | 64 | …
ASME 16.1 | 250 | 1.5 | 6.12 |  | 0.875 | 4 | 0.75 | [5 empty] | 2.75 | [10 empty] | 155 | [6 empty] | 70 | [32 empty] | 0.81 | 3.56 | 4.5 | 1.12 | 0.87 | 1.5 | … | 3 | … | 20.6 | 91 | 114 | 29 | 22 | 38 | … | 70 | …
ASME 16.1 | 250 | 2 | 6.5 |  | 0.75 | 8 | 0.62 | [5 empty] | 3.31 | [10 empty] | 165 | [6 empty] | 84 | [32 empty] | 0.88 | 4.19 | 5 | 1.25 | 1 | 2 | .. | 3 | … | 22.2 | 106 | 127 | 32 | 25 | 51 | … | 70 | …
ASME 16.1 | 250 | 2.5 | 7.5 |  | 0.875 | 8 | 0.75 | [5 empty] | 3.94 | [10 empty] | 190 | [6 empty] | 100 | [32 empty] | 1 | 4.94 | 5.88 | 1.43 | 1.13 | 2.5 | … | 3.5 | … | 25.4 | 125 | 149 | 37 | 29 | 64 | … | 83 | …
ASME 16.1 | 250 | 3 | 8.25 |  | 0.875 | 8 | 0.75 | [5 empty] | 4.62 | [10 empty] | 210 | [6 empty] | 118 | [32 empty] | 1.12 | 5.69 | 6.62 | 1.56 | 1.19 | 3 | … | 3.5 | … | 28.6 | 144 | 168 | 40 | 31 | 76 | … | 89 | …
ASME 16.1 | 250 | 3.5 | 9 |  | 0.875 | 8 | 0.75 | [5 empty] | 5.25 | [10 empty] | 230 | [6 empty] | 133 | [32 empty] | 1.19 | 6.31 | 7.25 | 1.62 | 1.25 | 3.5 | .. | 3.5 | … | 30.2 | 160 | 184 | 41 | 32 | 89 | … | 89 | …
ASME 16.1 | 250 | 4 | 10 |  | 0.875 | 8 | 0.75 | [5 empty] | 5.75 | [10 empty] | 255 | [6 empty] | 146 | [32 empty] | 1.25 | 6.94 | 7.88 | 1.75 | 1.31 | 4 | … | 4 | … | 31.8 | 176 | 200 | 44 | 33 | 102 | … | 95 | …
ASME 16.1 | 250 | 5 | 11 |  | 0.875 | 8 | 0.75 | [5 empty] | 7 | [10 empty] | 280 | [6 empty] | 178 | [32 empty] | 1.38 | 8.31 | 9.25 | 1.88 | 1.44 | 5 | … | 4 | … | 34.9 | 211 | 235 | 48 | 36 | 127 | … | 102 | …
ASME 16.1 | 250 | 6 | 12.5 |  | 0.875 | 12 | 0.75 | [5 empty] | 8.12 | [10 empty] | 320 | [6 empty] | 206 | [32 empty] | 1.44 | 9.69 | 10.62 | 1.94 | 1.56 | 6 | .. | 4 | … | 36.5 | 246 | 270 | 49 | 39 | 152 | … | 102 | …
ASME 16.1 | 250 | 8 | 15 |  | 1.125 | 12 | 0.88 | [5 empty] | 10.25 | [10 empty] | 380 | [6 empty] | 260 | [32 empty] | 1.62 | 11.94 | 13 | 2.19 | 1.75 | 8 | … | 4.5 | … | 41.3 | 303 | 330 | 56 | 43 | 203 | … | 114 | …
ASME 16.1 | 250 | 10 | 17.5 |  | 1.25 | 16 | 1 | [5 empty] | 12.62 | [10 empty] | 445 | [6 empty] | 321 | [32 empty] | 1.88 | 14.06 | 15.25 | 2.38 | 1.94 | 10 | 0.94 | 5.5 | … | 47.6 | 357 | 387 | 60 | 49 | 254 | 23.8 | 131 | …
ASME 16.1 | 250 | 12 | 20.5 |  | 1.25 | 16 | 1.12 | [5 empty] | 14.75 | [10 empty] | 520 | [6 empty] | 375 | [32 empty] | 2 | 16.44 | 17.75 | 2.56 | 2.19 | 12 | 1 | 5.5 | … | 50.8 | 418 | 451 | 65 | 54 | 305 | 25.4 | 140 | …
ASME 16.1 | 250 | 14 | 23 |  | 1.375 | 20 | 1.12 | [5 empty] | 16.25 | [10 empty] | 585 | [6 empty] | 413 | [32 empty] | 2.12 | 18.94 | 20.25 | 2.69 | 2.25 | 13.25 | 1.12 | 6 | … | 54 | 481 | 514 | 68 | 57 | 337 | 28.6 | 152 | …
ASME 16.1 | 250 | 16 | 25 |  | 1.375 | 20 | 1.25 | [5 empty] | 18.38 | [10 empty] | 650 | [6 empty] | 467 | [32 empty] | 2.25 | 21.06 | 22.5 | 2.88 | 2.5 | 15.25 | 1.25 | 6.5 | … | 57.2 | 535 | 572 | 73 | 62 | 387 | 31.8 | 159 | …
ASME 16.1 | 250 | 18 | 28 |  | 1.375 | 24 | 1.25 | [5 empty] | … | [10 empty] | 710 | [6 empty] | … | [32 empty] | 2.38 | 23.31 | 24.75 | … | … | 17 | 1.38 | 6.5 | … | 60.3 | 592 | 629 | … | … | 432 | 34.9 | 165 | …
ASME 16.1 | 250 | 20 | 30.5 |  | 1.375 | 24 | 1.25 | [5 empty] | … | [10 empty] | 775 | [6 empty] | … | [32 empty] | 2.5 | 25.56 | 27 | … | … | 19 | 1.5 | 7 | … | 63.5 | 649 | 686 | … | … | 483 | 38.1 | 172 | …
ASME 16.1 | 250 | 24 | 36 |  | 1.625 | 24 | 1.5 | [5 empty] | … | [10 empty] | 915 | [6 empty] | … | [32 empty] | 2.75 | 30.31 | 32 | … | … | 23 | 1.62 | 7.5 | 9.5 | 69.8 | 770 | 813 | … | … | 584 | 41.3 | 191 | 241
ASME 16.1 | 250 | 30 | 43 |  | 2 | 28 | 1.75 | [5 empty] | … | [10 empty] | 1090 | [6 empty] | … | [32 empty] | 3 | 37.19 | 39.25 | … | … | 29 | 2 | 8.5 | 10.5 | 76.2 | 945 | 997 | … | … | 737 | 50.8 | 216 | 268
ASME 16.1 | 250 | 36 (10) | 50 |  | 2.25 | 32 | 2 | [5 empty] | … | [10 empty] | 1270 | [6 empty] | … | [32 empty] | 3.38 | 43.69 | 46 | … | … | … | … | 9.5 | 12 | 85.7 | 1110 | 1168 | … | … | … | … | 241 | 298
ASME 16.1 | 250 | 42 (10) | 57 |  | 2.25 | 36 | 2 | [5 empty] | … | [10 empty] | 1450 | [6 empty] | … | [32 empty] | 3.69 | 50.44 | 52.75 | … | … | … | … | 10 | 12.5 | 93.7 | 1281 | 1340 | … | … | … | … | 254 | 318
ASME 16.1 | 250 | 48 (10) | 65 |  | 2.25 | 40 | 2 | [5 empty] | … | [10 empty] | 1650 | [6 empty] | … | [32 empty] | 4 | 58.44 | 60.75 | … | … | … | … | 11 | 13 | 101.6 | 1484 | 1543 | … | … | … | … | 273 | 330
AWWA C207 | B | 4 | 9 | 7.5 |  | 8 | 0.625 |  |  |  | 0.625 |  | N/A |  |  |  | N/A |  | 4.57 | [33 empty] | N/A | [28 empty] | 0.625 | 86 | 129
AWWA C207 | B | 5 | 10 | 8.5 |  | 8 | 0.75 |  |  |  | 0.625 |  | N/A |  |  |  | N/A |  | 5.66 | [33 empty] | N/A | [28 empty] | 0.625 | 86 | 129
AWWA C207 | B | 6 | 11 | 9.5 |  | 8 | 0.75 |  |  |  | 0.688 |  | N/A |  |  |  | N/A |  | 6.72 | [33 empty] | N/A | [28 empty] | 0.688 | 86 | 129
AWWA C207 | B | 8 | 13.5 | 11.75 |  | 8 | 0.75 |  |  |  | 0.688 |  | N/A |  |  |  | N/A |  | 8.72 | [33 empty] | N/A | [28 empty] | 0.688 | 86 | 129
AWWA C207 | B | 10 | 16 | 14.25 |  | 12 | 0.875 |  |  |  | 0.688 |  | N/A |  |  |  | N/A |  | 10.88 | [33 empty] | N/A | [28 empty] | 0.688 | 86 | 129
AWWA C207 | B | 12 | 19 | 17 |  | 12 | 0.875 |  |  |  | 0.719 |  | N/A |  |  |  | N/A |  | 12.88 | [33 empty] | N/A | [28 empty] | 0.688 | 86 | 129
AWWA C207 | B | 14 | 21 | 18.75 |  | 12 | 1 |  |  |  | 0.791 |  | N/A |  |  |  | N/A |  | 14.19 | [33 empty] | N/A | [28 empty] | 0.688 | 86 | 129
AWWA C207 | B | 16 | 23.5 | 21.25 |  | 16 | 1 |  |  |  | 0.892 |  | N/A |  |  |  | N/A |  | 16.19 | [33 empty] | N/A | [28 empty] | 0.688 | 86 | 129
AWWA C207 | B | 18 | 25 | 22.75 |  | 16 | 1.125 |  |  |  | 0.95 |  | N/A |  |  |  | N/A |  | 18.19 | [33 empty] | N/A | [28 empty] | 0.688 | 86 | 129
AWWA C207 | B | 20 | 27.5 | 25 |  | 20 | 1.125 |  |  |  | 1.04 |  | N/A |  |  |  | N/A |  | 20.19 | [33 empty] | N/A | [28 empty] | 0.688 | 86 | 129
AWWA C207 | B | 22 | 29.5 | 27.25 |  | 20 | 1.25 |  |  |  | 1.132 |  | N/A |  |  |  | N/A |  | 22.19 | [33 empty] | N/A | [28 empty] | 0.75 | 86 | 129
AWWA C207 | B | 24 | 32 | 29.5 |  | 20 | 1.25 |  |  |  | 1.216 |  | N/A |  |  |  | N/A |  | 24.19 | [33 empty] | N/A | [28 empty] | 0.75 | 86 | 129
AWWA C207 | B | 26 | 34.25 | 31.75 |  | 24 | 1.25 |  |  |  | 1.307 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 0.812 | 86 | 129
AWWA C207 | B | 28 | 36.5 | 34 |  | 28 | 1.25 |  |  |  | 1.398 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 0.875 | 86 | 129
AWWA C207 | B | 30 | 38.75 | 36 |  | 28 | 1.25 |  |  |  | 1.477 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 0.875 | 86 | 129
AWWA C207 | B | 32 | 41.75 | 38.5 |  | 28 | 1.5 |  |  |  | 1.581 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 0.938 | 86 | 129
AWWA C207 | B | 34 | 43.75 | 40.5 |  | 32 | 1.5 |  |  |  | 1.661 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 0.938 | 86 | 129
AWWA C207 | B | 36 | 46 | 42.75 |  | 32 | 1.5 |  |  |  | 1.751 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 1 | 86 | 129
AWWA C207 | B | 38 | 48.75 | 45.25 |  | 32 | 1.5 |  |  |  | 1.853 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 1 | 86 | 129
AWWA C207 | B | 40 | 50.75 | 47.25 |  | 36 | 1.5 |  |  |  | 1.933 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 1 | 86 | 129
AWWA C207 | B | 42 | 53 | 49.5 |  | 36 | 1.5 |  |  |  | 2.023 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 1.125 | 86 | 129
AWWA C207 | B | 44 | 55.25 | 51.75 |  | 40 | 1.5 |  |  |  | 2.114 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 1.125 | 86 | 129
AWWA C207 | B | 46 | 57.25 | 53.75 |  | 40 | 1.5 |  |  |  | 2.194 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 1.125 | 86 | 129
AWWA C207 | B | 48 | 59.5 | 56 |  | 44 | 1.5 |  |  |  | 2.285 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 1.25 | 86 | 129
AWWA C207 | B | 50 | 61.75 | 58.25 |  | 44 | 1.75 |  |  |  | 2.377 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 1.25 | 86 | 129
AWWA C207 | B | 52 | 64 | 60.5 |  | 44 | 1.75 |  |  |  | 2.468 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 1.25 | 86 | 129
AWWA C207 | B | 54 | 66.25 | 62.75 |  | 44 | 1.75 |  |  |  | 2.559 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 1.375 | 86 | 129
AWWA C207 | B | 60 | 73 | 69.25 |  | 52 | 1.75 |  |  |  | 2.82 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 1.5 | 86 | 129
AWWA C207 | B | 66 | 80 | 76 |  | 52 | 1.75 |  |  |  | 3.092 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 1.625 | 86 | 129
AWWA C207 | B | 72 | 86.5 | 82.5 |  | 60 | 1.75 |  |  |  | 3.353 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 1.75 | 86 | 129
AWWA C207 | B | 78 | 93 | 89 |  | 64 | 2 |  |  |  | - |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 2 | 86 | 129
AWWA C207 | B | 84 | 99.75 | 95.5 |  | 64 | 2 |  |  |  | - |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 2 | 86 | 129
AWWA C207 | B | 90 | 106.5 | 102 |  | 68 | 2.25 |  |  |  | - |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 2.25 | 86 | 129
AWWA C207 | B | 96 | 113.25 | 108.5 |  | 68 | 2.25 |  |  |  | - |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 2.25 | 86 | 129
AWWA C207 | B | 102 | 120 | 114.5 |  | 72 | 2.5 |  |  |  | - |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 2.5 | 86 | 129
AWWA C207 | B | 108 | 126.75 | 120.75 |  | 72 | 2.5 |  |  |  | - |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 2.5 | 86 | 129
AWWA C207 | B | 114 | 133.5 | 126.75 |  | 76 | 2.75 |  |  |  | - |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 2.75 | 86 | 129
AWWA C207 | B | 120 | 140.25 | 132.75 |  | 76 | 2.75 |  |  |  | - |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 2.75 | 86 | 129
AWWA C207 | B | 126 | 147 | 139.25 |  | 80 | 3 |  |  |  | - |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 3 | 86 | 129
AWWA C207 | B | 132 | 153.75 | 145.75 |  | 80 | 3 |  |  |  | - |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 3 | 86 | 129
AWWA C207 | B | 144 | 167.25 | 158.25 |  | 84 | 3.25 |  |  |  | - |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 3.25 | 86 | 129
AWWA C207 | D | 4 | 9 | 7.5 |  | 8 | 0.625 |  |  |  | 0.625 |  | 5.312 |  |  |  | 0.875 |  | 4.57 | [33 empty] | 0.5 | [28 empty] | 0.625 | 175-150 | 262.5
AWWA C207 | D | 5 | 10 | 8.5 |  | 8 | 0.75 |  |  |  | 0.65 |  | 6.312 |  |  |  | 1.25 |  | 5.66 | [33 empty] | 0.562 | [28 empty] | 0.625 | 175-150 | 262.5
AWWA C207 | D | 6 | 11 | 9.5 |  | 8 | 0.75 |  |  |  | 0.693 |  | 7.562 |  |  |  | 1.25 |  | 6.72 | [33 empty] | 0.562 | [28 empty] | 0.688 | 175-150 | 262.5
AWWA C207 | D | 8 | 13.5 | 11.75 |  | 8 | 0.75 |  |  |  | 0.812 |  | 9.688 |  |  |  | 1.25 |  | 8.72 | [33 empty] | 0.562 | [28 empty] | 0.688 | 175-150 | 262.5
AWWA C207 | D | 10 | 16 | 14.25 |  | 12 | 0.875 |  |  |  | 0.953 |  | 12 |  |  |  | 1.25 |  | 10.88 | [33 empty] | 0.688 | [28 empty] | 0.688 | 175-150 | 262.5
AWWA C207 | D | 12 | 19 | 17 |  | 12 | 0.875 |  |  |  | 1.117 |  | 14.375 |  |  |  | 1.25 |  | 12.88 | [33 empty] | 0.688 | [28 empty] | 0.812 | 175-150 | 262.5
AWWA C207 | D | 14 | 21 | 18.75 |  | 12 | 1 |  |  |  | 1.133 |  | 15.75 |  |  |  | 1.25 |  | 14.19 | [33 empty] | 0.75 | [28 empty] | 0.938 | 175-150 | 225
AWWA C207 | D | 16 | 23.5 | 21.25 |  | 16 | 1 |  |  |  | 1.265 |  | 18 |  |  |  | 1.25 |  | 16.19 | [33 empty] | 0.75 | [28 empty] | 1 | 175-150 | 225
AWWA C207 | D | 18 | 25 | 22.75 |  | 16 | 1.125 |  |  |  | 1.331 |  | 19.875 |  |  |  | 1.25 |  | 18.19 | [33 empty] | 0.75 | [28 empty] | 1.062 | 175-150 | 225
AWWA C207 | D | 20 | 27.5 | 25 |  | 20 | 1.125 |  |  |  | 1.448 |  | 22 |  |  |  | 1.25 |  | 20.19 | [33 empty] | 0.75 | [28 empty] | 1.125 | 175-150 | 225
AWWA C207 | D | 22 | 29.5 | 27.25 |  | 20 | 1.25 |  |  |  | 1.568 |  | 24.25 |  |  |  | 1.75 |  | 22.19 | [33 empty] | 1 | [28 empty] | 1.188 | 175-150 | 225
AWWA C207 | D | 24 | 32 | 29.5 |  | 20 | 1.25 |  |  |  | 1.661 |  | 26.125 |  |  |  | 1.75 |  | 24.19 | [33 empty] | 1 | [28 empty] | 1.25 | 175-150 | 225
AWWA C207 | D | 26 | 34.25 | 31.75 |  | 24 | 1.25 |  |  |  | 1.786 |  | 28.5 |  |  |  | 1.75 |  | - | [33 empty] | 1 | [28 empty] | 1.312 | 175-150 | 225
AWWA C207 | D | 28 | 36.5 | 34 |  | 28 | 1.25 |  |  |  | 1.906 |  | 30.5 |  |  |  | 1.75 |  | - | [33 empty] | 1 | [28 empty] | 1.312 | 175-150 | 225
AWWA C207 | D | 30 | 38.75 | 36 |  | 28 | 1.25 |  |  |  | 2.008 |  | 32.5 |  |  |  | 1.75 |  | - | [33 empty] | 1 | [28 empty] | 1.375 | 175-150 | 225
AWWA C207 | D | 32 | 41.75 | 38.5 |  | 28 | 1.5 |  |  |  | 2.15 |  | 34.75 |  |  |  | 1.75 |  | - | [33 empty] | 1.125 | [28 empty] | 1.5 | 175-150 | 225
AWWA C207 | D | 34 | 43.75 | 40.5 |  | 32 | 1.5 |  |  |  | 2.252 |  | 36.75 |  |  |  | 1.75 |  | - | [33 empty] | 1.125 | [28 empty] | 1.5 | 175-150 | 225
AWWA C207 | D | 36 | 46 | 42.75 |  | 32 | 1.5 |  |  |  | 2.37 |  | 38.75 |  |  |  | 1.75 |  | - | [33 empty] | 1.125 | [28 empty] | 1.625 | 175-150 | 225
AWWA C207 | D | 38 | 48.75 | 45.25 |  | 32 | 1.5 |  |  |  | 2.506 |  | 40.75 |  |  |  | 1.75 |  | - | [33 empty] | 1.125 | [28 empty] | 1.625 | 175-150 | 225
AWWA C207 | D | 40 | 50.75 | 47.25 |  | 36 | 1.5 |  |  |  | 2.609 |  | 43 |  |  |  | 1.75 |  | - | [33 empty] | 1.125 | [28 empty] | 1.625 | 175-150 | 225
AWWA C207 | D | 42 | 53 | 49.5 |  | 36 | 1.5 |  |  |  | 2.729 |  | 45 |  |  |  | 1.75 |  | - | [33 empty] | 1.25 | [28 empty] | 1.75 | 175-150 | 225
AWWA C207 | D | 44 | 55.25 | 51.75 |  | 40 | 1.5 |  |  |  | 2.849 |  | 47 |  |  |  | 2.25 |  | - | [33 empty] | 1.25 | [28 empty] | 1.75 | 175-150 | 225
AWWA C207 | D | 46 | 57.25 | 53.75 |  | 40 | 1.5 |  |  |  | 2.952 |  | 49 |  |  |  | 2.25 |  | - | [33 empty] | 1.25 | [28 empty] | 1.75 | 175-150 | 225
AWWA C207 | D | 48 | 59.5 | 56 |  | 44 | 1.5 |  |  |  | 3.072 |  | 51 |  |  |  | 2.5 |  | - | [33 empty] | 1.375 | [28 empty] | 1.875 | 175-150 | 225
AWWA C207 | D | 50 | 61.75 | 58.25 |  | 44 | 1.75 |  |  |  | 3.196 |  | 53 |  |  |  | 2.5 |  | - | [33 empty] | 1.375 | [28 empty] | 2 | 175-150 | 225
AWWA C207 | D | 52 | 64 | 60.5 |  | 44 | 1.75 |  |  |  | 3.315 |  | 55 |  |  |  | 2.5 |  | - | [33 empty] | 1.375 | [28 empty] | 2 | 175-150 | 225
AWWA C207 | D | 54 | 66.25 | 62.75 |  | 44 | 1.75 |  |  |  | 3.435 |  | 57 |  |  |  | 2.5 |  | - | [33 empty] | 1.375 | [28 empty] | 2.125 | 175-150 | 225
AWWA C207 | D | 60 | 73 | 69.25 |  | 52 | 1.75 |  |  |  | 3.779 |  | 63 |  |  |  | 2.75 |  | - | [33 empty] | 1.5 | [28 empty] | 2.25 | 175-150 | 225
AWWA C207 | D | 66 | 80 | 76 |  | 52 | 1.75 |  |  |  | 4.136 |  | 69 |  |  |  | 2.75 |  | - | [33 empty] | 1.5 | [28 empty] | 2.5 | 175-150 | 225
AWWA C207 | D | 72 | 86.5 | 82.5 |  | 60 | 1.75 |  |  |  | 4.48 |  | 75 |  |  |  | 2.75 |  | - | [33 empty] | 1.5 | [28 empty] | 2.625 | 175-150 | 225
AWWA C207 | D | 78 | 93 | 89 |  | 64 | 2 |  |  |  | - |  | 81.25 |  |  |  | 3 |  | - | [33 empty] | 1.75 | [28 empty] | 2.75 | 175-150 | 225
AWWA C207 | D | 84 | 99.75 | 95.5 |  | 64 | 2 |  |  |  | - |  | 87.5 |  |  |  | 3 |  | - | [33 empty] | 1.75 | [28 empty] | 2.875 | 175-150 | 225
AWWA C207 | D | 90 | 106.5 | 102 |  | 68 | 2.25 |  |  |  | - |  | 93.75 |  |  |  | 3.25 |  | - | [33 empty] | 2 | [28 empty] | 3 | 175-150 | 225
AWWA C207 | D | 96 | 113.25 | 108.5 |  | 68 | 2.25 |  |  |  | - |  | 100 |  |  |  | 3.25 |  | - | [33 empty] | 2 | [28 empty] | 3.25 | 175-150 | 225
AWWA C207 | D | 102 | 120 | 114.5 |  | 72 | 2.5 |  |  |  | - |  | - |  |  |  | - |  | - | [33 empty] | - | [28 empty] | 3.25 | 175-150 | 225
AWWA C207 | D | 108 | 126.75 | 120.75 |  | 72 | 2.5 |  |  |  | - |  | - |  |  |  | - |  | - | [33 empty] | - | [28 empty] | 3.375 | 175-150 | 225
AWWA C207 | D | 114 | 133.5 | 126.75 |  | 76 | 2.75 |  |  |  | - |  | - |  |  |  | - |  | - | [33 empty] | - | [28 empty] | 3.5 | 175-150 | 225
AWWA C207 | D | 120 | 140.25 | 132.75 |  | 76 | 2.75 |  |  |  | - |  | - |  |  |  | - |  | - | [33 empty] | - | [28 empty] | 3.5 | 175-150 | 225
AWWA C207 | D | 126 | 147 | 139.25 |  | 80 | 3 |  |  |  | - |  | - |  |  |  | - |  | - | [33 empty] | - | [28 empty] | 3.75 | 175-150 | 225
AWWA C207 | D | 132 | 153.75 | 145.75 |  | 80 | 3 |  |  |  | - |  | - |  |  |  | - |  | - | [33 empty] | - | [28 empty] | 3.875 | 175-150 | 225
AWWA C207 | D | 144 | 167.25 | 158.25 |  | 84 | 3.25 |  |  |  | - |  | - |  |  |  | - |  | - | [33 empty] | - | [28 empty] | 4.125 | 175-150 | 225
AWWA C207 | E | 4 | 9 | 7.5 |  | 8 | 0.625 |  |  |  | 1.125 |  | 5.312 |  |  |  | 1.312 |  | 4.57 | [33 empty] | 0.938 | [28 empty] | 1.125 | 275 | 412.5
AWWA C207 | E | 5 | 10 | 8.5 |  | 8 | 0.75 |  |  |  | 1.188 |  | 6.438 |  |  |  | 1.438 |  | 5.66 | [33 empty] | 0.938 | [28 empty] | 1.188 | 275 | 412.5
AWWA C207 | E | 6 | 11 | 9.5 |  | 8 | 0.75 |  |  |  | 1.313 |  | 7.562 |  |  |  | 1.562 |  | 6.72 | [33 empty] | 1 | [28 empty] | 1.313 | 275 | 412.5
AWWA C207 | E | 8 | 13.5 | 11.75 |  | 8 | 0.75 |  |  |  | 1.5 |  | 9.688 |  |  |  | 1.75 |  | 8.72 | [33 empty] | 1.125 | [28 empty] | 1.5 | 275 | 412.5
AWWA C207 | E | 10 | 16 | 14.25 |  | 12 | 0.875 |  |  |  | 1.563 |  | 12 |  |  |  | 1.938 |  | 10.88 | [33 empty] | 1.188 | [28 empty] | 1.563 | 275 | 412.5
AWWA C207 | E | 12 | 19 | 17 |  | 12 | 0.875 |  |  |  | 1.75 |  | 14.375 |  |  |  | 2.188 |  | 12.88 | [33 empty] | 1.25 | [28 empty] | 1.75 | 275 | 412.5
AWWA C207 | E | 14 | 21 | 18.75 |  | 12 | 1 |  |  |  | 1.875 |  | 15.75 |  |  |  | 2.25 |  | 14.19 | [33 empty] | 1.375 | [28 empty] | 1.875 | 275 | 412.5
AWWA C207 | E | 16 | 23.5 | 21.25 |  | 16 | 1 |  |  |  | 2 |  | 18 |  |  |  | 2.5 |  | 16.19 | [33 empty] | 1.438 | [28 empty] | 2 | 275 | 412.5
AWWA C207 | E | 18 | 25 | 22.75 |  | 16 | 1.125 |  |  |  | 2.125 |  | 19.875 |  |  |  | 2.688 |  | 18.19 | [33 empty] | 1.562 | [28 empty] | 2.125 | 275 | 412.5
AWWA C207 | E | 20 | 27.5 | 25 |  | 20 | 1.125 |  |  |  | 2.375 |  | 22 |  |  |  | 2.875 |  | 20.19 | [33 empty] | 1.688 | [28 empty] | 2.375 | 275 | 412.5
AWWA C207 | E | 22 | 29.5 | 27.25 |  | 20 | 1.25 |  |  |  | 2.5 |  | 24 |  |  |  | 3.125 |  | 22.19 | [33 empty] | 1.812 | [28 empty] | 2.5 | 275 | 412.5
AWWA C207 | E | 24 | 32 | 29.5 |  | 20 | 1.25 |  |  |  | 2.625 |  | 26.125 |  |  |  | 3.25 |  | 24.19 | [33 empty] | 1.875 | [28 empty] | 2.625 | 275 | 412.5
AWWA C207 | E | 26 | 34.25 | 31.75 |  | 24 | 1.25 |  |  |  | 2.75 |  | 28.5 |  |  |  | 3.375 |  | - | [33 empty] | 2 | [28 empty] | 2.75 | 275 | 412.5
AWWA C207 | E | 28 | 36.5 | 34 |  | 28 | 1.25 |  |  |  | 2.75 |  | 30.75 |  |  |  | 3.438 |  | - | [33 empty] | 2.062 | [28 empty] | 2.75 | 275 | 412.5
AWWA C207 | E | 30 | 38.75 | 36 |  | 28 | 1.25 |  |  |  | 2.875 |  | 32.75 |  |  |  | 3.5 |  | - | [33 empty] | 2.125 | [28 empty] | 2.875 | 275 | 412.5
AWWA C207 | E | 32 | 41.75 | 38.5 |  | 28 | 1.5 |  |  |  | 3 |  | 35 |  |  |  | 3.625 |  | - | [33 empty] | 2.25 | [28 empty] | 3 | 275 | 412.5
AWWA C207 | E | 34 | 43.75 | 40.5 |  | 32 | 1.5 |  |  |  | 3.05 |  | 37 |  |  |  | 3.688 |  | - | [33 empty] | 2.312 | [28 empty] | 3 | 275 | 412.5
AWWA C207 | E | 36 | 46 | 42.75 |  | 32 | 1.5 |  |  |  | 3.209 |  | 39.25 |  |  |  | 3.75 |  | - | [33 empty] | 2.375 | [28 empty] | 3.125 | 275 | 412.5
AWWA C207 | E | 38 | 48.75 | 45.25 |  | 32 | 1.5 |  |  |  | 3.394 |  | 41.75 |  |  |  | 3.75 |  | - | [33 empty] | 2.375 | [28 empty] | 3.125 | 275 | 412.5
AWWA C207 | E | 40 | 50.75 | 47.25 |  | 36 | 1.5 |  |  |  | 3.533 |  | 43.75 |  |  |  | 3.875 |  | - | [33 empty] | 2.5 | [28 empty] | 3.25 | 275 | 412.5
AWWA C207 | E | 42 | 53 | 49.5 |  | 36 | 1.5 |  |  |  | 3.695 |  | 46 |  |  |  | 4 |  | - | [33 empty] | 2.625 | [28 empty] | 3.375 | 275 | 412.5
AWWA C207 | E | 44 | 55.25 | 51.75 |  | 40 | 1.5 |  |  |  | 3.857 |  | 48 |  |  |  | 4 |  | - | [33 empty] | 2.625 | [28 empty] | 3.375 | 275 | 412.5
AWWA C207 | E | 46 | 57.25 | 53.75 |  | 40 | 1.5 |  |  |  | 3.997 |  | 50 |  |  |  | 4.062 |  | - | [33 empty] | 2.688 | [28 empty] | 3.438 | 275 | 412.5
AWWA C207 | E | 48 | 59.5 | 56 |  | 44 | 1.5 |  |  |  | 4.159 |  | 52.25 |  |  |  | 4.125 |  | - | [33 empty] | 2.75 | [28 empty] | 3.5 | 275 | 412.5
AWWA C207 | E | 50 | 61.75 | 58.25 |  | 44 | 1.75 |  |  |  | 4.327 |  | 54.25 |  |  |  | 4.125 |  | - | [33 empty] | 2.75 | [28 empty] | 3.5 | 275 | 412.5
AWWA C207 | E | 52 | 64 | 60.5 |  | 44 | 1.75 |  |  |  | 4.489 |  | 56.5 |  |  |  | 4.25 |  | - | [33 empty] | 2.875 | [28 empty] | 3.625 | 275 | 412.5
AWWA C207 | E | 54 | 66.25 | 62.75 |  | 44 | 1.75 |  |  |  | 4.651 |  | 58.75 |  |  |  | 4.375 |  | - | [33 empty] | 3 | [28 empty] | 3.75 | 275 | 412.5
AWWA C207 | E | 60 | 73 | 69.75 |  | 52 | 1.75 |  |  |  | 5.116 |  | 65.25 |  |  |  | 4.5 |  | - | [33 empty] | 3.125 | [28 empty] | 3.875 | 275 | 412.5
AWWA C207 | E | 66 | 80 | 76 |  | 52 | 1.75 |  |  |  | 5.601 |  | 71.5 |  |  |  | 4.875 |  | - | [33 empty] | 3.375 | [28 empty] | 4.25 | 275 | 412.5
AWWA C207 | E | 72 | 86.5 | 82.5 |  | 60 | 1.75 |  |  |  | 6.066 |  | 78.5 |  |  |  | 5 |  | - | [33 empty] | 3.5 | [28 empty] | 4.375 | 275 | 412.5
AWWA C207 | E | 78 | 93 | 89 |  | 64 | 2 |  |  |  | - |  | 84.5 |  |  |  | 5.375 |  | - | [33 empty] | 3.875 | [28 empty] | 4.75 | 275 | 412.5
AWWA C207 | E | 84 | 99.75 | 95.5 |  | 64 | 2 |  |  |  | - |  | 90.5 |  |  |  | 5.375 |  | - | [33 empty] | 3.875 | [28 empty] | 4.75 | 275 | 412.5
AWWA C207 | E | 90 | 106.5 | 102 |  | 68 | 2.25 |  |  |  | - |  | 96.75 |  |  |  | 5.75 |  | - | [33 empty] | 4.25 | [28 empty] | 5.125 | 275 | 412.5
AWWA C207 | E | 96 | 113.25 | 108.5 |  | 68 | 2.25 |  |  |  | - |  | 102.75 |  |  |  | 5.75 |  | - | [33 empty] | 4.25 | [28 empty] | 5.125 | 275 | 412.5
AWWA C207 | E | 102 | 120 | 114.5 |  | 72 | 2.5 |  |  |  | - |  | - |  |  |  | - |  | - | [33 empty] | - | [28 empty] | 5.5 | 275 | 412.5
AWWA C207 | E | 108 | 126.75 | 120.75 |  | 72 | 2.5 |  |  |  | - |  | - |  |  |  | - |  | - | [33 empty] | - | [28 empty] | 5.5 | 275 | 412.5
AWWA C207 | E | 114 | 133.5 | 126.75 |  | 76 | 2.75 |  |  |  | - |  | - |  |  |  | - |  | - | [33 empty] | - | [28 empty] | 5.875 | 275 | 412.5
AWWA C207 | E | 120 | 140.25 | 132.75 |  | 76 | 2.75 |  |  |  | - |  | - |  |  |  | - |  | - | [33 empty] | - | [28 empty] | 5.875 | 275 | 412.5
AWWA C207 | E | 126 | 147 | 139.25 |  | 80 | 3 |  |  |  | - |  | - |  |  |  | - |  | - | [33 empty] | - | [28 empty] | 6.25 | 275 | 412.5
AWWA C207 | E | 132 | 153.75 | 145.75 |  | 80 | 3 |  |  |  | - |  | - |  |  |  | - |  | - | [33 empty] | - | [28 empty] | 6.25 | 275 | 412.5
AWWA C207 | E | 144 | 167.25 | 158.25 |  | 84 | 3.25 |  |  |  | - |  | - |  |  |  | - |  | - | [33 empty] | - | [28 empty] | 6.75 | 275 | 412.5
AWWA C207 | F | 4 | 10 | 7.88 |  | 8 | 0.75 |  |  |  | 1.13 |  | N/A |  |  |  | N/A |  | 4.57 | [33 empty] | N/A | [28 empty] | 1.13 | 300 | 450
AWWA C207 | F | 5 | 11 | 9.25 |  | 8 | 0.75 |  |  |  | 1.21 |  | N/A |  |  |  | N/A |  | 5.66 | [33 empty] | N/A | [28 empty] | 1.21 | 300 | 450
AWWA C207 | F | 6 | 12.5 | 10.62 |  | 12 | 0.75 |  |  |  | 1.31 |  | N/A |  |  |  | N/A |  | 6.73 | [33 empty] | N/A | [28 empty] | 1.31 | 300 | 450
AWWA C207 | F | 8 | 15 | 13 |  | 12 | 0.875 |  |  |  | 1.31 |  | N/A |  |  |  | N/A |  | 8.73 | [33 empty] | N/A | [28 empty] | 1.31 | 300 | 450
AWWA C207 | F | 10 | 17.5 | 15.25 |  | 16 | 1 |  |  |  | 1.5 |  | N/A |  |  |  | N/A |  | 10.88 | [33 empty] | N/A | [28 empty] | 1.5 | 300 | 450
AWWA C207 | F | 12 | 20.5 | 17.75 |  | 16 | 1.125 |  |  |  | 1.63 |  | N/A |  |  |  | N/A |  | 12.88 | [33 empty] | N/A | [28 empty] | 1.63 | 300 | 450
AWWA C207 | F | 14 | 23 | 20.25 |  | 20 | 1.125 |  |  |  | 1.94 |  | N/A |  |  |  | N/A |  | 14.19 | [33 empty] | N/A | [28 empty] | 1.94 | 300 | 450
AWWA C207 | F | 16 | 25.5 | 22.5 |  | 20 | 1.25 |  |  |  | 2.14 |  | N/A |  |  |  | N/A |  | 16.19 | [33 empty] | N/A | [28 empty] | 2.14 | 300 | 450
AWWA C207 | F | 18 | 28 | 24.75 |  | 24 | 1.25 |  |  |  | 2.25 |  | N/A |  |  |  | N/A |  | 18.19 | [33 empty] | N/A | [28 empty] | 2.25 | 300 | 450
AWWA C207 | F | 20 | 30.5 | 27 |  | 24 | 1.25 |  |  |  | 2.33 |  | N/A |  |  |  | N/A |  | 20.19 | [33 empty] | N/A | [28 empty] | 2.33 | 300 | 450
AWWA C207 | F | 22 | 33 | 29.25 |  | 24 | 1.255 |  |  |  | 2.5 |  | N/A |  |  |  | N/A |  | 22.19 | [33 empty] | N/A | [28 empty] | 2.5 | 300 | 450
AWWA C207 | F | 24 | 36 | 32 |  | 24 | 1.5 |  |  |  | 2.69 |  | N/A |  |  |  | N/A |  | 24.19 | [33 empty] | N/A | [28 empty] | 2.69 | 300 | 450
AWWA C207 | F | 26 | 38.25 | 34.5 |  | 28 | 1.75 |  |  |  | 3 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 3 | 300 | 450
AWWA C207 | F | 28 | 40.75 | 37 |  | 28 | 1.75 |  |  |  | 3.13 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 3.13 | 300 | 450
AWWA C207 | F | 30 | 43 | 39.25 |  | 28 | 1.75 |  |  |  | 3.166 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 3.15 | 300 | 450
AWWA C207 | F | 32 | 45.25 | 41.5 |  | 28 | 1.75 |  |  |  | 3.332 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 3.25 | 300 | 450
AWWA C207 | F | 34 | 47.5 | 43.5 |  | 28 | 1.75 |  |  |  | 3.475 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 3.38 | 300 | 450
AWWA C207 | F | 36 | 50 | 46 |  | 32 | 2 |  |  |  | 3.671 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 3.46 | 300 | 450
AWWA C207 | F | 38 | 52.25 | 48 |  | 32 | 2 |  |  |  | 3.815 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 3.5 | 300 | 450
AWWA C207 | F | 40 | 54.25 | 50.25 |  | 36 | 2 |  |  |  | 3.982 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 3.63 | 300 | 450
AWWA C207 | F | 42 | 57 | 52.75 |  | 36 | 2 |  |  |  | 4.171 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 3.81 | 300 | 450
AWWA C207 | F | 44 | 59.25 | 55 |  | 36 | 2 |  |  |  | 4.338 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 4 | 300 | 450
AWWA C207 | F | 46 | 61.5 | 57.25 |  | 40 | 2 |  |  |  | 4.505 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 4.13 | 300 | 450
AWWA C207 | F | 48 | 65 | 60.75 |  | 40 | 2 |  |  |  | 4.781 |  | N/A |  |  |  | N/A |  | - | [33 empty] | N/A | [28 empty] | 4.5 | 300 | 450

## For reference only (2)
AWWA C207 | Hub Flange | TRUE | TRUE | TRUE |  | TRUE | TRUE |  |  | TRUE |  | TRUE |  |  |  | TRUE |  | TRUE |  |  |  |  | TRUE | [25 empty] | TRUE
ASME 16.1 | Raised Face | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  |  | TRUE | [10 empty] | TRUE | [5 empty] | TRUE | [30 empty] | TRUE | TRUE | TRUE | TRUE |  |  |  |  | TRUE | TRUE |  | TRUE | TRUE
ASME 16.47 Series A&B (300,150,75) | Raised Face | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  | TRUE | [10 empty] | TRUE | TRUE | TRUE |  |  |  | TRUE | [17 empty] | TRUE |  | TRUE |  | TRUE | TRUE |  | TRUE | TRUE | TRUE |  | TRUE | TRUE
ASME 16.47 Series A&B (400,600,900) | Raised Face | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  |  |  | TRUE | [10 empty] | TRUE | TRUE |  |  |  |  | TRUE | [16 empty] | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | TRUE
ASME 16.5 Class 150 |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE |  | TRUE |  |  | TRUE | TRUE |  | TRUE |  | TRUE | TRUE | TRUE | [17 empty] | TRUE |  | TRUE
ASME 16.5 Class 300 |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE |  | TRUE |  |  | TRUE | TRUE |  | TRUE |  | TRUE | TRUE | TRUE |  |  | TRUE |  | TRUE |  | TRUE |  |  | TRUE | [5 empty] | TRUE | TRUE | TRUE |  | TRUE
ASME 16.5 Class 400 |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE |  | TRUE |  |  | TRUE | TRUE |  | Note |  | N/A | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE | [5 empty] | TRUE |  | TRUE |  | TRUE
ASME 16.5 Class 600 |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE |  | TRUE |  |  | TRUE | TRUE |  | Note |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE |  | TRUE |  |  |  | TRUE
ASME 16.5 Class 900 |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE |  | TRUE |  |  | TRUE | TRUE |  | Note |  | N/A | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE |  | TRUE |  |  | TRUE | [5 empty] | TRUE | TRUE
ASME 16.5 Class 1500 |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE |  | TRUE |  |  | TRUE | TRUE |  | Note |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE |  | TRUE |  |  | TRUE | [5 empty] | TRUE | TRUE
ASME 16.5 Class 2500 |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  |  | TRUE | TRUE | TRUE |  | TRUE |  |  | TRUE |  |  | Note |  | N/A | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE |  | TRUE |  |  | TRUE | [5 empty] | TRUE | TRUE
TYPE | Flange Class | Nominal Pipe Size (NPS) | Outside Diameter Flange (O) | Drilling-Diameter Bolt Circle (W) | Drilling-Diameter Bolt Holes | Drilling-Number of Bolts | Drilling-Bolt Diameter | Stud Bolts (L)-Raised Face (0.06 in) | Machine Bolts (L)-Raised Face (0.06in) | Min Thickness Flange (tf) | Min Thickness Lap Joint (tf) | Diameter of Hub (X) | Diameter Beginning Chamfer Welding Neck (Ah) in | Length Through Hub-Threaded Slip on/Socket Welding (Y) in | Length Through Hub- Lapped (Y) in | Length Through Hub Bore Welding Neck (Y) in | Min Thread Length Threaded (T) in | Bore- Min Slip On Socket Weld (B) in | Bore- Min Lapped (B) in | Bore- Weld Neck/Socket Weld (B) in | Corner Bore Radius of Lapped Flange and Pipe (r) in | Depth of socket (D) in | Outside Diameter Flange (O) mm | Diameter Bolt Circle (W) mm | Stud Bolts (L)- 1.5 mm Raised Face | Machine Bolts (L)- 1.5mm Raised Face | Min Thickness Flange (tf) mm | Min Thickness Lap Joint (tf) mm | Diameter of Hub (X) mm | Diameter Beginning Chamfer Welding Neck (Ah) mm | Length through Hub-Threaded/Slip-on/Socket Weld (Y) mm | Length Through Hub- Lapped (Y) mm | Length Through Bore- Welding Neck (Y) mm | Min Thread Length Threaded (T) mm | Bore- Min Slip On Socket Weld (B) mm | Bore- Min Lapped (B) mm | Bore- Weld Neck/Socket Weld (B) mm | Corner Bore Radius of Lapped Flange and Pipe (r) mm | Depth of socket (D) mm | Min Counterbore Threaded Flange (in) | Min Counterbore Threaded Flange (mm) | Length Bolts-Raised Face (0.25 in) (L) | Length Bolts-Male and Female (L) | Length Bolts-6.4 mm Raised Face (L) | Length Bolts-Male and Female (L) | Length of Bolts (L)- Stud Bolt Raised Face (.25 in) | Hub Diameter Top (A) in. | Raised Face Diameter (R) in. | Min Thickness Flange- WNF (tf) in. | Min Thickness Flange- Blind (tf) in. | Length Through Hub (Y) in. | Min Fillet Radius (r1) in. | Length of Bolts- Stud Bolt Raised Face (6.44mm) | Hub Diameter Top (A) mm | Raised Face Diameter (R) mm | Min Thickness Flange (tf)- WNF mm | Min Thickness Flange (tf)-Blind mm | Length Through Hub (Y) mm | Min Fillet Radius (r1) mm | Min Thickness Flange (Q) in. | Raised Face Diameter (W) in. | Hub- Min Length (Y) in. | Hub- Min Thread Length (T) in. | Blind Flange- Diameter of Port (I) in. | Blind Flange- Wall Thickness (V) in. | Bolting- Length of Bolts in. | Bolting- Length of Stud Bolts in. | Min Thickness Flange (Q) mm | Raised Face Diameter (W) mm | Bolt Hole- Diameter Bolt Circle mm | Hub- Min Length (Y) mm | Hub- Min Thread Length (T) mm | Blind Flange- Diameter of Port (I) mm | Blind Flange- Wall Thickness (V) mm | Bolting- Length of Bolts mm | Bolting- Length of Stud Bolts mm | Flange Thickness in. | Psi | Max Pressure (psi)
ASME 16.5 | 150 | 0.5 | 3.5 | 2.38 | 0.625 | 4 | 0.5 | 2.25 | 2 | 0.38 | 0.44 | 1.19 | 0.84 | 0.56 | 0.62 | 1.81 | 0.62 | 0.88 | 0.9 | 0.62 | 0.12 | 0.38 | 89 | 60.5 | 55 | 50 | 9.7 | 11.2 | 30 | 21.3 | 14 | 16 | 46 | 16 | 22.4 | 22.9 | 1.7 | 3 | 10 | N/A | N/A
ASME 16.5 | 150 | 0.75 | 3.88 | 2.75 | 0.625 | 4 | 0.5 | 2.5 | 2 | 0.44 | 0.5 | 1.5 | 1.05 | 0.56 | 0.62 | 2 | 0.62 | 1.09 | 1.11 | 0.82 | 0.12 | 0.44 | 99 | 69.8 | 65 | 50 | 11.2 | 12.7 | 38 | 26.7 | 14 | 16 | 51 | 16 | 27.7 | 28.2 | 20.8 | 3 | 11 | N/A | N/A
ASME 16.5 | 150 | 1 | 4.25 | 3.12 | 0.625 | 4 | 0.5 | 2.5 | 2.25 | 0.5 | 0.56 | 1.94 | 1.32 | 0.62 | 0.69 | 2.12 | 0.69 | 1.36 | 1.38 | 1.05 | 0.12 | 0.5 | 108 | 79.2 | 65 | 55 | 12.7 | 14.2 | 49 | 33.5 | 16 | 18 | 54 | 18 | 34.5 | 35.1 | 26.7 | 3 | 13 | N/A | N/A
ASME 16.5 | 150 | 1.25 | 4.62 | 3.5 | 0.625 | 4 | 0.5 | 2.75 | 2.25 | 0.56 | 0.62 | 2.31 | 1.66 | 0.75 | 0.81 | 2.19 | 0.81 | 1.7 | 1.72 | 1.38 | 0.19 | 0.56 | 117 | 88.9 | 70 | 55 | 14.2 | 15.7 | 59 | 42.2 | 19 | 21 | 56 | 21 | 43.2 | 43.7 | 35.1 | 5 | 14 | N/A | N/A
ASME 16.5 | 150 | 1.5 | 5 | 3.88 | 0.625 | 4 | 0.5 | 2.75 | 2.5 | 0.62 | 0.69 | 2.56 | 1.9 | 0.81 | 0.88 | 2.83 | 0.88 | 1.95 | 1.97 | 1.61 | 0.25 | 0.62 | 127 | 98.6 | 70 | 65 | 15.9 | 17.5 | 65 | 48.3 | 21 | 22 | 60 | 22 | 49.5 | 50 | 40.9 | 6 | 16 | N/A | N/A
ASME 16.5 | 150 | 2 | 6 | 4.75 | 0.75 | 4 | 0.625 | 3.25 | 2.75 | 0.69 | 0.75 | 3.06 | 2.38 | 0.94 | 1 | 2.44 | 1 | 2.44 | 2.46 | 2.07 | 0.31 | 0.69 | 152 | 120.6 | 85 | 70 | 17.5 | 19 | 78 | 60.5 | 24 | 25 | 62 | 25 | 61.9 | 62.5 | 52.6 | 8 | 18 | N/A | N/A
ASME 16.5 | 150 | 2.5 | 7 | 5.5 | 0.75 | 4 | 0.625 | 3.5 | 3 | 0.81 | 0.88 | 3.56 | 2.88 | 1.06 | 1.12 | 2.69 | 1.12 | 2.94 | 2.97 | 2.47 | 0.31 | 0.75 | 178 | 139.7 | 90 | 75 | 20.6 | 22.4 | 90 | 73.2 | 27 | 28 | 68 | 28 | 74.7 | 75.4 | 62.7 | 8 | 19 | N/A | N/A
ASME 16.5 | 150 | 3 | 7.5 | 6 | 0.75 | 4 | 0.625 | 3.5 | 3 | 0.88 | 0.94 | 4.25 | 3.5 | 1.12 | 1.19 | 2.69 | 1.19 | 3.57 | 3.6 | 3.07 | 0.38 | 0.81 | 190 | 152.4 | 90 | 75 | 22.4 | 23.9 | 108 | 88.9 | 28 | 30 | 68 | 30 | 90.7 | 91.4 | 78 | 10 | 21 | N/A | N/A
ASME 16.5 | 150 | 3.5 | 8.5 | 7 | 0.75 | 8 | 0.625 | 3.5 | 3 | 0.88 | 0.94 | 4.81 | 4 | 1.19 | 1.25 | 2.75 | 1.25 | 4.07 | 4.1 | 3.55 | 0.38 | … | 216 | 177.8 | 90 | 75 | 22.4 | 23.9 | 122 | 101.6 | 30 | 32 | 70 | 32 | 103.4 | 104.1 | 90.2 | 10 | … | N/A | N/A
ASME 16.5 | 150 | 4 | 9 | 7.5 | 0.75 | 8 | 0.625 | 3.5 | 3 | 0.88 | 0.94 | 5.31 | 4.5 | 1.25 | 1.31 | 2.94 | 1.31 | 4.57 | 4.6 | 4.03 | 0.44 | … | 229 | 190.5 | 90 | 75 | 22.4 | 23.9 | 135 | 114.3 | 32 | 33 | 75 | 33 | 116.1 | 116.8 | 102.4 | 11 | … | N/A | N/A
ASME 16.5 | 150 | 5 | 10 | 8.5 | 0.875 | 8 | 0.75 | 3.75 | 3.25 | 0.88 | 0.94 | 6.44 | 5.56 | 1.38 | 1.44 | 3.44 | 1.44 | 5.66 | 5.69 | 5.05 | 0.44 | … | 254 | 215.9 | 95 | 85 | 22.4 | 23.9 | 164 | 141.2 | 35 | 37 | 87 | 37 | 143.8 | 144.5 | 128.3 | 11 | … | N/A | N/A
ASME 16.5 | 150 | 6 | 11 | 9.5 | 0.875 | 8 | 0.75 | 4 | 3.25 | 0.94 | 1 | 7.56 | 6.63 | 1.5 | 1.56 | 3.44 | 1.56 | 6.72 | 6.75 | 6.07 | 0.5 | … | 279 | 241.3 | 100 | 85 | 23.9 | 25.4 | 192 | 168.4 | 38 | 40 | 87 | 40 | 170.7 | 171.4 | 154.2 | 13 | … | N/A | N/A
ASME 16.5 | 150 | 8 | 13.5 | 11.75 | 0.875 | 8 | 0.75 | 4.25 | 3.5 | 1.06 | 1.12 | 9.69 | 8.63 | 1.69 | 1.75 | 3.94 | 1.75 | 8.72 | 8.75 | 7.98 | 0.5 | … | 343 | 298.4 | 110 | 90 | 26.9 | 28.4 | 246 | 219.2 | 43 | 44 | 100 | 44 | 221.5 | 222.2 | 202.7 | 13 | … | N/A | N/A
ASME 16.5 | 150 | 10 | 16 | 14.25 | 1 | 12 | 0.875 | 4.5 | 4 | 1.12 | 1.19 | 12 | 10.75 | 1.88 | 1.94 | 3.94 | 1.94 | 10.88 | 10.92 | 10.02 | 0.5 | … | 406 | 362 | 115 | 100 | 28.4 | 30.2 | 305 | 273 | 48 | 49 | 100 | 49 | 276.4 | 277.4 | 254.5 | 13 | … | N/A | N/A
ASME 16.5 | 150 | 12 | 19 | 17 | 1 | 12 | 0.875 | 4.75 | 4 | 1.19 | 1.25 | 14.38 | 12.75 | 2.12 | 2.19 | 4.44 | 2.19 | 12.88 | 12.92 | 12 | 0.5 | … | 483 | 431.8 | 120 | 100 | 30.2 | 31.8 | 365 | 323.8 | 54 | 56 | 113 | 56 | 327.2 | 328.2 | 304.8 | 13 | … | N/A | N/A
ASME 16.5 | 150 | 14 | 21 | 18.75 | 1.125 | 12 | 1 | 5.25 | 4.5 | 1.31 | 1.38 | 15.75 | 14 | 2.19 | 3.12 | 4.94 | 2.25 | 14.14 | 14.18 | (8) | 0.5 | … | 533 | 476.2 | 135 | 115 | 33.3 | 35.1 | 400 | 355.6 | 56 | 79 | 125 | 57 | 359.2 | 360.2 | (8) | 13 | … | N/A | N/A
ASME 16.5 | 150 | 16 | 23.5 | 21.25 | 1.125 | 16 | 1 | 5.25 | 4.5 | 1.38 | 1.44 | 18 | 16 | 2.44 | 3.44 | 4.94 | 2.5 | 16.16 | 16.19 | (8) | 0.5 | … | 597 | 539.8 | 135 | 115 | 35.1 | 36.6 | 457 | 406.4 | 62 | 87 | 125 | 64 | 410.5 | 411.2 | (8) | 13 | … | N/A | N/A
ASME 16.5 | 150 | 18 | 25 | 22.75 | 1.25 | 16 | 1.125 | 5.75 | 5 | 1.5 | 1.56 | 19.88 | 18 | 2.62 | 3.81 | 5.44 | 2.69 | 18.18 | 18.2 | (8) | 0.5 | … | 635 | 577.8 | 145 | 125 | 38.1 | 39.6 | 505 | 457.2 | 67 | 97 | 138 | 68 | 461.8 | 462.3 | (8) | 13 | … | N/A | N/A
ASME 16.5 | 150 | 20 | 27.5 | 25 | 1.25 | 20 | 1.125 | 6.25 | 5.5 | 1.62 | 1.69 | 22 | 20 | 2.81 | 4.06 | 5.62 | 2.88 | 20.2 | 20.25 | (8) | 0.5 | … | 693 | 635 | 160 | 140 | 41.1 | 42.9 | 559 | 508 | 71 | 103 | 143 | 73 | 513.1 | 514.4 | (8) | 13 | … | N/A | N/A
ASME 16.5 | 150 | 22 | 29.5 | 27.25 | 1.375 | 20 | 1.25 | 6.75 | 6 | 1.75 | 1.81 | 24 | 22 | 3.06 | 4.25 | 5.82 | … | 22.22 | 22.25 | (8) | 0.5 | … | 749 | 692.2 | 170 | 150 | 44.4 | 46 | 610 | 558.8 | 78 | 108 | 148 | … | 564.4 | 565.2 | (8) | 13 | … | N/A | N/A
ASME 16.5 | 150 | 24 | 32 | 29.5 | 1.375 | 20 | 1.25 | 6.75 | 6 | 1.81 | 1.88 | 26.12 | 24 | 3.19 | 4.38 | 5.94 | 3.25 | 24.25 | 24.25 | (8) | 0.5 | … | 813 | 749.3 | 170 | 150 | 46 | 47.8 | 663 | 609.6 | 81 | 111 | 151 | 83 | 616 | 616 | (8) | 13 | … | N/A | N/A
ASME 16.5 | 300 | 0.5 | 3.75 | 2.62 | 0.625 | 4 | 0.5 | 2.5 | 2.25 | 0.5 | 0.56 | 1.5 | 0.84 | 0.81 | 0.88 | 2 | 0.62 | 0.88 | 0.9 | 0.62 | 0.12 | 0.38 | 95 | 66.5 | 65 | 55 | 12.7 | 14.2 | 38 | 21.3 | 21 | 22 | 51 | 16 | 22.4 | 22.9 | 15.7 | 3 | 10 | 0.93 | 23.6
ASME 16.5 | 300 | 0.75 | 4.62 | 3.25 | 0.75 | 4 | 0.625 | 3 | 2.5 | 0.56 | 0.62 | 1.88 | 1.05 | 0.94 | 1 | 2.19 | 0.62 | 1.09 | 1.11 | 0.82 | 0.12 | 0.44 | 117 | 82.6 | 75 | 65 | 14.2 | 15.7 | 48 | 26.7 | 24 | 25 | 56 | 16 | 27.7 | 28.2 | 20.8 | 3 | 11 | 1.14 | 29
ASME 16.5 | 300 | 1 | 4.88 | 3.5 | 0.75 | 4 | 0.625 | 3 | 2.5 | 0.62 | 0.69 | 2.12 | 1.32 | 1 | 1.06 | 2.38 | 0.69 | 1.36 | 1.38 | 1.05 | 0.12 | 0.5 | 124 | 88.9 | 75 | 65 | 15.7 | 17.5 | 54 | 33.5 | 25 | 27 | 60 | 18 | 34.5 | 35.1 | 26.7 | 3 | 13 | 1.41 | 35.8
ASME 16.5 | 300 | 1.25 | 5.25 | 3.88 | 0.75 | 4 | 0.625 | 3.25 | 2.75 | 0.69 | 0.75 | 2.5 | 1.66 | 1 | 1.06 | 2.5 | 0.81 | 1.7 | 1.72 | 1.38 | 0.19 | 0.56 | 133 | 98.6 | 85 | 70 | 17.5 | 19 | 64 | 42.2 | 25 | 27 | 64 | 21 | 43.2 | 43.7 | 35.1 | 5 | 14 | 1.75 | 44.4
ASME 16.5 | 300 | 1.5 | 6.12 | 4.5 | 0.875 | 4 | 0.75 | 3.5 | 3 | 0.75 | 0.81 | 2.75 | 1.9 | 1.13 | 1.16 | 2.63 | 0.88 | 1.95 | 1.97 | 1.61 | 0.25 | 0.62 | 155 | 114.3 | 90 | 75 | 19 | 20.6 | 70 | 48.3 | 29 | 30 | 67 | 22 | 49.5 | 50 | 40.9 | 6 | 16 | 1.98 | 50.3
ASME 16.5 | 300 | 2 | 6.5 | 5 | 0.75 | 8 | 0.625 | 3.5 | 3 | 0.81 | 0.88 | 3.31 | 2.38 | 1.25 | 1.31 | 2.69 | 1.12 | 2.44 | 2.46 | 2.07 | 0.31 | 0.69 | 165 | 127 | 90 | 75 | 20.6 | 22.4 | 84 | 60.5 | 32 | 33 | 68 | 28 | 62 | 62.5 | 52.6 | 8 | 17 | 2.5 | 63.5
ASME 16.5 | 300 | 2.5 | 7.5 | 5.88 | 0.875 | 8 | 0.75 | 4 | 3.25 | 0.94 | 1 | 3.94 | 2.88 | 1.44 | 1.5 | 2.94 | 1.25 | 2.94 | 2.97 | 2.47 | 0.31 | 0.75 | 190 | 149.4 | 100 | 85 | 23.9 | 25.4 | 100 | 73.2 | 37 | 38 | 75 | 32 | 74.7 | 75.4 | 62.7 | 8 | 19 | 3 | 76.2
ASME 16.5 | 300 | 3 | 8.25 | 6.62 | 0.875 | 8 | 0.75 | 4.25 | 3.5 | 1.06 | 1.12 | 4.62 | 3.5 | 1.63 | 1.69 | 3.06 | 1.25 | 3.57 | 3.6 | 3.07 | 0.38 | 0.81 | 210 | 168.1 | 110 | 90 | 26.9 | 28.4 | 117 | 88.9 | 41 | 43 | 78 | 32 | 90.7 | 91.4 | 78 | 10 | 21 | 3.63 | 92.2
ASME 16.5 | 300 | 3.5 | 9 | 7.25 | 0.875 | 8 | 0.75 | 4.25 | 3.75 | 1.12 | 1.19 | 5.25 | 4 | 1.69 | 1.75 | 3.13 | 1.44 | 4.07 | 4.1 | 3.55 | 0.38 | … | 229 | 184.2 | 110 | 95 | 28.4 | 30.2 | 133 | 101.6 | 43 | 44 | 80 | 37 | 103.4 | 104.1 | 90.2 | 10 | … | 4.13 | 104.9
ASME 16.5 | 300 | 4 | 10 | 7.88 | 0.875 | 8 | 0.75 | 4.5 | 3.75 | 1.19 | 1.25 | 5.75 | 4.5 | 1.82 | 1.88 | 3.32 | 1.44 | 4.57 | 4.6 | 4.03 | 0.44 | … | 254 | 200.2 | 115 | 95 | 30.2 | 31.8 | 146 | 114.3 | 46 | 48 | 84 | 37 | 116.1 | 116.8 | 102.4 | 11 | … | 4.63 | 117.6
ASME 16.5 | 300 | 5 | 11 | 9.25 | 0.875 | 8 | 0.75 | 4.75 | 4.25 | 1.31 | 1.38 | 7 | 5.56 | 1.94 | 2 | 3.82 | 1.69 | 5.66 | 5.69 | 5.05 | 0.44 | … | 279 | 235 | 120 | 110 | 33.3 | 35.1 | 178 | 141.2 | 49 | 51 | 97 | 43 | 143.8 | 144.5 | 128.3 | 11 | … | 5.69 | 144.5
ASME 16.5 | 300 | 6 | 12.5 | 10.62 | 0.875 | 12 | 0.75 | 4.75 | 4.25 | 1.38 | 1.44 | 8.12 | 6.63 | 2 | 2.06 | 3.82 | 1.81 | 6.72 | 6.75 | 6.07 | 0.5 | … | 318 | 269.7 | 120 | 110 | 35.1 | 36.6 | 206 | 168.4 | 51 | 52 | 97 | 46 | 170.7 | 171.4 | 154.2 | 13 | … | 6.75 | 171.4
ASME 16.5 | 300 | 8 | 15 | 13 | 1 | 12 | 0.875 | 5.5 | 4.75 | 1.56 | 1.62 | 10.25 | 8.63 | 2.38 | 2.44 | 4.32 | 2 | 8.72 | 8.75 | 7.98 | 0.5 | … | 381 | 330.2 | 140 | 120 | 39.6 | 41.1 | 260 | 219.2 | 60 | 62 | 110 | 51 | 221.5 | 222.2 | 202.7 | 13 | … | 8.75 | 222.2
ASME 16.5 | 300 | 10 | 17.5 | 15.25 | 1.125 | 16 | 1 | 6.25 | 5.5 | 1.81 | 1.88 | 12.62 | 10.75 | 2.56 | 3.75 | 4.56 | 2.19 | 10.88 | 10.92 | 10.02 | 0.5 | … | 444 | 387.4 | 160 | 140 | 46 | 47.8 | 321 | 273 | 65 | 95 | 116 | 56 | 276.4 | 277.4 | 254.5 | 13 | … | 10.88 | 276.4
ASME 16.5 | 300 | 12 | 20.5 | 17.75 | 1.25 | 16 | 1.125 | 6.75 | 5.75 | 1.94 | 2 | 14.75 | 12.75 | 2.82 | 4 | 5.06 | 2.38 | 12.88 | 12.92 | 12 | 0.5 | … | 521 | 450.8 | 170 | 145 | 49.3 | 50.8 | 375 | 323.8 | 72 | 102 | 129 | 60 | 327.2 | 328.2 | 304.8 | 13 | … | 12.94 | 328.7
ASME 16.5 | 300 | 14 | 23 | 20.25 | 1.25 | 20 | 1.125 | 7 | 6.25 | 2.06 | 2.12 | 16.75 | 14 | 2.94 | 4.38 | 5.56 | 2.5 | 14.14 | 14.18 | (7) | 0.5 | … | 584 | 514.4 | 180 | 160 | 52.3 | 53.8 | 425 | 355.6 | 75 | 111 | 141 | 64 | 359.2 | 360.2 | (7) | 13 | … | 14.19 | 360.4
ASME 16.5 | 300 | 16 | 25.5 | 22.5 | 1.375 | 20 | 1.25 | 7.5 | 6.5 | 2.19 | 2.25 | 19 | 16 | 3.19 | 4.75 | 5.69 | 2.69 | 16.16 | 16.19 | (7) | 0.5 | … | 648 | 571.5 | 190 | 165 | 55.6 | 57.2 | 483 | 406.4 | 81 | 121 | 145 | 68 | 410.5 | 411.2 | (7) | 13 | … | 16.19 | 411.2
ASME 16.5 | 300 | 18 | 28 | 24.75 | 1.375 | 24 | 1.25 | 7.75 | 6.75 | 2.31 | 2.38 | 21 | 18 | 3.44 | 5.12 | 6.19 | 2.75 | 18.18 | 18.2 | (7) | 0.5 | … | 711 | 628.6 | 195 | 170 | 58.7 | 60.5 | 533 | 457.2 | 87 | 130 | 157 | 70 | 461.8 | 462.3 | (7) | 13 | … | 18.19 | 462
ASME 16.5 | 300 | 20 | 30.5 | 27 | 1.375 | 24 | 1.25 | 8 | 7.25 | 2.44 | 2.5 | 23.12 | 20 | 3.69 | 5.5 | 6.32 | 2.88 | 20.2 | 20.25 | (7) | 0.5 | … | 775 | 685.8 | 205 | 185 | 62 | 63.5 | 587 | 508 | 94 | 140 | 161 | 73 | 513.1 | 514.4 | (7) | 13 | … | 20.19 | 512.8
ASME 16.5 | 300 | 22 | 33 | 29.25 | 1.625 | 24 | 1.5 | 9 | 8 | 2.56 | 2.62 | 25.25 | 22 | 3.94 | 5.69 | 6.44 | … | 22.22 | 22.25 | (7) | 0.5 | … | 838 | 743 | 230 | 205 | 65 | 66.5 | 641 | 558.8 | 100 | 145 | 164 | … | 564.4 | 565.2 | (7) | 13 | … | … | …
ASME 16.5 | 300 | 24 | 36 | 32 | 1.625 | 24 | 1.5 | 9 | 8 | 2.69 | 2.75 | 27.62 | 24 | 4.13 | 6 | 6.56 | 3.25 | 24.25 | 24.25 | (7) | 0.5 | … | 914 | 812.8 | 230 | 205 | 68.3 | 68.8 | 702 | 609.6 | 105 | 152 | 167 | 83 | 616 | 616 | (7) | 13 | … | 24.19 | 614.4
ASME 16.5 | 400 | 0.5 | (5) | (5) | (5) | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5)
ASME 16.5 | 400 | 0.75 | (5) | (5) | (5) | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5)
ASME 16.5 | 400 | 1 | (5) | (5) | (5) | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5)
ASME 16.5 | 400 | 1.25 | (5) | (5) | (5) | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5)
ASME 16.5 | 400 | 1.5 | (5) | (5) | (5) | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5)
ASME 16.5 | 400 | 2 | (5) | (5) | (5) | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5)
ASME 16.5 | 400 | 2.5 | (5) | (5) | (5) | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5)
ASME 16.5 | 400 | 3 | (5) | (5) | (5) | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5)
ASME 16.5 | 400 | 3.5 | (5) | (5) | (5) | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5)
ASME 16.5 | 400 | 4 | 10 | 7.88 | 1 | 8 | 0.875 |  |  | 1.38 | N/A | 5.75 | 4.5 | 2 | 2 | 3.5 | 1.44 | 4.57 | 4.63 | (5) | 0.44 | N/A | 254 | 200.2 |  |  | 35.1 | N/A | 146 | 114.3 | 51 | 51 | 89 | 37 | 116.1 | 116.8 | (5) | 11 | N/A | 4.63 | 117.6 | 5.5 | 5.25 | 140 | 135
ASME 16.5 | 400 | 5 | 11 | 9.25 | 1 | 8 | 0.875 |  |  | 1.5 | N/A | 7 | 5.56 | 2.12 | 2.12 | 4 | 1.69 | 5.66 | 5.69 | (5) | 0.44 | N/A | 279 | 235 |  |  | 38.1 | N/A | 178 | 141.2 | 54 | 54 | 102 | 43 | 143.8 | 144.5 | (5) | 11 | N/A | 5.69 | 144.5 | 5.75 | 5.25 | 145 | 135
ASME 16.5 | 400 | 6 | 12.5 | 10.62 | 1 | 12 | 0.875 |  |  | 1.62 | N/A | 8.12 | 6.63 | 2.25 | 2.25 | 4.06 | 1.81 | 6.72 | 6.75 | (5) | 0.5 | N/A | 318 | 269.7 |  |  | 41.1 | N/A | 206 | 168.4 | 57 | 57 | 103 | 46 | 170.7 | 171.4 | (5) | 13 | N/A | 6.75 | 171.4 | 6 | 5.75 | 150 | 145
ASME 16.5 | 400 | 8 | 15 | 13 | 1.125 | 12 | 1 |  |  | 1.88 | N/A | 10.25 | 8.63 | 2.69 | 2.69 | 4.62 | 2 | 8.72 | 8.75 | (5) | 0.5 | N/A | 381 | 330.2 |  |  | 47.8 | N/A | 260 | 219.2 | 68 | 68 | 117 | 51 | 221.5 | 222.2 | (5) | 13 | N/A | 8.75 | 222.2 | 6.75 | 6.5 | 170 | 165
ASME 16.5 | 400 | 10 | 17.5 | 15.25 | 1.25 | 16 | 1.125 |  |  | 2.12 | N/A | 12.62 | 10.75 | 2.88 | 4 | 4.88 | 2.19 | 10.88 | 10.92 | (5) | 0.5 | N/A | 444 | 387.4 |  |  | 53.8 | N/A | 321 | 273 | 73 | 102 | 124 | 56 | 276.4 | 277.4 | (5) | 13 | N/A | 10.88 | 276.4 | 7.5 | 7.25 | 190 | 185
ASME 16.5 | 400 | 12 | 20.5 | 17.75 | 1.375 | 16 | 1.25 |  |  | 2.25 | N/A | 14.75 | 12.75 | 3.12 | 4.25 | 5.38 | 2.38 | 12.88 | 12.92 | (5) | 0.5 | N/A | 521 | 450.8 |  |  | 57.2 | N/A | 375 | 323.8 | 79 | 108 | 137 | 60 | 327.2 | 328.2 | (5) | 13 | N/A | 12.94 | 328.7 | 8 | 7.75 | 205 | 195
ASME 16.5 | 400 | 14 | 23 | 20.25 | 1.375 | 20 | 1.25 |  |  | 2.38 | N/A | 16.75 | 14 | 3.31 | 4.62 | 5.88 | 2.5 | 14.14 | 14.18 | (5) | 0.5 | N/A | 584 | 514.4 |  |  | 60.5 | N/A | 425 | 355.6 | 84 | 117 | 149 | 64 | 359.2 | 360.2 | (5) | 13 | N/A | 14.19 | 360.4 | 8.25 | 8 | 210 | 205
ASME 16.5 | 400 | 16 | 25.5 | 23 | 1.5 | 20 | 1.375 |  |  | 2.5 | N/A | 19 | 16 | 3.69 | 5 | 6 | 2.69 | 16.16 | 16.19 | (5) | 0.5 | N/A | 648 | 571.5 |  |  | 63.5 | N/A | 483 | 406.4 | 94 | 127 | 152 | 68 | 410.5 | 411.2 | (5) | 13 | N/A | 16.19 | 411.2 | 8.75 | 8.5 | 220 | 215
ASME 16.5 | 400 | 18 | 28 | 24.75 | 1.5 | 24 | 1.375 |  |  | 2.62 | N/A | 21 | 18 | 3.88 | 5.38 | 6.5 | 2.75 | 18.18 | 18.2 | (5) | 0.5 | N/A | 711 | 628.6 |  |  | 66.5 | N/A | 533 | 457.2 | 99 | 137 | 165 | 70 | 461.8 | 462.3 | (5) | 13 | N/A | 18.19 | 462 | 9 | 8.75 | 230 | 220
ASME 16.5 | 400 | 20 | 30.5 | 27 | 1.625 | 24 | 1.5 |  |  | 2.75 | N/A | 23.12 | 20 | 4 | 5.75 | 6.62 | 2.88 | 20.2 | 20.25 | (5) | 0.5 | N/A | 775 | 685.8 |  |  | 69.8 | N/A | 587 | 508 | 102 | 146 | 168 | 73 | 513.1 | 514.4 | (5) | 13 | N/A | 20.19 | 512.8 | 9.5 | 9.25 | 240 | 235
ASME 16.5 | 400 | 22 | 33 | 29.25 | 1.75 | 24 | 1.625 |  |  | 2.88 | N/A | 25.25 | 22 | 4.25 | 6 | 6.75 | … | 22.22 | 22.25 | (5) | 0.5 | N/A | 838 | 743 |  |  | 73.2 | N/A | 641 | 558.8 | 108 | 152 | 171 | … | 564.4 | 565.2 | (5) | 13 | N/A | … | … | 10 | 9.75 | 255 | 250
ASME 16.5 | 400 | 24 | 36 | 32 | 1.875 | 24 | 1.75 |  |  | 3 | N/A | 27.62 | 24 | 4.5 | 6.25 | 6.88 | 3.25 | 24.25 | 24.25 | (5) | 0.5 | N/A | 914 | 812.8 |  |  | 76.2 | N/A | 702 | 609.6 | 114 | 159 | 175 | 83 | 616 | 616 | (5) | 13 | N/A | 24.19 | 614.4 | 10.5 | 10.25 | 265 | 260
ASME 16.5 | 600 | 0.5 | 3.75 | 2.62 | 0.625 | 4 | 0.5 |  |  | 0.56 | N/A | 1.5 | 0.84 | 0.88 | 0.88 | 2.06 | 0.62 | 0.88 | 0.9 | (4) | 0.12 | 0.38 | 95 | 66.5 |  |  | 14.2 | N/A | 38 | 21.3 | 22 | 22 | 52 | 16 | 22.4 | 22.9 | (4) | 3 | 10 | 0.93 | 23.6 | 3 | 2.75 | 75 | 70
ASME 16.5 | 600 | 0.75 | 4.62 | 3.25 | 0.75 | 4 | 0.625 |  |  | 0.62 | N/A | 1.88 | 1.05 | 1 | 1 | 2.25 | 0.62 | 1.09 | 1.11 | (4) | 0.12 | 0.44 | 117 | 82.6 |  |  | 15.7 | N/A | 48 | 26.7 | 25 | 25 | 57 | 16 | 27.7 | 28.2 | (4) | 3 | 11 | 1.14 | 29 | 3.5 | 3.25 | 90 | 85
ASME 16.5 | 600 | 1 | 4.88 | 3.5 | 0.75 | 4 | 0.625 |  |  | 0.69 | N/A | 2.12 | 1.32 | 1.06 | 1.06 | 2.44 | 0.69 | 1.36 | 1.38 | (4) | 0.12 | 0.5 | 124 | 88.9 |  |  | 17.5 | N/A | 54 | 33.5 | 27 | 27 | 62 | 18 | 34.5 | 35.1 | (4) | 3 | 13 | 1.41 | 35.8 | 3.5 | 3.25 | 90 | 85
ASME 16.5 | 600 | 1.25 | 5.25 | 3.88 | 0.75 | 4 | 0.625 |  |  | 0.81 | N/A | 2.5 | 1.66 | 1.12 | 1.12 | 2.62 | 0.81 | 1.7 | 1.72 | (4) | 0.19 | 0.56 | 133 | 98.6 |  |  | 20.3 | N/A | 64 | 42.2 | 28 | 28 | 67 | 21 | 43.2 | 43.7 | (4) | 5 | 14 | 1.75 | 44.4 | 3.75 | 3.5 | 95 | 90
ASME 16.5 | 600 | 1.5 | 6.12 | 4.5 | 0.875 | 4 | 0.75 |  |  | 0.88 | N/A | 2.75 | 1.9 | 1.25 | 1.25 | 2.75 | 0.88 | 1.95 | 1.97 | (4) | 0.25 | 0.62 | 155 | 114.3 |  |  | 22.4 | N/A | 70 | 48.3 | 32 | 32 | 70 | 22 | 49.5 | 50 | (4) | 6 | 16 | 1.99 | 50.5 | 4.25 | 4 | 110 | 100
ASME 16.5 | 600 | 2 | 6.5 | 5 | 0.75 | 8 | 0.625 |  |  | 1 | N/A | 3.31 | 2.38 | 1.44 | 1.44 | 2.88 | 1.12 | 2.44 | 2.46 | (4) | 0.31 | 0.69 | 165 | 127 |  |  | 25.4 | N/A | 84 | 60.5 | 37 | 37 | 73 | 28 | 62 | 62.5 | (4) | 8 | 18 | 0.25 | 63.5 | 4.25 | 4 | 110 | 100
ASME 16.5 | 600 | 2.5 | 7.5 | 5.88 | 0.875 | 8 | 0.75 |  |  | 1.12 | N/A | 3.94 | 2.88 | 1.62 | 1.62 | 3.12 | 1.25 | 2.94 | 2.97 | (4) | 0.31 | 0.75 | 190 | 149.4 |  |  | 28.4 | N/A | 100 | 73.2 | 41 | 41 | 79 | 32 | 74.7 | 75.4 | (4) | 8 | 19 | 3 | 76.2 | 4.75 | 4.5 | 120 | 115
ASME 16.5 | 600 | 3 | 8.25 | 6.62 | 0.875 | 8 | 0.75 |  |  | 1.25 | N/A | 4.62 | 3.5 | 1.81 | 1.81 | 3.25 | 1.38 | 3.57 | 3.6 | (4) | 0.38 | 0.81 | 210 | 168.1 |  |  | 31.8 | N/A | 117 | 88.9 | 46 | 46 | 83 | 35 | 90.7 | 91.4 | (4) | 10 | 21 | 3.63 | 92.2 | 5 | 4.75 | 125 | 120
ASME 16.5 | 600 | 3.5 | 9 | 7.25 | 1 | 8 | 0.875 |  |  | 1.38 | N/A | 5.25 | 4 | 1.94 | 1.94 | 3.38 | 1.56 | 4.07 | 4.1 | (4) | 0.38 | … | 229 | 184.2 |  |  | 35.1 | N/A | 133 | 101.6 | 49 | 49 | 86 | 40 | 103.4 | 104.1 | (4) | 10 | … | 4.13 | 104.9 | 5.5 | 5.25 | 140 | 135
ASME 16.5 | 600 | 4 | 10.75 | 8.5 | 1 | 8 | 0.875 |  |  | 1.5 | N/A | 6 | 4.5 | 2.12 | 2.12 | 4 | 1.62 | 4.57 | 4.6 | (4) | 0.44 | … | 273 | 215.9 |  |  | 38.1 | N/A | 152 | 114.3 | 54 | 54 | 102 | 41 | 116.1 | 116.8 | (4) | 11 | … | 4.63 | 117.6 | 5.75 | 5.5 | 145 | 140
ASME 16.5 | 600 | 5 | 13 | 10.5 | 1.125 | 8 | 1 |  |  | 1.75 | N/A | 7.44 | 5.56 | 2.38 | 2.38 | 4.5 | 1.88 | 5.66 | 5.69 | (4) | 0.44 | … | 330 | 266.7 |  |  | 44.4 | N/A | 189 | 141.2 | 60 | 60 | 114 | 48 | 143.8 | 144.5 | (4) | 11 | … | 5.69 | 144.5 | 6.5 | 6.25 | 165 | 160
ASME 16.5 | 600 | 6 | 14 | 11.5 | 1.125 | 12 | 1 |  |  | 1.88 | N/A | 8.75 | 6.63 | 2.62 | 2.62 | 4.62 | 2 | 6.72 | 6.75 | (4) | 0.5 | … | 356 | 292.1 |  |  | 47.8 | N/A | 222 | 168.4 | 67 | 67 | 117 | 51 | 170.7 | 171.4 | (4) | 13 | … | 6.75 | 171.4 | 6.75 | 6.5 | 170 | 165
ASME 16.5 | 600 | 8 | 16.5 | 13.75 | 1.25 | 12 | 1.125 |  |  | 2.19 | N/A | 10.75 | 8.63 | 3 | 3 | 5.25 | 2.25 | 8.72 | 8.75 | (4) | 0.5 | … | 419 | 349.2 |  |  | 55.6 | N/A | 273 | 219.2 | 76 | 76 | 133 | 57 | 221.5 | 222.2 | (4) | 13 | … | 8.75 | 222.2 | 7.5 | 7.25 | 190 | 185
ASME 16.5 | 600 | 10 | 20 | 17 | 1.375 | 16 | 1.25 |  |  | 2.5 | N/A | 13.5 | 10.75 | 3.38 | 4.38 | 6 | 2.56 | 10.88 | 10.92 | (4) | 0.5 | … | 508 | 431.8 |  |  | 63.5 | N/A | 343 | 273 | 86 | 111 | 152 | 65 | 276.2 | 277.4 | (4) | 13 | … | 10.88 | 276.4 | 8.5 | 8.25 | 215 | 210
ASME 16.5 | 600 | 12 | 22 | 19.25 | 1.375 | 20 | 1.25 |  |  | 2.62 | N/A | 15.75 | 12.75 | 3.62 | 4.62 | 6.12 | 2.75 | 12.88 | 12.92 | (4) | 0.5 | … | 559 | 489 |  |  | 66.5 | N/A | 400 | 323.8 | 92 | 117 | 155 | 70 | 327 | 328.2 | (4) | 13 | … | 12.94 | 328.7 | 8.75 | 8.5 | 220 | 215
ASME 16.5 | 600 | 14 | 23.75 | 20.75 | 1.5 | 20 | 1.375 |  |  | 2.75 | N/A | 17 | 14 | 3.69 | 5 | 6.5 | 2.88 | 14.14 | 14.18 | (4) | 0.5 | … | 603 | 527 |  |  | 69.8 | N/A | 432 | 355.6 | 94 | 127 | 165 | 73 | 359.2 | 360.2 | (4) | 13 | … | 14.19 | 360.4 | 9.25 | 9 | 235 | 230
ASME 16.5 | 600 | 16 | 27 | 23.75 | 1.625 | 20 | 1.5 |  |  | 3 | N/A | 19.5 | 16 | 4.19 | 5.5 | 7 | 3.06 | 16.16 | 16.19 | (4) | 0.5 | … | 686 | 603.2 |  |  | 76.2 | N/A | 495 | 406.4 | 106 | 140 | 178 | 78 | 410.5 | 411.2 | (4) | 13 | … | 16.19 | 411.2 | 10 | 9.75 | 255 | 250
ASME 16.5 | 600 | 18 | 29.25 | 25.75 | 1.75 | 20 | 1.625 |  |  | 3.25 | N/A | 21.5 | 18 | 4.62 | 6 | 7.25 | 3.12 | 18.18 | 18.2 | (4) | 0.5 | … | 743 | 654 |  |  | 82.6 | N/A | 546 | 457.2 | 117 | 152 | 184 | 79 | 461.8 | 462.3 | (4) | 13 | … | 18.19 | 462 | 10.75 | 10.5 | 275 | 265
ASME 16.5 | 600 | 20 | 32 | 28.5 | 1.75 | 24 | 1.625 |  |  | 3.5 | N/A | 24 | 20 | 5 | 6.5 | 7.5 | 3.25 | 20.2 | 20.25 | (4) | 0.5 | … | 813 | 723.9 |  |  | 88.9 | N/A | 610 | 508 | 127 | 165 | 190 | 83 | 513.1 | 514.4 | (4) | 13 | … | 20.19 | 512.8 | 11.25 | 11 | 285 | 280
ASME 16.5 | 600 | 22 | 34.25 | 30.62 | 1.875 | 24 | 1.75 |  |  | 3.75 | N/A | 26.25 | 22 | 5.25 | 6.88 | 7.75 | … | 22.22 | 22.25 | (4) | 0.5 | … | 870 | 777.7 |  |  | 95.2 | N/A | 663 | 558.8 | 133 | 175 | 197 | … | 564.4 | 565.2 | (4) | 13 | … | … | … | 12 | … | 305 | …
ASME 16.5 | 600 | 24 | 37 | 33 | 2 | 24 | 1.875 |  |  | 4 | N/A | 28.25 | 24 | 5.5 | 7.25 | 8 | 3.62 | 24.25 | 24.25 | (4) | 0.5 | … | 940 | 838.2 |  |  | 101.6 | N/A | 718 | 609.6 | 140 | 184 | 203 | 92 | 616 | 616 | (4) | 13 | … | 24.19 | 614.4 | 13 | 12.75 | 330 | 325
ASME 16.5 | 900 | 0.5 | (5) | (5) | (5) | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5)
ASME 16.5 | 900 | 0.75 | (5) | (5) | (5) | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5)
ASME 16.5 | 900 | 1 | (5) | (5) | (5) | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5)
ASME 16.5 | 900 | 1.25 | (5) | (5) | (5) | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5)
ASME 16.5 | 900 | 1.5 | (5) | (5) | (5) | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5)
ASME 16.5 | 900 | 2 | (5) | (5) | (5) | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5)
ASME 16.5 | 900 | 2.5 | (5) | (5) | (5) | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (5) | (5) |  |  | (4) | N/A | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | (4) | N/A | (4) | (4) | (5) | (5) | (5) | (5)
ASME 16.5 | 900 | 3 | 9.5 | 7.5 | 1 | 8 | 0.875 |  |  | 1.5 | N/A | 5 | 3.5 | 2.12 | 2.12 | 4 | 1.62 | 3.57 | 3.6 | (5) | 0.38 | N/A | 241 | 190.5 |  |  | 38.1 | N/A | 127 | 88.9 | 54 | 54 | 102 | 41 | 90.7 | 91.4 | (5) | 10 | N/A | 3.63 | 92.2 | 5.75 | 5.75 | 145 | 145
ASME 16.5 | 900 | 4 | 11.5 | 9.25 | 1.25 | 8 | 1.125 |  |  | 1.75 | N/A | 6.25 | 4.5 | 2.75 | 2.75 | 4.5 | 1.88 | 4.57 | 4.6 | (5) | 0.44 | N/A | 292 | 235 |  |  | 44.5 | N/A | 159 | 114.3 | 70 | 70 | 114 | 48 | 116.1 | 116.8 | (5) | 11 | N/A | 4.63 | 117.6 | 6.75 | 6.75 | 170 | 170
ASME 16.5 | 900 | 5 | 13.75 | 11 | 1.375 | 8 | 1.25 |  |  | 2 | N/A | 7.5 | 5.56 | 3.12 | 3.12 | 5 | 2.12 | 5.66 | 5.69 | (5) | 0.44 | N/A | 349 | 279.4 |  |  | 50.8 | N/A | 190 | 141.2 | 79 | 79 | 127 | 54 | 143.8 | 144.5 | (5) | 11 | N/A | 5.69 | 144.5 | 7.5 | 7.5 | 190 | 190
ASME 16.5 | 900 | 6 | 15 | 12.5 | 1.25 | 12 | 1.125 |  |  | 2.19 | N/A | 9.25 | 6.63 | 3.38 | 3.38 | 5.5 | 2.25 | 6.72 | 6.75 | (5) | 0.5 | N/A | 381 | 317.5 |  |  | 55.6 | N/A | 235 | 168.4 | 86 | 86 | 140 | 57 | 170.7 | 171.4 | (5) | 13 | N/A | 6.75 | 171.4 | 7.5 | 7.75 | 190 | 195
ASME 16.5 | 900 | 8 | 18.5 | 15.5 | 1.5 | 12 | 1.375 |  |  | 2.5 | N/A | 11.75 | 8.63 | 4 | 4.5 | 6.38 | 2.5 | 8.72 | 8.75 | (5) | 0.5 | N/A | 470 | 393.7 |  |  | 63.5 | N/A | 298 | 219.2 | 102 | 114 | 162 | 64 | 221.5 | 222.2 | (5) | 13 | N/A | 8.75 | 222.2 | 8.75 | 8.75 | 220 | 220
ASME 16.5 | 900 | 10 | 21.5 | 18.5 | 1.5 | 16 | 1.375 |  |  | 2.75 | N/A | 14.5 | 10.75 | 4.25 | 5 | 7.25 | 2.81 | 10.88 | 10.92 | (5) | 0.5 | N/A | 546 | 469.9 |  |  | 69.8 | N/A | 368 | 273 | 108 | 127 | 184 | 71 | 276.4 | 277.4 | (5) | 13 | N/A | 10.88 | 276.4 | 9.25 | 9.25 | 235 | 235
ASME 16.5 | 900 | 12 | 24 | 21 | 1.5 | 20 | 1.375 |  |  | 3.12 | N/A | 16.5 | 12.75 | 4.62 | 5.62 | 7.88 | 3 | 12.88 | 12.92 | (5) | 0.5 | N/A | 610 | 533.4 |  |  | 79.2 | N/A | 419 | 323.8 | 117 | 143 | 200 | 76 | 327.2 | 328.2 | (5) | 13 | N/A | 12.94 | 328.7 | 10 | 10 | 255 | 255
ASME 16.5 | 900 | 14 | 25.25 | 22 | 1.625 | 20 | 1.5 |  |  | 3.38 | N/A | 17.75 | 14 | 5.12 | 6.12 | 8.38 | 3.25 | 14.14 | 14.18 | (5) | 0.5 | N/A | 641 | 558.8 |  |  | 85.9 | N/A | 451 | 355.6 | 130 | 155 | 213 | 83 | 359.2 | 360.2 | (5) | 13 | N/A | 14.19 | 360.4 | 10.75 | 11 | 275 | 280
ASME 16.5 | 900 | 16 | 27.75 | 24.25 | 1.75 | 20 | 1.625 |  |  | 3.5 | N/A | 20 | 16 | 5.25 | 6.5 | 8.5 | 3.38 | 16.16 | 16.19 | (5) | 0.5 | N/A | 705 | 616 |  |  | 88.9 | N/A | 508 | 406.4 | 133 | 165 | 216 | 86 | 410.5 | 411.2 | (5) | 13 | N/A | 16.19 | 411.2 | 11.25 | 11.5 | 285 | 290
ASME 16.5 | 900 | 18 | 31 | 27 | 2 | 20 | 1.875 |  |  | 4 | N/A | 22.25 | 18 | 6 | 7.5 | 9 | 3.5 | 18.18 | 18.2 | (5) | 0.5 | N/A | 787 | 685.8 |  |  | 101.6 | N/A | 565 | 457.2 | 152 | 190 | 229 | 89 | 461.8 | 462.3 | (5) | 13 | N/A | 18.19 | 462 | 12.75 | 13.25 | 325 | 335
ASME 16.5 | 900 | 20 | 33.75 | 29.5 | 2.125 | 20 | 2 |  |  | 4.25 | N/A | 24.5 | 20 | 6.25 | 8.25 | 9.75 | 3.62 | 20.2 | 20.25 | (5) | 0.5 | N/A | 857 | 749.3 |  |  | 108 | N/A | 622 | 508 | 159 | 210 | 248 | 92 | 513.1 | 514.4 | (5) | 13 | N/A | 20.19 | 512.8 | 13.75 | 14.25 | 350 | 360
ASME 16.5 | 900 | 24 | 41 | 35.5 | 2.625 | 20 | 2.5 |  |  | 5.5 | N/A | 29.5 | 24 | 8 | 10.5 | 11.5 | 4 | 24.25 | 24.25 | (5) | 0.5 | N/A | 1041 | 901.7 |  |  | 139.7 | N/A | 749 | 609.6 | 203 | 267 | 292 | 102 | 616 | 616 | (5) | 13 | N/A | 24.19 | 614.4 | 17.25 | 18 | 440 | 455
ASME 16.5 | 1500 | 0.5 | 4.75 | 3.25 | 0.875 | 4 | 0.75 |  |  | 0.88 | N/A | 1.5 | 0.84 | 1.25 | 1.25 | 2.28 | 0.88 | 0.88 | 0.9 | (4) | 0.12 | 0.38 | 121 | 82.6 |  |  | 22.4 | N/A | 38 | 21.3 | 32 | 32 | 60 | 22 | 22.4 | 22.9 | (4) | 3 | 10 | 0.93 | 23.6 | 4.25 | 4 | 110 | 100
ASME 16.5 | 1500 | 0.75 | 5.12 | 3.5 | 0.875 | 4 | 0.75 |  |  | 1 | N/A | 1.75 | 1.05 | 1.38 | 1.38 | 2.75 | 1 | 1.09 | 1.11 | (4) | 0.12 | 0.44 | 130 | 88.9 |  |  | 25.4 | N/A | 44 | 26.7 | 35 | 35 | 70 | 25 | 27.7 | 28.2 | (4) | 3 | 11 | 1.14 | 29 | 4.5 | 4.25 | 115 | 110
ASME 16.5 | 1500 | 1 | 5.88 | 4 | 1 | 4 | 0.875 |  |  | 1.12 | N/A | 2.06 | 1.32 | 1.62 | 1.62 | 2.88 | 1.12 | 1.36 | 1.38 | (4) | 0.12 | 0.5 | 149 | 101.6 |  |  | 28.4 | N/A | 52 | 33.5 | 41 | 41 | 73 | 28 | 34.5 | 35.4 | (4) | 3 | 13 | 1.41 | 35.8 | 5 | 4.75 | 125 | 120
ASME 16.5 | 1500 | 1.25 | 6.25 | 4.38 | 1 | 4 | 0.875 |  |  | 1.12 | N/A | 2.5 | 1.66 | 1.62 | 1.62 | 2.88 | 1.19 | 1.7 | 1.72 | (4) | 0.19 | 0.56 | 159 | 111.1 |  |  | 28.4 | N/A | 64 | 42.2 | 41 | 41 | 73 | 30 | 43.2 | 43.7 | (4) | 5 | 14 | 1.75 | 44.4 | 5 | 4.75 | 125 | 120
ASME 16.5 | 1500 | 1.5 | 7 | 4.88 | 1.125 | 4 | 1 |  |  | 1.25 | N/A | 2.75 | 1.9 | 1.75 | 1.75 | 3.25 | 1.25 | 1.95 | 1.97 | (4) | 0.25 | 0.62 | 178 | 124 |  |  | 31.8 | N/A | 70 | 48.3 | 44 | 44 | 83 | 32 | 49.5 | 50 | (4) | 6 | 16 | 1.99 | 50.5 | 5.5 | 5.25 | 140 | 135
ASME 16.5 | 1500 | 2 | 8.5 | 6.5 | 1 | 8 | 0.875 |  |  | 1.5 | N/A | 4.12 | 2.38 | 2.25 | 2.25 | 4 | 1.5 | 2.44 | 2.46 | (4) | 0.31 | 0.69 | 216 | 165.1 |  |  | 38.1 | N/A | 105 | 60.5 | 57 | 57 | 102 | 38 | 62 | 62.5 | (4) | 8 | 18 | 2.5 | 63.5 | 5.75 | 5.5 | 145 | 140
ASME 16.5 | 1500 | 2.5 | 9.62 | 7.5 | 1.125 | 8 | 1 |  |  | 1.62 | N/A | 4.88 | 2.88 | 2.5 | 2.5 | 4.12 | 1.88 | 2.94 | 2.97 | (4) | 0.31 | 0.75 | 244 | 190.5 |  |  | 41.1 | N/A | 124 | 73.2 | 64 | 64 | 105 | 48 | 74.7 | 75.4 | (4) | 8 | 19 | 3 | 76.2 | 6.25 | 6 | 160 | 150
ASME 16.5 | 1500 | 3 | 10.5 | 8 | 1.125 | 8 | 1.125 |  |  | 1.88 | N/A | 5.25 | 3.5 | … | 2.88 | 4.62 | … | … | 3.6 | (4) | 0.38 | … | 267 | 203.2 |  |  | 47.8 | N/A | 133 | 88.9 | … | 73 | 117 | … | … | 91.4 | (4) | 10 | … | … | … | 7 | 6.75 | 180 | 170
ASME 16.5 | 1500 | 4 | 12.25 | 9.5 | 1.375 | 8 | 1.25 |  |  | 2.12 | N/A | 6.38 | 4.5 | … | 3.56 | 4.88 | … | … | 4.6 | (4) | 0.44 | … | 311 | 241.3 |  |  | 53.8 | N/A | 162 | 114.3 | … | 90 | 124 | … | … | 116.8 | (4) | 11 | … | … | … | 7.75 | 7.5 | 195 | 190
ASME 16.5 | 1500 | 5 | 14.75 | 11.5 | 1.625 | 8 | 1.5 |  |  | 2.88 | N/A | 7.75 | 5.56 | … | 4.12 | 6.12 | … | … | 5.69 | (4) | 0.44 | … | 375 | 292.1 |  |  | 73.2 | N/A | 197 | 141.2 | … | 105 | 155 | … | … | 144.5 | (4) | 11 | … | … | … | 9.75 | 9.5 | 250 | 240
ASME 16.5 | 1500 | 6 | 15.5 | 12.5 | 1.5 | 12 | 1.375 |  |  | 3.25 | N/A | 9 | 6.63 | … | 4.69 | 6.75 | … | … | 6.75 | (4) | 0.5 | … | 394 | 317.5 |  |  | 82.6 | N/A | 229 | 168.4 | … | 119 | 171 | … | … | 171.4 | (4) | 13 | … | … | … | 10.25 | 10 | 260 | 255
ASME 16.5 | 1500 | 8 | 19 | 15.5 | 1.75 | 12 | 1.625 |  |  | 3.62 | N/A | 11.5 | 8.63 | … | 5.62 | 8.38 | … | … | 8.75 | (4) | 0.5 | … | 483 | 393.7 |  |  | 91.9 | N/A | 292 | 219.2 | … | 143 | 213 | … | … | 222.2 | (4) | 13 | … | … | … | 11.5 | 11.25 | 290 | 285
ASME 16.5 | 1500 | 10 | 23 | 19 | 2 | 12 | 1.875 |  |  | 4.25 | N/A | 14.5 | 10.75 | … | 7 | 10 | … | … | 10.92 | (4) | 0.5 | … | 584 | 482.6 |  |  | 108 | N/A | 368 | 273 | … | 178 | 254 | … | … | 277.4 | (4) | 13 | … | … | … | 13.25 | 13 | 335 | 330
ASME 16.5 | 1500 | 12 | 26.5 | 22.5 | 2.125 | 16 | 2 |  |  | 4.88 | N/A | 17.75 | 12.75 | … | 8.62 | 11.12 | … | … | 12.92 | (4) | 0.5 | … | 673 | 571.5 |  |  | 124 | N/A | 451 | 323.8 | … | 219 | 282 | … | … | 328.2 | (4) | 13 | … | … | … | 14.75 | 14.5 | 375 | 370
ASME 16.5 | 1500 | 14 | 29.5 | 25 | 2.375 | 16 | 2.25 |  |  | 5.25 | N/A | 19.5 | 14 | … | 9.5 | 11.75 | … | … | 14.18 | (4) | 0.5 | … | 749 | 635 |  |  | 133.4 | N/A | 495 | 355.6 | … | 241 | 298 | … | … | 360.2 | (4) | 13 | … | … | … | 16 | 15.75 | 405 | 400
ASME 16.5 | 1500 | 16 | 32.5 | 27.75 | 2.625 | 16 | 2.5 |  |  | 5.75 | N/A | 21.75 | 16 | … | 10.25 | 12.25 | … | … | 16.19 | (4) | 0.5 | … | 826 | 704.8 |  |  | 146 | N/A | 552 | 406.4 | … | 260 | 311 | … | … | 411.2 | (4) | 13 | … | … | … | 17.5 | 17.25 | 445 | 440
ASME 16.5 | 1500 | 18 | 36 | 30.5 | 2.875 | 16 | 2.75 |  |  | 6.38 | N/A | 23.5 | 18 | … | 10.88 | 12.88 | … | … | 18.2 | (4) | 0.5 | … | 914 | 774.7 |  |  | 162.1 | N/A | 597 | 457.2 | … | 276 | 327 | … | … | 462.3 | (4) | 13 | … | … | … | 19.5 | 19.25 | 495 | 490
ASME 16.5 | 1500 | 20 | 38.75 | 32.75 | 3.125 | 16 | 3 |  |  | 7 | N/A | 25.25 | 20 | … | 11.5 | 14 | … | … | 20.25 | (4) | 0.5 | … | 984 | 831.8 |  |  | 177.8 | N/A | 641 | 508 | … | 292 | 356 | … | … | 514.4 | (4) | 13 | … | … | … | 21.25 | 21 | 540 | 535
ASME 16.5 | 1500 | 24 | 46 | 39 | 3.625 | 16 | 3 |  |  | 8 | N/A | 30 | 24 | … | 13 | 16 | … | … | 24.25 | (4) | 0.5 | … | 1168 | 990.6 |  |  | 203.2 | N/A | 762 | 609.6 | … | 330 | 406 | … | … | 616 | (4) | 13 | … | … | … | 24.25 | 24 | 615 | 610
ASME 16.5 | 2500 | 0.5 | 5.25 | 3.5 | 0.875 | 4 | 0.75 |  |  | 1.19 | N/A | 1.69 | 0.84 | 1.56 | 1.56 | 2.88 | 1.12 | N/A | 0.9 | (4) | 0.12 | N/A | 133 | 88.9 |  |  | 30.2 | N/A | 43 | 21.3 | 40 | 40 | 73 | 28 | N/A | 22.9 | (4) | 3 | N/A | 0.93 | 23.6 | 4.75 | 4.5 | 120 | 115
ASME 16.5 | 2500 | 0.75 | 5.5 | 3.75 | 0.875 | 4 | 0.75 |  |  | 1.25 | N/A | 2 | 1.05 | 1.69 | 1.69 | 3.12 | 1.25 | N/A | 1.11 | (4) | 0.12 | N/A | 140 | 95.2 |  |  | 31.8 | N/A | 51 | 26.7 | 43 | 43 | 79 | 32 | N/A | 28.2 | (4) | 3 | N/A | 1.14 | 29 | 5 | 4.75 | 125 | 120
ASME 16.5 | 2500 | 1 | 6.25 | 4.25 | 1 | 4 | 0.875 |  |  | 1.38 | N/A | 2.25 | 1.32 | 1.88 | 1.88 | 3.5 | 1.38 | N/A | 1.38 | (4) | 0.12 | N/A | 159 | 108 |  |  | 35.1 | N/A | 57 | 33.5 | 52 | 48 | 89 | 35 | N/A | 35.1 | (4) | 3 | N/A | 1.41 | 35.8 | 5.5 | 5.25 | 140 | 135
ASME 16.5 | 2500 | 1.25 | 7.25 | 5.12 | 1.125 | 4 | 1 |  |  | 1.5 | N/A | 2.88 | 1.66 | 2.06 | 2.06 | 3.75 | 1.5 | N/A | 1.72 | (4) | 0.19 | N/A | 184 | 130 |  |  | 38.1 | N/A | 73 | 42.2 | 60 | 52 | 95 | 38 | N/A | 43.7 | (4) | 5 | N/A | 1.75 | 44.4 | 6 | 5.75 | 150 | 145
ASME 16.5 | 2500 | 1.5 | 8 | 5.75 | 1.25 | 4 | 1.125 |  |  | 1.75 | N/A | 3.12 | 1.9 | 2.38 | 2.38 | 4.38 | 1.75 | N/A | 1.97 | (4) | 0.25 | N/A | 203 | 146 |  |  | 44.4 | N/A | 79 | 48.3 | 70 | 60 | 111 | 44 | N/A | 50 | (4) | 6 | N/A | 1.99 | 50.5 | 6.75 | 6.5 | 170 | 165
ASME 16.5 | 2500 | 2 | 9.25 | 6.75 | 1.125 | 8 | 1 |  |  | 2 | N/A | 3.75 | 2.38 | 2.75 | 2.75 | 5 | 2 | N/A | 2.46 | (4) | 0.31 | N/A | 235 | 171.4 |  |  | 50.8 | N/A | 95 | 60.5 | 79 | 70 | 127 | 51 | N/A | 62.5 | (4) | 8 | N/A | 2.5 | 63.5 | 7 | 6.75 | 180 | 170
ASME 16.5 | 2500 | 2.5 | 10.5 | 7.75 | 1.25 | 8 | 1.125 |  |  | 2.25 | N/A | 4.5 | 2.88 | 3.12 | 3.12 | 5.62 | 2.25 | N/A | 2.97 | (4) | 0.31 | N/A | 267 | 196.8 |  |  | 57.2 | N/A | 114 | 73.2 | … | 79 | 143 | 57 | N/A | 75.4 | (4) | 8 | N/A | 3 | 76.2 | 7.75 | 7.5 | 195 | 190
ASME 16.5 | 2500 | 3 | 12 | 9 | 1.375 | 8 | 1.25 |  |  | 2.62 | N/A | 5.25 | 3.5 | … | 3.62 | 6.62 | … | N/A | 3.6 | (4) | 0.38 | N/A | 305 | 228.6 |  |  | 66.5 | N/A | 133 | 88.9 | … | 92 | 168 | … | N/A | 91.4 | (4) | 10 | N/A | … | … | 8.75 | 8.5 | 220 | 215
ASME 16.5 | 2500 | 4 | 14 | 10.75 | 1.625 | 8 | 1.5 |  |  | 3 | N/A | 6.5 | 4.5 | … | 4.25 | 7.5 | … | N/A | 4.6 | (4) | 0.44 | N/A | 356 | 273 |  |  | 76.2 | N/A | 165 | 114.3 | … | 108 | 190 | … | N/A | 116.8 | (4) | 11 | N/A | … | … | 10 | 9.75 | 255 | 250
ASME 16.5 | 2500 | 5 | 16.5 | 12.75 | 1.875 | 8 | 1.75 |  |  | 3.62 | N/A | 8 | 5.56 | … | 5.12 | 9 | … | N/A | 5.69 | (4) | 0.44 | N/A | 419 | 323.8 |  |  | 91.9 | N/A | 203 | 141.2 | … | 130 | 229 | … | N/A | 144.5 | (4) | 11 | N/A | … | … | 11.75 | 11.5 | 300 | 290
ASME 16.5 | 2500 | 6 | 19 | 14.5 | 2.125 | 8 | 2 |  |  | 4.25 | N/A | 9.25 | 6.63 | … | 6 | 10.75 | … | N/A | 6.75 | (4) | 0.5 | N/A | 483 | 368.3 |  |  | 108 | N/A | 235 | 168.4 | … | 152 | 273 | … | N/A | 171.4 | (4) | 13 | N/A | … | … | 13.5 | 13.25 | 345 | 335
ASME 16.5 | 2500 | 8 | 21.75 | 17.25 | 2.125 | 12 | 2 |  |  | 5 | N/A | 12 | 8.63 | … | 7 | 12.5 | … | N/A | 8.75 | (4) | 0.5 | N/A | 552 | 438.2 |  |  | 127 | N/A | 605 | 219.2 | … | 178 | 318 | … | N/A | 222.2 | (4) | 13 | N/A | … | … | 15 | 14.75 | 380 | 375
ASME 16.5 | 2500 | 10 | 26.5 | 21.25 | 2.625 | 12 | 2.5 |  |  | 6.5 | N/A | 14.75 | 10.75 | … | 9 | 16.5 | … | N/A | 10.92 | (4) | 0.5 | N/A | 673 | 539.8 |  |  | 165.1 | N/A | 375 | 273 | … | 229 | 419 | … | N/A | 277.4 | (4) | 13 | N/A | … | … | 19.25 | 19 | 490 | 485
ASME 16.5 | 2500 | 12 | 30 | 24.38 | 2.875 | 12 | 2.75 |  |  | 7.25 | N/A | 17.38 | 12.75 | … | 10 | 18.25 | … | N/A | 12.92 | (4) | 0.5 | N/A | 762 | 619.3 |  |  | 184.2 | N/A | 441 | 323.8 | … | 2543 | 464 | … | N/A | 328.2 | (4) | 13 | N/A | … | … | 21.25 | 21 | 540 | 535
ASME 16.47 Series A | 400 | 26 | 38.25 | 34.5 | 1.875 | 28 | 1.75 |  |  |  |  | 28.62 | [10 empty] | 972 | 876.3 |  |  |  |  | 727 | [16 empty] | 12 | 26 | 29.5 | 3.5 | 3.88 | 7.62 | 0.44 | 310 | 660.4 | 749 | 88.9 | 98.6 | 194 | 11
ASME 16.47 Series A | 400 | 28 | 40.75 | 37 | 2 | 28 | 1.875 |  |  |  |  | 30.81 | [10 empty] | 1035 | 939.8 |  |  |  |  | 783 | [16 empty] | 13 | 28 | 31.5 | 3.75 | 4.12 | 8.12 | 0.5 | 330 | 711.2 | 800 | 95.2 | 104.6 | 206 | 13
ASME 16.47 Series A | 400 | 30 | 43 | 39.25 | 2.125 | 28 | 2 |  |  |  |  | 32.94 | [10 empty] | 1092 | 997 |  |  |  |  | 837 | [16 empty] | 13.5 | 30 | 33.75 | 4 | 4.38 | 8.62 | 0.5 | 345 | 762 | 857 | 101.6 | 111.3 | 219 | 13
ASME 16.47 Series A | 400 | 32 | 45.25 | 41.5 | 2.125 | 28 | 2 |  |  |  |  | 35 | [10 empty] | 1149 | 1054.1 |  |  |  |  | 339 | [16 empty] | 14 | 32 | 36 | 4.25 | 4.56 | 9.12 | 0.5 | 360 | 812.8 | 914 | 108 | 115.8 | 232 | 13
ASME 16.47 Series A | 400 | 34 | 47.5 | 43.5 | 2.125 | 28 | 2 |  |  |  |  | 37.19 | [10 empty] | 1206 | 1104.9 |  |  |  |  | 945 | [16 empty] | 14.5 | 34 | 38 | 4.38 | 4.81 | 9.5 | 0.56 | 365 | 863.6 | 965 | 111.3 | 122.2 | 241 | 14
ASME 16.47 Series A | 400 | 36 | 50 | 46 | 2.125 | 32 | 2 |  |  |  |  | 39.38 | [10 empty] | 1270 | 1168.4 |  |  |  |  | 1000 | [16 empty] | 14.5 | 36 | 40.25 | 4.5 | 5.06 | 9.88 | 0.56 | 375 | 914.4 | 1022 | 114.3 | 128.5 | 251 | 14
ASME 16.47 Series A | 400 | 38 | 47.5 | 44 | 1.875 | 32 | 1.75 |  |  |  |  | 39.5 | [10 empty] | 1206 | 1117.6 |  |  |  |  | 1003 | [16 empty] | 15 | 38 | 40.75 | 4.88 | 4.88 | 8.12 | 0.56 | 380 | 965.2 | 1035 | 124 | 124 | 206 | 14
ASME 16.47 Series A | 400 | 40 | 50 | 46.25 | 2 | 32 | 1.875 |  |  |  |  | 41.5 | [10 empty] | 1270 | 1174.8 |  |  |  |  | 1054 | [16 empty] | 15.5 | 40 | 43 | 5.12 | 5.12 | 8.5 | 0.56 | 405 | 1016 | 1092 | 130 | 130 | 216 | 14
ASME 16.47 Series A | 400 | 42 | 52 | 48.25 | 2 | 32 | 1.875 |  |  |  |  | 43.62 | [10 empty] | 1321 | 1225.6 |  |  |  |  | 1108 | [16 empty] | 16 | 42 | 45 | 5.25 | 5.25 | 8.81 | 0.56 | 405 | 1066.8 | 1143 | 133.4 | 133.4 | 224 | 14
ASME 16.47 Series A | 400 | 44 | 54.5 | 50.5 | 2.125 | 32 | 2 |  |  |  |  | 45.62 | [10 empty] | 1384 | 1282.7 |  |  |  |  | 1159 | [16 empty] | 16.5 | 44 | 47.25 | 5.5 | 5.5 | 9.18 | 0.56 | 425 | 1117.6 | 1200 | 139.7 | 139.7 | 233 | 14
ASME 16.47 Series A | 400 | 46 | 56.75 | 52.75 | 2.125 | 36 | 2 |  |  |  |  | 47.75 | [10 empty] | 1441 | 1339.8 |  |  |  |  | 1213 | [16 empty] | 17 | 46 | 49.5 | 5.75 | 5.75 | 9.62 | 0.56 | 435 | 1168.4 | 1257 | 146 | 146 | 244 | 14
ASME 16.47 Series A | 400 | 48 | 59.5 | 55.25 | 2.375 | 28 | 2.25 |  |  |  |  | 49.88 | [10 empty] | 1511 | 1403.4 |  |  |  |  | 1267 | [16 empty] | 18 | 48 | 51.5 | 6 | 6 | 10.12 | 0.56 | 460 | 1219.2 | 1308 | 152.4 | 152.4 | 257 | 14
ASME 16.47 Series A | 400 | 50 | 61.75 | 57.5 | 2.375 | 32 | 2.25 |  |  |  |  | 52 | [10 empty] | 1568 | 1460.5 |  |  |  |  | 1321 | [16 empty] | 18.5 | 50 | 53.62 | 6.19 | 6.25 | 10.56 | 0.56 | 470 | 1270 | 1362 | 157.2 | 158.8 | 268 | 14
ASME 16.47 Series A | 400 | 52 | 63.75 | 59.5 | 2.375 | 32 | 2.25 |  |  |  |  | 54 | [10 empty] | 1619 | 1511.3 |  |  |  |  | 1372 | [16 empty] | 19 | 52 | 55.62 | 6.38 | 6.44 | 10.88 | 0.56 | 480 | 1320.8 | 1413 | 162.1 | 163.6 | 276 | 14
ASME 16.47 Series A | 400 | 54 | 67 | 62.25 | 2.625 | 28 | 2.5 |  |  |  |  | 56.12 | [10 empty] | 1702 | 1581.2 |  |  |  |  | 1425 | [16 empty] | 20 | 54 | 57.88 | 6.69 | 6.75 | 11.38 | 0.56 | 510 | 1371.6 | 1470 | 169.9 | 171.4 | 289 | 14
ASME 16.47 Series A | 400 | 56 | 69 | 64.25 | 2.625 | 32 | 2.5 |  |  |  |  | 58.25 | [10 empty] | 1753 | 1632 |  |  |  |  | 1480 | [16 empty] | 20.5 | 56 | 60.12 | 6.88 | 6.94 | 11.75 | 0.56 | 520 | 1422.4 | 1527 | 174.8 | 176.3 | 298 | 14
ASME 16.47 Series A | 400 | 58 | 71 | 66.25 | 2.625 | 32 | 2.5 |  |  |  |  | 60.25 | [10 empty] | 1803 | 1682.8 |  |  |  |  | 1530 | [16 empty] | 20.75 | 58 | 62.12 | 7 | 7.12 | 12.06 | 0.56 | 530 | 1473.2 | 1578 | 177.8 | 180.8 | 306 | 14
ASME 16.47 Series A | 400 | 60 | 74.25 | 69 | 2.875 | 32 | 2.75 |  |  |  |  | 62.38 | [10 empty] | 1886 | 1752.6 |  |  |  |  | 1584 | [16 empty] | 21.75 | 60 | 64.38 | 7.31 | 7.44 | 12.56 | 0.56 | 560 | 1524 | 1635 | 185.7 | 189 | 319 | 14
ASME 16.47 Series A | 600 | 26 | 40 | 36 | 2 | 28 | 1.875 |  |  |  |  | 29.44 | [10 empty] | 1016 | 914.4 |  |  |  |  | 748 | [16 empty] | 14 | 26 | 29.5 | 4.25 | 4.94 | 8.75 | 0.5 | 355 | 660.4 | 749 | 108 | 125.5 | 222 | 13
ASME 16.47 Series A | 600 | 28 | 42.25 | 38 | 2.125 | 28 | 2 |  |  |  |  | 31.62 | [10 empty] | 1073 | 965.2 |  |  |  |  | 803 | [16 empty] | 14.5 | 28 | 31.5 | 4.38 | 5.19 | 9.25 | 0.5 | 365 | 711.2 | 800 | 111.3 | 131.8 | 235 | 13
ASME 16.47 Series A | 600 | 30 | 44.5 | 40.25 | 2.375 | 28 | 2 |  |  |  |  | 33.94 | [10 empty] | 1130 | 1022.4 |  |  |  |  | 862 | [16 empty] | 14.5 | 30 | 33.75 | 4.5 | 5.5 | 9.75 | 0.5 | 375 | 762 | 857 | 114.3 | 139.7 | 248 | 13
ASME 16.47 Series A | 600 | 32 | 47 | 42.5 | 2.375 | 28 | 2.25 |  |  |  |  | 36.12 | [10 empty] | 1194 | 1079.5 |  |  |  |  | 917 | [16 empty] | 15.25 | 32 | 36 | 4.62 | 5.81 | 10.25 | 0.56 | 390 | 812.8 | 914 | 117.3 | 147.6 | 260 | 13
ASME 16.47 Series A | 600 | 34 | 49 | 44.5 | 2.625 | 28 | 2.25 |  |  |  |  | 38.31 | [10 empty] | 1245 | 1130.3 |  |  |  |  | 973 | [16 empty] | 15.5 | 34 | 38 | 4.75 | 6.06 | 10.62 | 0.56 | 400 | 863.6 | 965 | 120.6 | 153.9 | 270 | 14
ASME 16.47 Series A | 600 | 36 | 51.75 | 47 | 2.375 | 28 | 2.5 |  |  |  |  | 40.62 | [10 empty] | 1314 | 1193.8 |  |  |  |  | 1032 | [16 empty] | 16.5 | 36 | 40.25 | 4.88 | 6.38 | 11.12 | 0.56 | 415 | 914.4 | 1022 | 124 | 162.1 | 282 | 14
ASME 16.47 Series A | 600 | 38 | 50 | 45.75 | 2.375 | 28 | 2.25 |  |  |  |  | 40.25 | [10 empty] | 1270 | 1162 |  |  |  |  | 1022 | [16 empty] | 18.25 | 38 | 41.5 | 6 | 6.12 | 10 | 0.56 | 465 | 965.2 | 1054 | 152.4 | 155.4 | 254 | 14
ASME 16.47 Series A | 600 | 40 | 52 | 47.75 | 2.625 | 32 | 2.25 |  |  |  |  | 42.25 | [10 empty] | 1321 | 1212.8 |  |  |  |  | 1073 | [16 empty] | 18.75 | 40 | 43.75 | 6.25 | 6.38 | 10.38 | 0.56 | 480 | 1016 | 1111 | 158.8 | 162.1 | 264 | 14
ASME 16.47 Series A | 600 | 42 | 55.25 | 50.5 | 2.625 | 28 | 2.5 |  |  |  |  | 44.38 | [10 empty] | 1403 | 1282.7 |  |  |  |  | 1127 | [16 empty] | 20 | 42 | 46 | 6.62 | 6.75 | 11 | 0.56 | 510 | 1066.8 | 1168 | 168.1 | 171.4 | 279 | 14
ASME 16.47 Series A | 600 | 44 | 57.25 | 52.5 | 2.625 | 32 | 2.5 |  |  |  |  | 46.5 | [10 empty] | 1454 | 1333.5 |  |  |  |  | 1181 | [16 empty] | 20.25 | 44 | 48.25 | 6.81 | 7 | 11.38 | 0.56 | 520 | 1117.6 | 1226 | 173 | 177.8 | 289 | 14
ASME 16.47 Series A | 600 | 46 | 59.5 | 54.75 | 2.875 | 32 | 2.5 |  |  |  |  | 48.62 | [10 empty] | 1511 | 1390.6 |  |  |  |  | 1235 | [16 empty] | 20.75 | 46 | 50.25 | 7.06 | 7.31 | 11.81 | 0.56 | 530 | 1168.4 | 1276 | 179.3 | 185.7 | 300 | 14
ASME 16.47 Series A | 600 | 48 | 62.75 | 57.5 | 3.125 | 32 | 2.75 |  |  |  |  | 50.75 | [10 empty] | 15.94 | 1460.5 |  |  |  |  | 1289 | [16 empty] | 22 | 48 | 52.5 | 7.44 | 7.69 | 12.44 | 0.56 | 565 | 1219.2 | 1334 | 189 | 195.3 | 316 | 14
ASME 16.47 Series A | 600 | 50 | 65.75 | 60 | 3.125 | 28 | 3 |  |  |  |  | 52.88 | [10 empty] | 1670 | 1524 |  |  |  |  | 1343 | [16 empty] | 23.25 | 50 | 54.5 | 7.75 | 8 | 12.94 | 0.56 | 595 | 1270 | 1384 | 196.8 | 203.2 | 329 | 14
ASME 16.47 Series A | 600 | 52 | 67.75 | 62 | 3.125 | 32 | 3 |  |  |  |  | 54.88 | [10 empty] | 1721 | 1574.8 |  |  |  |  | 1394 | [16 empty] | 23.75 | 52 | 56.5 | 8 | 8.25 | 13.25 | 0.56 | 605 | 1320.8 | 1435 | 203.2 | 209.6 | 337 | 14
ASME 16.47 Series A | 600 | 54 | 70 | 64.25 | 3.125 | 32 | 3 |  |  |  |  | 57 | [10 empty] | 1778 | 1632 |  |  |  |  | 1448 | [16 empty] | 2425 | 54 | 58.75 | 8.25 | 8.56 | 13.75 | 0.56 | 620 | 1371.6 | 1492 | 209.6 | 217.4 | 349 | 14
ASME 16.47 Series A | 600 | 56 | 73 | 66.75 | 3.375 | 32 | 3.25 |  |  |  |  | 59.12 | [10 empty] | 1854 | 1695.4 |  |  |  |  | 1502 | [16 empty] | 25.5 | 56 | 60.75 | 8.56 | 8.88 | 14.25 | 0.62 | 645 | 1422.4 | 1543 | 217.4 | 225.6 | 362 | 16
ASME 16.47 Series A | 600 | 58 | 75 | 68.75 | 3.375 | 32 | 3.25 |  |  |  |  | 61.12 | [10 empty] | 1905 | 1746.2 |  |  |  |  | 1553 | [16 empty] | 25.75 | 58 | 63 | 8.75 | 9.12 | 14.53 | 0.62 | 655 | 1473.2 | 1600 | 222.2 | 231.6 | 370 | 16
ASME 16.47 Series A | 600 | 60 | 78.5 | 71.75 | 3.625 | 28 | 3.5 |  |  |  |  | 63.38 | [10 empty] | 1994 | 1822.4 |  |  |  |  | 1610 | [16 empty] | 27.25 | 60 | 65.25 | 9.19 | 9.56 | 15.31 | 0.69 | 690 | 1524 | 1657 | 233.4 | 242.8 | 389 | 17
ASME 16.47 Series A | 900 | 26 | 42.75 | 37.5 | 2.875 | 20 | 2.75 |  |  |  |  | 30.5 | [10 empty] | 1086 | 952.5 |  |  |  |  | 775 | [16 empty] | 18.25 | 26 | 29.5 | 5.5 | 6.31 | 11.25 | 0.44 | 465 | 660.4 | 749 | 139.7 | 160.3 | 286 | 11
ASME 16.47 Series A | 900 | 28 | 46 | 40.25 | 3.125 | 20 | 3 |  |  |  |  | 32.75 | [10 empty] | 1168 | 1022.4 |  |  |  |  | 832 | [16 empty] | 19 | 28 | 31.5 | 5.62 | 6.753 | 11.75 | 0.5 | 485 | 711.2 | 800 | 142.7 | 171.4 | 298 | 13
ASME 16.47 Series A | 900 | 30 | 48.5 | 42.75 | 3.125 | 20 | 3 |  |  |  |  | 35 | [10 empty] | 1232 | 1085.8 |  |  |  |  | 889 | [16 empty] | 19.5 | 30 | 33.75 | 5.88 | 7.18 | 12.25 | 0.5 | 495 | 762 | 857 | 129.4 | 182.4 | 311 | 13
ASME 16.47 Series A | 900 | 32 | 51.75 | 45.5 | 3.375 | 20 | 3.25 |  |  |  |  | 37.25 | [10 empty] | 1314 | 1155.7 |  |  |  |  | 946 | [16 empty] | 20.75 | 32 | 36 | 6.25 | 7.62 | 13 | 0.5 | 530 | 812.8 | 914 | 158.8 | 193.5 | 330 | 13
ASME 16.47 Series A | 900 | 34 | 55 | 48.25 | 3.625 | 20 | 3.5 |  |  |  |  | 39.62 | [10 empty] | 1397 | 1225.6 |  |  |  |  | 1006 | [16 empty] | 21.75 | 34 | 38 | 6.5 | 8.06 | 13.75 | 0.56 | 555 | 863.6 | 965 | 165.1 | 204.7 | 349 | 14
ASME 16.47 Series A | 900 | 36 | 57.5 | 50.75 | 3.625 | 20 | 3.5 |  |  |  |  | 41.88 | [10 empty] | 1460 | 1289 |  |  |  |  | 1064 | [16 empty] | 22.25 | 36 | 40.25 | 6.75 | 8.44 | 14.25 | 0.56 | 565 | 914.4 | 1022 | 171.4 | 214.4 | 362 | 14
ASME 16.47 Series A | 900 | 38 | 57.5 | 50.75 | 3.625 | 20 | 3.5 |  |  |  |  | 42.25 | [10 empty] | 1460 | 1289 |  |  |  |  | 1073 | [16 empty] | 23.75 | 38 | 43.25 | 7.5 | 8.5 | 13.88 | 0.75 | 605 | 965.2 | 1099 | 190.5 | 215.9 | 353 | 19
ASME 16.47 Series A | 900 | 40 | 59.5 | 52.75 | 3.625 | 24 | 3.5 |  |  |  |  | 44.38 | [10 empty] | 1511 | 1339.8 |  |  |  |  | 1127 | [16 empty] | 24.5 | 40 | 45.75 | 7.75 | 8.81 | 14.31 | 0.81 | 620 | 1016 | 1162 | 196.8 | 223.8 | 363 | 21
ASME 16.47 Series A | 900 | 42 | 61.5 | 54.75 | 3.625 | 24 | 3.5 |  |  |  |  | 46.31 | [10 empty] | 1562 | 1390.6 |  |  |  |  | 1176 | [16 empty] | 25 | 42 | 47.75 | 8.12 | 9.12 | 14.62 | 0.81 | 635 | 1066.8 | 1213 | 206.2 | 231.6 | 371 | 21
ASME 16.47 Series A | 900 | 44 | 64.88 | 57.75 | 3.875 | 24 | 3.75 |  |  |  |  | 48.62 | [10 empty] | 1648 | 1463.5 |  |  |  |  | 1235 | [16 empty] | 26 | 44 | 50 | 8.44 | 9.56 | 15.38 | 0.88 | 665 | 1117.6 | 1270 | 214.4 | 242.8 | 391 | 22
ASME 16.47 Series A | 900 | 46 | 68.25 | 60.5 | 4.125 | 24 | 4 |  |  |  |  | 50.88 | [10 empty] | 1734 | 1536.7 |  |  |  |  | 1292 | [16 empty] | 27.5 | 46 | 52.5 | 8.88 | 10.06 | 16.18 | 0.88 | 7000 | 1168.4 | 1334 | 225.6 | 255.5 | 411 | 22
ASME 16.47 Series A | 900 | 48 | 70.25 | 62.5 | 4.125 | 24 | 4 |  |  |  |  | 52.88 | [10 empty] | 1784 | 1587.5 |  |  |  |  | 1343 | [16 empty] | 28 | 48 | 54.5 | 9.19 | 10.38 | 16.5 | 0.94 | 715 | 1219.2 | 1384 | 233.4 | 263.7 | 419 | 24
ASME 16.47 Series B | 400 | 26 | 33.5 | 30.75 | 1.5 | 28 | 1.375 |  |  |  |  | 27.12 | [10 empty] | 851 | 781 |  |  |  |  | 689 | [16 empty] | 14.25 | 26 | 28 | 3.5 | 3.5 | 5.88 | 0.44 | 290 | 660.4 | 711 | 88.9 | 88.9 | 149 | 11
ASME 16.47 Series B | 400 | 28 | 36 | 33 | 1.625 | 24 | 1.5 |  |  |  |  | 29.12 | [10 empty] | 914 | 838.2 |  |  |  |  | 740 | [16 empty] | 14.75 | 28 | 30 | 3.75 | 3.75 | 6.25 | 0.5 | 310 | 711.2 | 762 | 95.2 | 95.2 | 159 | 13
ASME 16.47 Series B | 400 | 30 | 38.25 | 35.25 | 1.625 | 28 | 1.5 |  |  |  |  | 31.25 | [10 empty] | 972 | 895.4 |  |  |  |  | 794 | [16 empty] | 15.5 | 30 | 32.25 | 4 | 4 | 6.69 | 0.5 | 320 | 768 | 819 | 101.6 | 101.6 | 170 | 13
ASME 16.47 Series B | 400 | 32 | 40.75 | 37.25 | 1.75 | 28 | 1.625 |  |  |  |  | 33.25 | [10 empty] | 1035 | 952.5 |  |  |  |  | 845 | [16 empty] | 16.25 | 32 | 34.38 | 4.25 | 4.25 | 7.06 | 0.5 | 345 | 812.8 | 873 | 108 | 108 | 179 | 13
ASME 16.47 Series B | 400 | 34 | 42.75 | 39.5 | 1.75 | 32 | 1.625 |  |  |  |  | 35.38 | [10 empty] | 1086 | 1003.3 |  |  |  |  | 899 | [16 empty] | 17.25 | 34 | 36.5 | 4.38 | 4.38 | 7.38 | 0.56 | 345 | 863.6 | 927 | 111.3 | 111.3 | 187 | 14
ASME 16.47 Series B | 400 | 36 | 45.5 | 42 | 1.875 | 28 | 1.75 |  |  |  |  | 37.5 | [10 empty] | 1156 | 1066.8 |  |  |  |  | 952 | [16 empty] | 18 | 36 | 38.62 | 4.69 | 4.69 | 7.88 | 0.56 | 370 | 914.4 | 981 | 119.1 | 119.1 | 200 | 14
ASME 16.47 Series B | 600 | 26 | 35 | 31.75 | 1.75 | 28 | 1.625 |  |  |  |  | 27.5 | [10 empty] | 889 | 806.4 |  |  |  |  | 698 | [16 empty] | 14.25 | 26 | 28.62 | 4.38 | 4.38 | 7.12 | 0.5 | 360 | 660.4 | 727 | 111.3 | 111.3 | 181 | 13
ASME 16.47 Series B | 600 | 28 | 37.5 | 34 | 1.875 | 28 | 1.75 |  |  |  |  | 29.62 | [10 empty] | 952 | 863.6 |  |  |  |  | 752 | [16 empty] | 14.75 | 28 | 30.88 | 4.56 | 4.56 | 7.5 | 0.5 | 375 | 711.2 | 784 | 115.8 | 115.8 | 190 | 13
ASME 16.47 Series B | 600 | 30 | 40.25 | 36.5 | 2 | 28 | 1.875 |  |  |  |  | 31.75 | [10 empty] | 1022 | 927.1 |  |  |  |  | 806 | [16 empty] | 15.5 | 30 | 33.12 | 4.94 | 5 | 8.06 | 0.5 | 395 | 762 | 841 | 125.5 | 127 | 205 | 13
ASME 16.47 Series B | 600 | 32 | 42.75 | 38.75 | 2.125 | 28 | 2 |  |  |  |  | 33.88 | [10 empty] | 1086 | 984.2 |  |  |  |  | 861 | [16 empty] | 16.25 | 32 | 35.25 | 5.12 | 5.31 | 8.5 | 0.5 | 415 | 812.8 | 895 | 130 | 134.9 | 216 | 13
ASME 16.47 Series B | 600 | 34 | 45.75 | 41.5 | 2.375 | 24 | 2.25 |  |  |  |  | 36 | [10 empty] | 1162 | 1054.1 |  |  |  |  | 914 | [16 empty] | 17.25 | 34 | 37.5 | 5.56 | 5.68 | 9.19 | 0.56 | 440 | 863.6 | 952 | 141.2 | 144.3 | 233 | 14
ASME 16.47 Series B | 600 | 36 | 47.75 | 43.5 | 2.375 | 28 | 2.25 |  |  |  |  | 38.12 | [10 empty] | 1213 | 1104.9 |  |  |  |  | 968 | [16 empty] | 18 | 36 | 39.75 | 5.75 | 5.94 | 9.56 | 0.56 | 460 | 914.4 | 1010 | 146 | 150.9 | 243 | 14
ASME 16.47 Series B | 900 | 26 | 40.25 | 35.5 | 2.625 | 20 | 2.5 |  |  |  |  | 29.25 | [10 empty] | 1022 | 901.7 |  |  |  |  | 743 | [16 empty] | 17.75 | 26 | 30 | 5.31 | 6.06 | 10.19 | 0.44 | 450 | 660.4 | 762 | 134.9 | 153.9 | 259 | 11
ASME 16.47 Series B | 900 | 28 | 43.5 | 38.25 | 2.875 | 20 | 2.75 |  |  |  |  | 31.38 | [10 empty] | 1105 | 971.6 |  |  |  |  | 797 | [16 empty] | 19.25 | 28 | 32.25 | 5.81 | 6.56 | 10.88 | 0.5 | 495 | 711.2 | 819 | 147.6 | 166.6 | 276 | 13
ASME 16.47 Series B | 900 | 30 | 46.5 | 40.75 | 3.125 | 20 | 3 |  |  |  |  | 33.5 | [10 empty] | 1181 | 1035 |  |  |  |  | 851 | [16 empty] | 20 | 30 | 34.5 | 6.12 | 6.93 | 11.38 | 0.5 | 510 | 762 | 876 | 155.4 | 176 | 289 | 13
ASME 16.47 Series B | 900 | 32 | 48.75 | 43 | 3.125 | 20 | 3 |  |  |  |  | 35.75 | [10 empty] | 1238 | 1092.2 |  |  |  |  | 908 | [16 empty] | 20.75 | 32 | 36.5 | 6.31 | 7.31 | 11.94 | 0.5 | 530 | 812.8 | 927 | 160.3 | 185.7 | 303 | 13
ASME 16.47 Series B | 900 | 34 | 51.75 | 45.5 | 3.375 | 20 | 3.25 |  |  |  |  | 37.88 | [10 empty] | 1314 | 1155.7 |  |  |  |  | 962 | [16 empty] | 22.25 | 34 | 39 | 6.75 | 7.68 | 12.56 | 0.56 | 565 | 863.6 | 991 | 171.4 | 195 | 319 | 14
ASME 16.47 Series B | 900 | 36 | 53 | 47.25 | 3.125 | 24 | 3 |  |  |  |  | 40 | [10 empty] | 1346 | 1200.2 |  |  |  |  | 1016 | [16 empty] | 22.5 | 36 | 40.5 | 6.81 | 7.94 | 12.81 | 0.56 | 570 | 914.4 | 1029 | 173 | 201.7 | 325 | 14
ASME 16.47 Series A | 300 | 26 | 38.25 | 34.5 | 1.75 | 28 | 1.625 | 10.5 |  |  |  | 28.38 | [10 empty] | 972 | 876.3 | 270 |  |  |  | 721 | [17 empty] | 26 | 29.5 | 3.07 | 3.25 | 7.19 | 0.38 |  | 660.4 | 749 | 78 | 82.6 | 183 | 10
ASME 16.47 Series A | 300 | 28 | 40.75 | 37 | 1.75 | 28 | 1.625 | 11 |  |  |  | 30.5 | [10 empty] | 1035 | 939.8 | 280 |  |  |  | 775 | [17 empty] | 28 | 31.5 | 3.32 | 3.5 | 7.69 | 0.44 |  | 711.2 | 800 | 84.3 | 88.9 | 195 | 11
ASME 16.47 Series A | 300 | 30 | 43 | 39.25 | 1.875 | 28 | 1.75 | 11.75 |  |  |  | 32.56 | [10 empty] | 1092 | 997 | 300 |  |  |  | 827 | [17 empty] | 30 | 33.75 | 3.57 | 3.69 | 8.19 | 0.44 |  | 762 | 857 | 90.7 | 93.7 | 208 | 11
ASME 16.47 Series A | 300 | 32 | 45.25 | 41.5 | 2 | 28 | 1.875 | 12.75 |  |  |  | 34.69 | [10 empty] | 1149 | 1054.1 | 320 |  |  |  | 881 | [17 empty] | 32 | 36 | 3.82 | 3.88 | 8.69 | 0.44 |  | 812.8 | 914 | 97 | 98.6 | 221 | 11
ASME 16.47 Series A | 300 | 34 | 47.5 | 43.5 | 2 | 28 | 1.875 | 13 |  |  |  | 36.88 | [10 empty] | 1206 | 1104.9 | 330 |  |  |  | 937 | [17 empty] | 34 | 38 | 3.94 | 4.07 | 9.07 | 0.5 |  | 863.6 | 965 | 100.1 | 103.4 | 230 | 13
ASME 16.47 Series A | 300 | 36 | 50 | 46 | 2.125 | 32 | 2 | 13.5 |  |  |  | 39 | [10 empty] | 1270 | 1168.4 | 340 |  |  |  | 991 | [17 empty] | 36 | 40.25 | 4.07 | 4.32 | 9.44 | 0.5 |  | 914.4 | 1022 | 103.4 | 109.7 | 240 | 13
ASME 16.47 Series A | 300 | 38 | 46 | 43 | 1.625 | 32 | 1.5 | 12.5 |  |  |  | 39.12 | [10 empty] | 1168 | 1092.2 | 32 |  |  |  | 994 | [17 empty] | 38 | 40.5 | 4.19 | 4.19 | 7.06 | 0.5 |  | 965.2 | 1029 | 106.4 | 106.4 | 179 | 13
ASME 16.47 Series A | 300 | 40 | 48.75 | 45.5 | 1.75 | 32 | 1.625 | 13.25 |  |  |  | 41.25 | [10 empty] | 1238 | 1155.7 | 340 |  |  |  | 1048 | [17 empty] | 40 | 42.75 | 4.44 | 4.44 | 7.56 | 0.5 |  | 1016 | 1086 | 112.8 | 112.8 | 192 | 13
ASME 16.47 Series A | 300 | 42 | 50.75 | 47.5 | 1.75 | 32 | 1.625 | 13.75 |  |  |  | 43.25 | [10 empty] | 1289 | 1206.5 | 350 |  |  |  | 1099 | [17 empty] | 42 | 44.75 | 4.63 | 4.63 | 7.82 | 0.5 |  | 1066.8 | 1137 | 117.6 | 117.6 | 199 | 13
ASME 16.47 Series A | 300 | 44 | 53.25 | 49.75 | 1.875 | 32 | 1.75 | 14.5 |  |  |  | 45.25 | [10 empty] | 1353 | 1263.6 | 365 |  |  |  | 1149 | [17 empty] | 44 | 47 | 4.82 | 4.82 | 8.06 | 0.5 |  | 1117.6 | 1194 | 122.4 | 122.4 | 205 | 13
ASME 16.47 Series A | 300 | 46 | 55.75 | 52 | 2 | 28 | 1.875 | 15 |  |  |  | 47.38 | [10 empty] | 1416 | 1320.8 | 380 |  |  |  | 1203 | [17 empty] | 46 | 49 | 5 | 5 | 8.44 | 0.5 |  | 1168.4 | 1245 | 127 | 127 | 214 | 13
ASME 16.47 Series A | 300 | 48 | 57.75 | 54 | 2 | 32 | 1.875 | 15.5 |  |  |  | 49.38 | [10 empty] | 1467 | 1371.6 | 390 |  |  |  | 1254 | [17 empty] | 48 | 51.25 | 5.19 | 5.19 | 8.75 | 0.5 |  | 1219.2 | 1302 | 131.8 | 131.8 | 222 | 13
ASME 16.47 Series A | 300 | 50 | 60.25 | 56.25 | 2.125 | 32 | 2 | 16 |  |  |  | 51.38 | [10 empty] | 1530 | 1428.8 | 410 |  |  |  | 1305 | [17 empty] | 50 | 53.5 | 5.44 | 5.44 | 9.07 | 0.5 |  | 1270 | 1359 | 138.2 | 138.2 | 230 | 13
ASME 16.47 Series A | 300 | 52 | 62.25 | 58.25 | 2.125 | 32 | 2 | 16.5 |  |  |  | 53.38 | [10 empty] | 1581 | 1479.6 | 420 |  |  |  | 1356 | [17 empty] | 52 | 55.5 | 5.63 | 5.63 | 9.32 | 0.5 |  | 1320.8 | 1410 | 143 | 143 | 237 | 13
ASME 16.47 Series A | 300 | 54 | 65.25 | 61 | 2.375 | 28 | 2.25 | 17.5 |  |  |  | 55.5 | [10 empty] | 1657 | 1549.4 | 450 |  |  |  | 1410 | [17 empty] | 54 | 57.75 | 5.94 | 5.94 | 9.88 | 0.5 |  | 1371.6 | 1467 | 150.9 | 150.9 | 251 | 13
ASME 16.47 Series A | 300 | 56 | 67.25 | 63 | 2.375 | 28 | 2.25 | 17.75 |  |  |  | 57.62 | [10 empty] | 1708 | 1600.2 | 450 |  |  |  | 1464 | [17 empty] | 56 | 59.75 | 6 | 6 | 10.19 | 0.5 |  | 1422.4 | 1518 | 152.4 | 152.4 | 259 | 13
ASME 16.47 Series A | 300 | 58 | 69.25 | 65 | 2.375 | 32 | 2.25 | 18.25 |  |  |  | 59.62 | [10 empty] | 1759 | 1651 | 465 |  |  |  | 1514 | [17 empty] | 58 | 62 | 6.19 | 6.19 | 10.44 | 0.5 |  | 1473.2 | 1575 | 157.2 | 157.2 | 265 | 13
ASME 16.47 Series A | 300 | 60 | 71.25 | 67 | 2.375 | 32 | 1.25 | 18.75 |  |  |  | 61.62 | [10 empty] | 1810 | 1701.8 | 475 |  |  |  | 1565 | [17 empty] | 60 | 64 | 6.38 | 6.38 | 10.69 | 0.5 |  | 1524 | 1626 | 160.1 | 160.1 | 272 | 13
ASME 16.47 Series A | 150 | 26 | 34.25 | 31.75 | 1.375 | 24 | 1.25 | 8.75 |  |  |  | 26.62 | [10 empty] | 870 | 806.4 | 225 |  |  |  | 676 | [17 empty] | 26 | 29.5 | 2.63 | 2.63 | 4.69 | 0.38 |  | 660.4 | 749 | 66.8 | 66.8 | 119 | 10
ASME 16.47 Series A | 150 | 28 | 36.5 | 34 | 1.375 | 28 | 1.25 | 9 |  |  |  | 28.62 | [10 empty] | 927 | 863.6 | 230 |  |  |  | 727 | [17 empty] | 28 | 31.5 | 2.75 | 2.75 | 4.88 | 0.44 |  | 711.2 | 800 | 69.8 | 69.8 | 124 | 11
ASME 16.47 Series A | 150 | 30 | 38.75 | 36 | 1.375 | 28 | 1.25 | 9.25 |  |  |  | 30.75 | [10 empty] | 984 | 914.4 | 235 |  |  |  | 781 | [17 empty] | 30 | 33.75 | 2.88 | 2.88 | 5.32 | 0.44 |  | 762 | 857 | 73.2 | 73.2 | 135 | 11
ASME 16.47 Series A | 150 | 32 | 41.75 | 38.5 | 1.625 | 28 | 1.5 | 10.5 |  |  |  | 32.75 | [10 empty] | 1060 | 977.9 | 265 |  |  |  | 832 | [17 empty] | 32 | 36 | 3.13 | 3.13 | 5.63 | 0.44 |  | 812.8 | 914 | 79.5 | 79.5 | 143 | 11
ASME 16.47 Series A | 150 | 34 | 43.75 | 40.5 | 1.625 | 32 | 1.5 | 10.5 |  |  |  | 34.75 | [10 empty] | 1111 | 1028.7 | 270 |  |  |  | 883 | [17 empty] | 34 | 38 | 3.19 | 3.19 | 5.82 | 0.5 |  | 863.6 | 965 | 81 | 81 | 148 | 13
ASME 16.47 Series A | 150 | 36 | 46 | 42.75 | 1.625 | 32 | 1.5 | 11.25 |  |  |  | 36.75 | [10 empty] | 1168 | 1085.8 | 285 |  |  |  | 933 | [17 empty] | 36 | 40.25 | 3.5 | 3.5 | 6.13 | 0.5 |  | 914.4 | 1022 | 88.9 | 88.9 | 156 | 13
ASME 16.47 Series A | 150 | 38 | 48.75 | 45.25 | 1.625 | 32 | 1.5 | 11 |  |  |  | 39 | [10 empty] | 1238 | 1149.4 | 280 |  |  |  | 991 | [17 empty] | 38 | 42.25 | 3.38 | 3.38 | 6.13 | 0.5 |  | 965.2 | 1073 | 85.9 | 85.9 | 156 | 13
ASME 16.47 Series A | 150 | 40 | 50.75 | 47.25 | 1.625 | 36 | 1.5 | 11.25 |  |  |  | 41 | [10 empty] | 1289 | 1200.2 | 285 |  |  |  | 1041 | [17 empty] | 40 | 44.25 | 3.5 | 3.5 | 6.38 | 0.5 |  | 1016 | 1124 | 88.9 | 88.9 | 162 | 13
ASME 16.47 Series A | 150 | 42 | 53 | 49.5 | 1.625 | 36 | 1.5 | 11.75 |  |  |  | 43 | [10 empty] | 1346 | 1257.3 | 300 |  |  |  | 1092 | [17 empty] | 42 | 47 | 3.75 | 3.75 | 6.69 | 0.5 |  | 1066.8 | 1194 | 95.2 | 95.2 | 170 | 13
ASME 16.47 Series A | 150 | 44 | 55.25 | 51.75 | 1.625 | 40 | 1.5 | 12 |  |  |  | 45 | [10 empty] | 1403 | 1314.4 | 305 |  |  |  | 1143 | [17 empty] | 44 | 49 | 3.94 | 3.94 | 6.94 | 0.5 |  | 1117.6 | 1245 | 100.1 | 100.1 | 176 | 13
ASME 16.47 Series A | 150 | 46 | 57.25 | 53.75 | 1.625 | 40 | 1.5 | 12.25 |  |  |  | 47.12 | [10 empty] | 1454 | 1365.2 | 310 |  |  |  | 1197 | [17 empty] | 46 | 51 | 4 | 4 | 7.25 | 0.5 |  | 1168.4 | 1295 | 101.6 | 101.6 | 184 | 13
ASME 16.47 Series A | 150 | 48 | 59.5 | 56 | 1.625 | 44 | 1.5 | 12.5 |  |  |  | 49.12 | [10 empty] | 1511 | 1422.4 | 320 |  |  |  | 1248 | [17 empty] | 48 | 52.5 | 4.19 | 4.19 | 7.5 | 0.5 |  | 1219.2 | 1359 | 106.4 | 106.4 | 191 | 13
ASME 16.47 Series A | 150 | 50 | 67.75 | 58.25 | 1.875 | 44 | 1.75 | 13.5 |  |  |  | 51.25 | [10 empty] | 1568 | 1479.6 | 340 |  |  |  | 1302 | [17 empty] | 50 | 55.5 | 4.32 | 4.32 | 7.94 | 0.5 |  | 1270 | 1410 | 109.7 | 109.7 | 202 | 13
ASME 16.47 Series A | 150 | 52 | 64 | 60.5 | 1.875 | 44 | 1.75 | 13.75 |  |  |  | 53.25 | [10 empty] | 1626 | 1536.7 | 350 |  |  |  | 1353 | [17 empty] | 52 | 57.5 | 4.5 | 4.5 | 8.19 | 0.5 |  | 1320.8 | 1431 | 114.3 | 114.3 | 208 | 13
ASME 16.47 Series A | 150 | 54 | 66.25 | 62.75 | 1.875 | 44 | 1.75 | 14 |  |  |  | 55.25 | [10 empty] | 1683 | 1593.8 | 360 |  |  |  | 1403 | [17 empty] | 54 | 59.5 | 4.69 | 4.69 | 8.44 | 0.5 |  | 1371.6 | 15111 | 119.1 | 119.1 | 214 | 13
ASME 16.47 Series A | 150 | 56 | 68.75 | 65 | 1.875 | 48 | 1.75 | 14.5 |  |  |  | 57.38 | [10 empty] | 1746 | 1651 | 365 |  |  |  | 1457 | [17 empty] | 56 | 62 | 4.82 | 4.82 | 8.94 | 0.5 |  | 1422.4 | 1575 | 122.4 | 122.4 | 227 | 13
ASME 16.47 Series A | 150 | 58 | 71 | 67.25 | 1.875 | 48 | 1.75 | 14.75 |  |  |  | 59.38 | [10 empty] | 1803 | 1708.2 | 380 |  |  |  | 1508 | [17 empty] | 58 | 64 | 5 | 5 | 9.19 | 0.5 |  | 1473.2 | 1626 | 127 | 127 | 233 | 13
ASME 16.47 Series A | 150 | 60 | 73 | 69.25 | 1.875 | 52 | 1.75 | 15 |  |  |  | 61.38 | [10 empty] | 1854 | 1759 | 380 |  |  |  | 1559 | [17 empty] | 60 | 66 | 5.13 | 5.13 | 9.38 | 0.5 |  | 1524 | 1676 | 130.3 | 130.3 | 238 | 13
ASME 16.47 Series B | 75 | 26 | 30 | 28.5 | 0.75 | 36 | 0.625 | 4.5 |  |  |  | 26.62 | [10 empty] | 760 | 723.9 | 115 |  |  |  | 676 | [17 empty] | 26.06 | 27.75 | 1.25 | 1.25 | 2.25 | 0.31 |  | 661.9 | 705 | 31.8 | 31.8 | 57 | 8
ASME 16.47 Series B | 75 | 28 | 32 | 30.5 | 0.75 | 40 | 0.625 | 4.5 |  |  |  | 28.62 | [10 empty] | 813 | 774.7 | 115 |  |  |  | 727 | [17 empty] | 28.06 | 29.75 | 1.25 | 1.25 | 2.38 | 0.31 |  | 712.7 | 756 | 31.8 | 31.8 | 60 | 8
ASME 16.47 Series B | 75 | 30 | 34 | 32.5 | 0.75 | 44 | 0.625 | 4.75 |  |  |  | 30.62 | [10 empty] | 864 | 825.5 | 115 |  |  |  | 778 | [17 empty] | 30.06 | 31.75 | 1.25 | 1.25 | 2.5 | 0.31 |  | 763.5 | 806 | 31.8 | 31.8 | 64 | 8
ASME 16.47 Series B | 75 | 32 | 36 | 34.5 | 0.75 | 48 | 0.625 | 4.75 |  |  |  | 32.62 | [10 empty] | 914 | 876.3 | 120 |  |  |  | 829 | [17 empty] | 32.06 | 33.75 | 1.32 | 1.38 | 2.69 | 0.31 |  | 814.3 | 857 | 33.5 | 35.1 | 68 | 8
ASME 16.47 Series B | 75 | 34 | 38 | 36.5 | 0.75 | 52 | 0.625 | 4.75 |  |  |  | 34.62 | [10 empty] | 965 | 927.1 | 120 |  |  |  | 879 | [17 empty] | 34.06 | 35.75 | 1.32 | 1.44 | 2.82 | 0.31 |  | 865.1 | 908 | 33.5 | 36.6 | 72 | 8
ASME 16.47 Series B | 75 | 36 | 40.69 | 39.06 | 0.875 | 40 | 0.75 | 5 |  |  |  | 36.81 | [10 empty] | 1034 | 992.1 | 130 |  |  |  | 935 | [17 empty] | 36.06 | 38 | 1.38 | 1.61 | 3.32 | 0.38 |  | 915.9 | 965 | 35.1 | 40.9 | 84 | 10
ASME 16.47 Series B | 75 | 38 | 42.69 | 41.06 | 0.875 | 40 | 0.75 | 5.25 |  |  |  | 38.81 | [10 empty] | 1084 | 1042.9 | 130 |  |  |  | 986 | [17 empty] | 38.06 | 40 | 1.44 | 1.69 | 3.44 | 0.38 |  | 966.7 | 1016 | 36.6 | 42.9 | 87 | 10
ASME 16.47 Series B | 75 | 40 | 44.69 | 43.06 | 0.875 | 44 | 0.75 | 5.25 |  |  |  | 40.81 | [10 empty] | 1135 | 1093.7 | 130 |  |  |  | 1037 | [17 empty] | 40.06 | 42 | 1.44 | 1.69 | 3.57 | 0.38 |  | 1017.5 | 1067 | 36.6 | 42.9 | 91 | 110
ASME 16.47 Series B | 75 | 42 | 46.69 | 45.06 | 0.875 | 48 | 0.75 | 5.25 |  |  |  | 42.81 | [10 empty] | 1186 | 1144.5 | 135 |  |  |  | 1087 | [17 empty] | 42.06 | 44 | 1.5 | 1.82 | 3.69 | 0.38 |  | 1068.3 | 1118 | 38.1 | 46.2 | 94 | 10
ASME 16.47 Series B | 75 | 44 | 49.25 | 47.38 | 1 | 36 | 0.875 | 5.75 |  |  |  | 44.88 | [10 empty] | 1251 | 1203.5 | 150 |  |  |  | 1140 | [17 empty] | 44.06 | 46.25 | 1.63 | 1.88 | 4.07 | 0.38 |  | 1119.1 | 1175 | 41.4 | 47.8 | 103 | 10
ASME 16.47 Series B | 75 | 46 | 51.25 | 49.38 | 1 | 40 | 0.875 | 6 |  |  |  | 46.88 | [10 empty] | 1302 | 1254.3 | 150 |  |  |  | 1191 | [17 empty] | 46.06 | 48.25 | 1.69 | 1.94 | 4.19 | 0.38 |  | 1169.9 | 1226 | 42.9 | 49.3 | 106 | 10
ASME 16.47 Series B | 75 | 48 | 53.25 | 51.38 | 1 | 44 | 0.875 | 6 |  |  |  | 48.88 | [10 empty] | 1353 | 1305.1 | 160 |  |  |  | 1242 | [17 empty] | 48.06 | 50.25 | 1.75 | 2.07 | 4.32 | 0.38 |  | 1220.7 | 1276 | 44.6 | 52.6 | 110 | 10
ASME 16.47 Series B | 75 | 50 | 55.25 | 53.38 | 1 | 44 | 0.875 | 6.25 |  |  |  | 50.94 | [10 empty] | 1403 | 1355.9 | 160 |  |  |  | 1294 | [17 empty] | 50.06 | 52.25 | 1.82 | 2.13 | 4.5 | 0.38 |  | 1271.5 | 1327 | 46.2 | 54.1 | 114 | 10
ASME 16.47 Series B | 75 | 52 | 57.38 | 55.5 | 1 | 48 | 0.875 | 6.25 |  |  |  | 52.94 | [10 empty] | 1457 | 1409.7 | 16 |  |  |  | 1345 | [17 empty] | 52.06 | 54.25 | 1.82 | 2.19 | 4.69 | 0.38 |  | 1322.3 | 1378 | 46.2 | 55.6 | 119 | 10
ASME 16.47 Series B | 75 | 54 | 59.38 | 57.5 | 1 | 48 | 0.875 | 6.25 |  |  |  | 55 | [10 empty] | 1508 | 1460.5 | 160 |  |  |  | 1397 | [17 empty] | 54.06 | 56.25 | 1.88 | 2.32 | 4.88 | 0.38 |  | 1373.1 | 1429 | 47.8 | 58.9 | 124 | 10
ASME 16.47 Series B | 75 | 56 | 62 | 59.88 | 1.125 | 40 | 1 | 6.75 |  |  |  | 57.12 | [10 empty] | 1575 | 1521 | 170 |  |  |  | 1451 | [17 empty] | 56.06 | 58.5 | 1.94 | 2.38 | 5.25 | 0.44 |  | 1423.9 | 1486 | 49.3 | 60.5 | 133 | 11
ASME 16.47 Series B | 75 | 58 | 64 | 61.88 | 1.125 | 44 | 1 | 7 |  |  |  | 59.12 | [10 empty] | 1626 | 1571.8 | 180 |  |  |  | 1502 | [17 empty] | 58.06 | 60.5 | 2 | 2.44 | 5.38 | 0.44 |  | 1474.7 | 1537 | 50.8 | 62 | 137 | 11
ASME 16.47 Series B | 75 | 60 | 66 | 63.88 | 1.125 | 44 | 1 | 7.25 |  |  |  | 61.12 | [10 empty] | 1676 | 1622.6 | 185 |  |  |  | 1553 | [17 empty] | 60.06 | 62.5 | 2.13 | 2.57 | 5.63 | 0.44 |  | 1525.5 | 1588 | 54.1 | 65.3 | 143 | 11
ASME 16.47 Series B | 150 | 26 | 30.94 | 29.31 | 0.875 | 36 | 0.75 | 5.5 |  |  |  | 26.94 | [10 empty] | 786 | 744.5 | 140 |  |  |  | 683 | [17 empty] | 26.06 | 28 | 1.57 | 1.69 | 3.44 | 0.38 |  | 661.9 | 711 | 39.9 | 42.9 | 87 | 10
ASME 16.47 Series B | 150 | 28 | 32.94 | 31.31 | 0.875 | 40 | 0.75 | 5.75 |  |  |  | 28.94 | [10 empty] | 837 | 795.3 | 145 |  |  |  | 735 | [17 empty] | 28.06 | 30 | 1.69 | 1.82 | 3.69 | 0.38 |  | 712.7 | 762 | 42.9 | 46.2 | 94 | 10
ASME 16.47 Series B | 150 | 30 | 34.94 | 33.31 | 0.875 | 44 | 0.75 | 5.75 |  |  |  | 31 | [10 empty] | 887 | 846.1 | 145 |  |  |  | 787 | [17 empty] | 30.06 | 32 | 1.69 | 1.94 | 3.88 | 0.38 |  | 763.5 | 813 | 42.9 | 49.3 | 98 | 10
ASME 16.47 Series B | 150 | 32 | 37.06 | 35.44 | 0.875 | 48 | 0.75 | 5.75 |  |  |  | 33.06 | [10 empty] | 941 | 900.2 | 150 |  |  |  | 840 | [17 empty] | 32.06 | 34 | 1.75 | 2.07 | 4.19 | 0.38 |  | 814.3 | 864 | 44.4 | 52.6 | 106 | 10
ASME 16.47 Series B | 150 | 34 | 39.56 | 37.69 | 1 | 40 | 0.875 | 6.25 |  |  |  | 35.12 | [10 empty] | 1005 | 957.3 | 165 |  |  |  | 892 | [17 empty] | 34.06 | 36.25 | 1.88 | 2.19 | 4.28 | 0.38 |  | 865.1 | 921 | 47.8 | 55.6 | 109 | 10
ASME 16.47 Series B | 150 | 36 | 41.62 | 39.75 | 1 | 44 | 0.875 | 6.5 |  |  |  | 37.19 | [10 empty] | 1057 | 1009.6 | 165 |  |  |  | 945 | [17 empty] | 36.06 | 38.25 | 2 | 2.25 | 4.57 | 0.38 |  | 915.9 | 972 | 50.8 | 57.2 | 116 | 10
ASME 16.47 Series B | 150 | 38 | 44.25 | 42.12 | 1.125 | 40 | 1 | 7.25 |  |  |  | 39.25 | [10 empty] | 1124 | 1069.8 | 185 |  |  |  | 997 | [17 empty] | 38.12 | 40.25 | 2.07 | 2.44 | 4.82 | 0.38 |  | 968.2 | 1022 | 52.6 | 62 | 122 | 10
ASME 16.47 Series B | 150 | 40 | 46.25 | 44.12 | 1.125 | 44 | 1 | 7.25 |  |  |  | 41.31 | [10 empty] | 1175 | 1120.6 | 185 |  |  |  | 1049 | [17 empty] | 40.12 | 42.5 | 2.13 | 2.57 | 5 | 0.38 |  | 1019 | 1080 | 54.1 | 65.3 | 127 | 10
ASME 16.47 Series B | 150 | 42 | 48.25 | 46.12 | 1.125 | 48 | 1 | 7.5 |  |  |  | 43.38 | [10 empty] | 1226 | 1171.4 | 190 |  |  |  | 1102 | [17 empty] | 42.12 | 44.5 | 2.25 | 2.63 | 5.19 | 0.44 |  | 1069.8 | 1130 | 57.2 | 66.8 | 132 | 11
ASME 16.47 Series B | 150 | 44 | 50.25 | 48.12 | 1.125 | 52 | 1 | 7.75 |  |  |  | 445.38 | [10 empty] | 1276 | 1222.2 | 195 |  |  |  | 1153 | [17 empty] | 44.12 | 46.5 | 2.32 | 2.75 | 5.32 | 0.44 |  | 1120.6 | 1181 | 58.9 | 69.8 | 135 | 11
ASME 16.47 Series B | 150 | 46 | 52.81 | 50.56 | 1.25 | 40 | 1.125 | 8 |  |  |  | 47.44 | [10 empty] | 1341 | 1284.2 | 205 |  |  |  | 1205 | [17 empty] | 46.12 | 48.62 | 2.38 | 2.88 | 5.63 | 0.44 |  | 1171.4 | 1235 | 60.5 | 73.2 | 143 | 11
ASME 16.47 Series B | 150 | 48 | 54.81 | 52.56 | 1.25 | 44 | 1.125 | 8.25 |  |  |  | 49.5 | [10 empty] | 1392 | 1335 | 210 |  |  |  | 1257 | [17 empty] | 48.12 | 50.75 | 2.5 | 3 | 5.82 | 0.44 |  | 1222.2 | 1289 | 63.5 | 76.2 | 148 | 11
ASME 16.47 Series B | 150 | 50 | 56.81 | 54.56 | 1.25 | 48 | 1.125 | 8.5 |  |  |  | 51.5 | [10 empty] | 1443 | 1385.8 | 215 |  |  |  | 1308 | [17 empty] | 50.12 | 52.75 | 2.63 | 3.13 | 6 | 0.44 |  | 1273 | 1340 | 66.8 | 79.5 | 152 | 11
ASME 16.47 Series B | 150 | 52 | 58.81 | 56.56 | 1.25 | 52 | 1.125 | 8.75 |  |  |  | 53.56 | [10 empty] | 1494 | 1436.6 | 220 |  |  |  | 1360 | [17 empty] | 52.12 | 54.75 | 2.69 | 3.25 | 6.13 | 0.44 |  | 1323.8 | 1391 | 68.3 | 82.6 | 156 | 11
ASME 16.47 Series B | 150 | 54 | 61 | 58.75 | 1.25 | 56 | 1.125 | 8.75 |  |  |  | 55.62 | [10 empty] | 1549 | 1492.2 | 225 |  |  |  | 1413 | [17 empty] | 54.12 | 56.75 | 2.75 | 3.38 | 6.32 | 0.44 |  | 1374.6 | 1441 | 69.8 | 85.9 | 161 | 11
ASME 16.47 Series B | 150 | 56 | 63 | 60.75 | 1.25 | 60 | 1.125 | 9 |  |  |  | 57.62 | [10 empty] | 1600 | 1543 | 225 |  |  |  | 1465 | [17 empty] | 56.12 | 58.75 | 2.82 | 3.5 | 6.5 | 0.56 |  | 1425.4 | 1492 | 71.6 | 88.9 | 165 | 14
ASME 16.47 Series B | 150 | 58 | 65.94 | 63.44 | 1.375 | 48 | 1.25 | 9.25 |  |  |  | 59.69 | [10 empty] | 1675 | 1611.4 | 235 |  |  |  | 1516 | [17 empty] | 58.12 | 60.75 | 2.88 | 3.62 | 6.82 | 0.56 |  | 1476.2 | 1543 | 73.2 | 91.9 | 173 | 14
ASME 16.47 Series B | 150 | 60 | 67.94 | 65.44 | 1.375 | 52 | 1.25 | 9.5 |  |  |  | 61.81 | [10 empty] | 1726 | 1662.2 | 240 |  |  |  | 1570 | [17 empty] | 60.12 | 63 | 2.94 | 3.75 | 7 | 0.56 |  | 1527 | 1600 | 74.7 | 95.2 | 178 | 14
ASME 16.47 Series B | 300 | 26 | 34.12 | 31.62 | 1.375 | 32 | 1.25 | 10.5 |  |  |  | 27.62 | [10 empty] | 867 | 803.1 | 270 |  |  |  | 702 | [17 empty] | 26.19 | 29 | 3.44 | 3.44 | 5.63 | 0.56 |  | 665.2 | 737 | 87.4 | 87.4 | 143 | 14
ASME 16.47 Series B | 300 | 28 | 36.25 | 33.75 | 1.375 | 36 | 1.25 | 10.5 |  |  |  | 29.75 | [10 empty] | 921 | 857.2 | 270 |  |  |  | 756 | [17 empty] | 28.19 | 31 | 3.44 | 3.44 | 5.81 | 0.56 |  | 716 | 787 | 87.4 | 87.4 | 148 | 14
ASME 16.47 Series B | 300 | 30 | 39 | 36.25 | 1.5 | 36 | 1.375 | 11.25 |  |  |  | 32 | [10 empty] | 991 | 920.8 | 285 |  |  |  | 813 | [17 empty] | 30.25 | 33.25 | 3.63 | 3.63 | 6.16 | 0.56 |  | 768.4 | 845 | 92.2 | 92.2 | 156 | 14
ASME 16.47 Series B | 300 | 32 | 41.5 | 38.5 | 1.625 | 32 | 1.5 | 12.25 |  |  |  | 34 | [10 empty] | 1054 | 977.9 | 310 |  |  |  | 864 | [17 empty] | 32.25 | 35.5 | 4 | 4 | 6.56 | 0.62 |  | 819.2 | 902 | 101.6 | 101.6 | 167 | 16
ASME 16.47 Series B | 300 | 34 | 43.62 | 40.62 | 1.625 | 36 | 1.5 | 12.25 |  |  |  | 36.12 | [10 empty] | 1108 | 1031.7 | 310 |  |  |  | 917 | [17 empty] | 34.25 | 37.5 | 4 | 4 | 6.75 | 0.62 |  | 870 | 952 | 101.6 | 101.6 | 171 | 16
ASME 16.47 Series B | 300 | 36 | 46.12 | 42.88 | 1.75 | 32 | 1.625 | 12.5 |  |  |  | 38 | [10 empty] | 1171 | 1089.2 | 320 |  |  |  | 965 | [17 empty] | 36.25 | 39.75 | 4 | 4 | 7.06 | 0.62 |  | 920.8 | 1010 | 101.6 | 101.6 | 179 | 16
ASME 16.47 Series B | 300 | 38 | 48.12 | 44.88 | 1.75 | 36 | 1.625 | 13 |  |  |  | 40 | [10 empty] | 1222 | 1140 | 335 |  |  |  | 1016 | [17 empty] | 38.25 | 41.75 | 4.31 | 4.31 | 7.5 | 0.62 |  | 971.6 | 1060 | 109.5 | 109.5 | 190 | 16
ASME 16.47 Series B | 300 | 40 | 50.12 | 46.88 | 1.75 | 40 | 1.625 | 13.5 |  |  |  | 42 | [10 empty] | 1273 | 1190.8 | 345 |  |  |  | 1067 | [17 empty] | 40.25 | 43.88 | 4.5 | 4.5 | 7.75 | 0.62 |  | 1022.4 | 1115 | 114.3 | 114.3 | 197 | 16
ASME 16.47 Series B | 300 | 42 | 52.5 | 49 | 1.875 | 36 | 1.75 | 14 |  |  |  | 44 | [10 empty] | 1334 | 1244.6 | 355 |  |  |  | 1118 | [17 empty] | 42.31 | 46 | 4.63 | 4.63 | 8 | 0.62 |  | 1074.7 | 1168 | 117.6 | 117.6 | 203 | 16
ASME 16.47 Series B | 300 | 44 | 54.5 | 51 | 1.875 | 40 | 1.75 | 14.5 |  |  |  | 46.19 | [10 empty] | 1384 | 1295.4 | 370 |  |  |  | 1173 | [17 empty] | 44.31 | 48 | 4.94 | 4.94 | 8.38 | 0.62 |  | 1125.5 | 1219 | 125.5 | 125.5 | 213 | 16
ASME 16.47 Series B | 300 | 46 | 57.5 | 53.75 | 2 | 36 | 1.875 | 15 |  |  |  | 48.38 | [10 empty] | 1460 | 1365.2 | 380 |  |  |  | 1229 | [17 empty] | 46.31 | 50 | 5 | 5.06 | 8.69 | 0.62 |  | 1176.3 | 1270 | 127 | 128.5 | 221 | 16
ASME 16.47 Series B | 300 | 48 | 59.5 | 55.75 | 2 | 40 | 1.875 | 15 |  |  |  | 50.31 | [10 empty] | 1511 | 1416 | 380 |  |  |  | 1278 | [17 empty] | 48.31 | 52.25 | 5 | 5.25 | 8.75 | 0.62 |  | 1227.1 | 1327 | 127 | 133.4 | 222 | 16
ASME 16.47 Series B | 300 | 50 | 61.5 | 57.75 | 2 | 44 | 1.875 | 15.75 |  |  |  | 52.38 | [10 empty] | 1562 | 1466.8 | 400 |  |  |  | 1330 | [17 empty] | 50.31 | 54.25 | 5.38 | 5.44 | 9.19 | 0.62 |  | 1277.9 | 1378 | 136.7 | 138.2 | 233 | 16
ASME 16.47 Series B | 300 | 52 | 63.5 | 59.75 | 2 | 48 | 1.875 | 16 |  |  |  | 54.44 | [10 empty] | 1613 | 1517.6 | 410 |  |  |  | 1383 | [17 empty] | 52.31 | 56.25 | 5.56 | 5.61 | 9.5 | 0.62 |  | 1328.7 | 1429 | 141.2 | 142.5 | 241 | 16
ASME 16.47 Series B | 300 | 54 | 65.88 | 62.12 | 2 | 48 | 1.875 | 15.75 |  |  |  | 56.5 | [10 empty] | 1673 | 1577.8 | 400 |  |  |  | 1435 | [17 empty] | 54.31 | 58.25 | 5.32 | 5.81 | 9.38 | 0.62 |  | 1379.5 | 1480 | 135.1 | 147.6 | 238 | 16
ASME 16.47 Series B | 300 | 56 | 69.5 | 65 | 2.375 | 36 | 2.25 | 17.75 |  |  |  | 58.81 | [10 empty] | 1765 | 1651 | 450 |  |  |  | 1494 | [17 empty] | 56.31 | 60.5 | 6 | 6.12 | 10.5 | 0.69 |  | 14300.3 | 1537 | 152.4 | 155.4 | 267 | 17
ASME 16.47 Series B | 300 | 58 | 71.94 | 67.44 | 2.375 | 40 | 2.25 | 17.75 |  |  |  | 60.94 | [10 empty] | 1827 | 1713 | 450 |  |  |  | 1548 | [17 empty] | 58.31 | 62.75 | 6 | 6.31 | 10.75 | 0.69 |  | 1481.1 | 1594 | 152.4 | 160.3 | 273 | 17
ASME 16.47 Series B | 300 | 60 | 73.94 | 69.44 | 2.375 | 40 | 2.25 | 17.5 |  |  |  | 62.94 | [10 empty] | 1878 | 1763.8 | 450 |  |  |  | 1599 | [17 empty] | 60.31 | 65 | 5.88 | 6.5 | 10.63 | 0.69 |  | 1531.9 | 1651 | 149.4 | 165.1 | 270 | 17
ASME 16.1 | 25 | 4 | 9 | 7.5 | 0.75 | 8 | 0.625 |  |  | 0.75 |  | 5.31 | [10 empty] | 230 | [5 empty] | 135 | [30 empty] | 0.75 | N/A | 1.31 | N/A | N/A | N/A | 2.5 | N/A | 19 | N/A | 191 | 33 | N/A | N/A | N/A | 64 | N/A
ASME 16.1 | 25 | 5 | 10 | 8.5 | 0.75 | 8 | 0.625 |  |  | 0.75 |  | 6.44 | [10 empty] | 255 | [5 empty] | 164 | [30 empty] | 0.75 | N/A | 1.44 | N/A | N/A | N/A | 2.5 | N/A | 19 | N/A | 216 | 37 | N/A | N/A | N/A | 64 | N/A
ASME 16.1 | 25 | 6 | 11 | 9.5 | 0.75 | 8 | 0.625 |  |  | 0.75 |  | 7.56 | [10 empty] | 280 | [5 empty] | 192 | [30 empty] | 0.75 | N/A | 1.56 | N/A | N/A | N/A | 2.5 | N/A | 19 | N/A | 241 | 40 | N/A | N/A | N/A | 64 | N/A
ASME 16.1 | 25 | 8 | 13.5 | 11.75 | 0.75 | 8 | 0.625 |  |  | 0.75 |  | 9.69 | [10 empty] | 345 | [5 empty] | 246 | [30 empty] | 0.75 | N/A | 1.75 | N/A | N/A | N/A | 2.5 | N/A | 19 | N/A | 299 | 45 | N/A | N/A | N/A | 64 | N/A
ASME 16.1 | 25 | 10 | 16 | 14.25 | 0.75 | 12 | 0.625 |  |  | 0.88 |  | 11.94 | [10 empty] | 405 | [5 empty] | 303 | [30 empty] | 0.88 | N/A | 1.94 | N/A | N/A | N/A | 3 | N/A | 22.2 | N/A | 368 | 49 | N/A | N/A | N/A | 70 | N/A
ASME 16.1 | 25 | 12 | 19 | 17 | 0.75 | 12 | 0.625 |  |  | 1 |  | 14.06 | [10 empty] | 485 | [5 empty] | 357 | [30 empty] | 1 | N/A | 2.19 | N/A | N/A | N/A | 3 | N/A | 25.4 | N/A | 432 | 56 | N/A | N/A | N/A | 76 | N/A
ASME 16.1 | 25 | 14 | 21 | 18.75 | 0.875 | 12 | 0.75 |  |  | 1.12 |  | 15.37 | [10 empty] | 535 | [5 empty] | 391 | [30 empty] | 1.12 | N/A | 2.25 | N/A | N/A | N/A | 3.5 | N/A | 28.6 | N/A | 476 | 57 | N/A | N/A | N/A | 89 | N/A
ASME 16.1 | 25 | 16 | 23.5 | 21.25 | 0.875 | 16 | 0.75 |  |  | 1.12 |  | 17.5 | [10 empty] | 595 | [5 empty] | 445 | [30 empty] | 1.12 | N/A | 2.5 | N/A | N/A | N/A | 3.5 | N/A | 28.6 | N/A | 540 | 64 | N/A | N/A | N/A | 89 | N/A
ASME 16.1 | 25 | 18 | 25 | 22.75 | 0.875 | 16 | 0.75 |  |  | 1.25 |  | 19.62 | [10 empty] | 635 | [5 empty] | 498 | [30 empty] | 1.25 | N/A | 2.69 | N/A | N/A | N/A | 4 | N/A | 31.8 | N/A | 578 | 68 | N/A | N/A | N/A | 95 | N/A
ASME 16.1 | 25 | 20 | 27.5 | 25 | 0.875 | 20 | 0.75 |  |  | 1.25 |  | 21.75 | [10 empty] | 700 | [5 empty] | 552 | [30 empty] | 1.25 | N/A | 2.88 | N/A | N/A | N/A | 4 | N/A | 31.8 | N/A | 635 | 78 | N/A | N/A | N/A | 95 | N/A
ASME 16.1 | 25 | 24 | 32 | 29.5 | 0.875 | 20 | 0.75 |  |  | 1.38 |  | 26 | [10 empty] | 815 | [5 empty] | 560 | [30 empty] | 1.38 | N/A | 3.25 | N/A | N/A | N/A | 4 | N/A | 34.9 | N/A | 749 | 83 | N/A | N/A | N/A | 102 | N/A
ASME 16.1 | 25 | 30 | 38.75 | 36 | 1 | 28 | 0.875 |  |  | 1.5 |  | … | [10 empty] | 985 | [5 empty] | … | [30 empty] | 1.5 | N/A | … | N/A | N/A | N/A | 4.5 | N/A | 38.1 | N/A | 914 | … | N/A | N/A | N/A | 114 | N/A
ASME 16.1 | 25 | 36 | 46 | 42.75 | 1 | 32 | 0.875 |  |  | 1.62 |  | … | [10 empty] | 1170 | [5 empty] | … | [30 empty] | 1.62 | N/A | … | N/A | N/A | N/A | 5 | N/A | 41.3 | N/A | 1085 | … | N/A | N/A | N/A | 121 | N/A
ASME 16.1 | 25 | 42 | 53 | 49.5 | 1.125 | 36 | 1 |  |  | 1.75 |  | … | [10 empty] | 1345 | [5 empty] | … | [30 empty] | 1.75 | N/A | … | N/A | N/A | N/A | 5.5 | N/A | 44.5 | N/A | 1257 | … | N/A | N/A | N/A | 133 | N/A
ASME 16.1 | 25 | 48 | 59.5 | 56 | 1.125 | 44 | 1 |  |  | 2 |  | … | [10 empty] | 1510 | [5 empty] | … | [30 empty] | 2 | N/A | … | N/A | N/A | N/A | 6 | N/A | 50.8 | N/A | 1422 | … | N/A | N/A | N/A | 146 | N/A
ASME 16.1 | 25 | 54 | 66.25 | 62.75 | 1.125 | 44 | 1 |  |  | 2.25 |  | … | [10 empty] | 1685 | [5 empty] | … | [30 empty] | 2.25 | N/A | … | N/A | N/A | N/A | 6.5 | N/A | 57.2 | N/A | 1594 | … | N/A | N/A | N/A | 159 | N/A
ASME 16.1 | 25 | 60 | 73 | 69.25 | 1.25 | 52 | 1.125 |  |  | 2.25 |  | … | [10 empty] | 1855 | [5 empty] | … | [30 empty] | 2.25 | N/A | … | N/A | N/A | N/A | 6.5 | N/A | 57.2 | N/A | 1759 | … | N/A | N/A | N/A | 159 | N/A
ASME 16.1 | 25 | 72 | 86.5 | 82.5 | 1.25 | 60 | 1.125 |  |  | 2.5 |  | … | [10 empty] | 2195 | [5 empty] | … | [30 empty] | 2.5 | N/A | … | N/A | N/A | N/A | 7 | N/A | 63.5 | N/A | 2095 | … | N/A | N/A | N/A | 172 | N/A
ASME 16.1 | 25 | 84 | 99.75 | 95.5 | 1.375 | 64 | 1.25 |  |  | 2.75 |  | … | [10 empty] | 2535 | [5 empty] | … | [30 empty] | 2.75 | N/A | … | N/A | N/A | N/A | 7.5 | N/A | 69.9 | N/A | 2425 | … | N/A | N/A | N/A | 191 | N/A
ASME 16.1 | 25 | 96 | 113.25 | 108.5 | 1.375 | 68 | 1.25 |  |  | 3 |  | … | [10 empty] | 2875 | [5 empty] | … | [30 empty] | 3 | N/A | … | N/A | N/A | N/A | 8 | N/A | 76.2 | N/A | 2756 | … | N/A | N/A | N/A | 203 | N/A
ASME 16.1 | 125 | 1 | 4.25 | 3.12 | 0.625 | 4 | 0.5 |  |  |  |  | 1.94 | [10 empty] | 110 | [5 empty] | 49 | [30 empty] | 0.44 | N/A | 0.69 | N/A | 1 | 0.38 | 2 | … | 11.1 | N/A | 79 | 18 | N/A | 25 | 9.6 | 45 | …
ASME 16.1 | 125 | 1.25 | 4.62 | 3.5 | 0.625 | 4 | 0.5 |  |  |  |  | 2.31 | [10 empty] | 115 | [5 empty] | 59 | [30 empty] | 0.5 | N/A | 0.81 | N/A | 1.25 | 0.44 | 2 | … | 12.7 | N/A | 89 | 21 | N/A | 32 | 11.1 | 51 | …
ASME 16.1 | 125 | 1.5 | 5 | 3.88 | 0.625 | 4 | 0.5 |  |  |  |  | 2.56 | [10 empty] | 125 | [5 empty] | 65 | [30 empty] | 0.56 | N/A | 0.88 | N/A | 1.5 | 0.5 | 2 | … | 14.3 | N/A | 98 | 22 | N/A | 38 | 12.7 | 51 | …
ASME 16.1 | 125 | 2 | 6 | 4.75 | 0.75 | 4 | 0.625 |  |  |  |  | 3.06 | [10 empty] | 150 | [5 empty] | 78 | [30 empty] | 0.62 | N/A | 1 | N/A | 2 | 0.56 | 2.5 | … | 15.9 | N/A | 121 | 25 | N/A | 51 | 14.3 | 57 | …
ASME 16.1 | 125 | 2.5 | 7 | 5.5 | 0.75 | 4 | 0.625 |  |  |  |  | 3.56 | [10 empty] | 180 | [5 empty] | 91 | [30 empty] | 0.69 | N/A | 1.12 | N/A | 2.5 | 0.63 | 2.5 | … | 17.5 | N/A | 140 | 29 | N/A | 64 | 15.9 | 64 | …
ASME 16.1 | 125 | 3 | 7.5 | 6 | 0.75 | 4 | 0.625 |  |  |  |  | 4.25 | [10 empty] | 190 | [5 empty] | 108 | [30 empty] | 0.75 | N/A | 1.19 | N/A | 3 | 0.69 | 2.5 | … | 19 | N/A | 152 | 30 | N/A | 76 | 17.5 | 64 | …
ASME 16.1 | 125 | 3.5 | 8.5 | 7 | 0.75 | 8 | 0.625 |  |  |  |  | 4.81 | [10 empty] | 215 | [5 empty] | 122 | [30 empty] | 0.81 | N/A | 1.25 | N/A | 3.5 | 0.75 | 3 | … | 20.6 | N/A | 178 | 32 | N/A | 89 | 19 | 70 | …
ASME 16.1 | 125 | 4 | 9 | 7.5 | 0.75 | 8 | 0.625 |  |  |  |  | 5.31 | [10 empty] | 230 | [5 empty] | 135 | [30 empty] | 0.94 | N/A | 1.31 | N/A | 4 | 0.88 | 3 | … | 23.8 | N/A | 191 | 33 | N/A | 102 | 22.2 | 76 | …
ASME 16.1 | 125 | 5 | 10 | 8.5 | 0.875 | 8 | 0.75 |  |  |  |  | 6.44 | [10 empty] | 255 | [5 empty] | 164 | [30 empty] | 0.94 | N/A | 1.44 | N/A | 5 | 0.88 | 3 | … | 23.8 | N/A | 216 | 37 | N/A | 125 | 22.2 | 76 | …
ASME 16.1 | 125 | 6 | 11 | 9.5 | 0.875 | 8 | 0.75 |  |  |  |  | 7.56 | [10 empty] | 280 | [5 empty] | 192 | [30 empty] | 1 | N/A | 1.56 | N/A | 6 | 0.94 | 3.5 | … | 25.4 | N/A | 241 | 40 | N/A | 152 | 23.8 | 83 | …
ASME 16.1 | 125 | 8 | 13.5 | 11.75 | 0.875 | 8 | 0.75 |  |  |  |  | 9.69 | [10 empty] | 345 | [5 empty] | 246 | [30 empty] | 1.12 | N/A | 1.75 | N/A | 8 | 1.06 | 3.5 | … | 28.6 | N/A | 299 | 45 | N/A | 203 | 27 | 89 | …
ASME 16.1 | 125 | 10 | 16 | 14.25 | 1 | 12 | 0.875 |  |  |  |  | 11.94 | [10 empty] | 405 | [5 empty] | 303 | [30 empty] | 1.19 | N/A | 1.94 | N/A | 10 | 1.12 | 4 | … | 30.2 | N/A | 362 | 49 | N/A | 254 | 28.6 | 95 | …
ASME 16.1 | 125 | 12 | 19 | 17 | 1 | 12 | 0.875 |  |  |  |  | 14.06 | [10 empty] | 485 | [5 empty] | 357 | [30 empty] | 1.25 | N/A | 2.19 | N/A | 12 | 0.81 | 4 | … | 31.8 | N/A | 432 | 56 | N/A | 305 | 20.6 | 95 | …
ASME 16.1 | 125 | 14 | 14 | 18.75 | 1.125 | 12 | 1 |  |  |  |  | 15.38 | [10 empty] | 535 | [5 empty] | 391 | [30 empty] | 1.38 | N/A | 2.25 | N/A | 14 | 0.88 | 4.5 | … | 35.1 | N/A | 476 | 57 | N/A | 356 | 22.2 | 108 | …
ASME 16.1 | 125 | 16 | 23.5 | 21.25 | 1.125 | 16 | 1 |  |  |  |  | 17.5 | [10 empty] | 595 | [5 empty] | 445 | [30 empty] | 1.44 | N/A | 2.5 | N/A | 16 | 1 | 4.5 | … | 36.5 | N/A | 540 | 64 | N/A | 406 | 25.4 | 114 | …
ASME 16.1 | 125 | 18 | 25 | 22.75 | 1.25 | 16 | 1.125 |  |  |  |  | 19.62 | [10 empty] | 635 | [5 empty] | 499 | [30 empty] | 1.56 | N/A | 2.69 | N/A | 18 | 1.06 | 5 | … | 39.7 | N/A | 578 | 68 | N/A | 457 | 27 | 121 | …
ASME 16.1 | 125 | 20 | 27.5 | 25 | 1.25 | 20 | 1.125 |  |  |  |  | 21.75 | [10 empty] | 700 | [5 empty] | 553 | [30 empty] | 1.69 | N/A | 2.88 | N/A | 20 | 1.12 | 5 | … | 42.9 | N/A | 635 | 73 | N/A | 508 | 28.6 | 127 | …
ASME 16.1 | 125 | 24 | 32 | 29.5 | 1.375 | 20 | 1.25 |  |  |  |  | 26 | [10 empty] | 815 | [5 empty] | 660 | [30 empty] | 1.88 | N/A | 3.25 | N/A | 24 | 1.25 | 5.5 | … | 47.6 | N/A | 749 | 83 | N/A | 610 | 31.8 | 140 | …
ASME 16.1 | 125 | 30 | 38.75 | 36 | 1.375 | 28 | 1.25 |  |  |  |  | … | [10 empty] | 985 | [5 empty] | … | [30 empty] | 2.12 | N/A | … | N/A | 30 | 1.44 | 6.5 | … | 54 | N/A | 914 | … | N/A | 762 | 36.6 | 159 | …
ASME 16.1 | 125 | 36 | 46 | 42.75 | 1.625 | 32 | 1.5 |  |  |  |  | … | [10 empty] | 1170 | [5 empty] | … | [30 empty] | 2.38 | N/A | … | N/A | 36 | 1.62 | 7 | 9 | 60.3 | N/A | 1086 | … | N/A | 914 | 41.3 | 178 | 222
ASME 16.1 | 125 | 42 | 53 | 49.5 | 1.625 | 36 | 1.5 |  |  |  |  | … | [10 empty] | 1345 | [5 empty] | … | [30 empty] | 2.62 | N/A | … | N/A | 42 | 1.81 | 7.5 | 9.5 | 66.7 | N/A | 1257 | … | N/A | 1066 | 46 | 191 | 235
ASME 16.1 | 125 | 48 | 59.5 | 56 | 1.625 | 44 | 1.5 |  |  |  |  | … | [10 empty] | 1510 | [5 empty] | … | [30 empty] | 2.75 | N/A | … | N/A | 48 | 2 | 8 | 9.5 | 69.9 | N/A | 1422 | … | N/A | 1219 | 50.8 | 197 | 242
ASME 16.1 | 125 | 54 (9) | 66.25 | 62.75 | 2 | 44 | 1.75 |  |  |  |  | … | [10 empty] | 1685 | [5 empty] | … | [30 empty] | 3 | N/A | … | N/A | … | … | 8.5 | 10.5 | 76.2 | N/A | 1594 | … | N/A | … | … | 216 | 267
ASME 16.1 | 125 | 60 (9) | 73 | 69.25 | 2 | 52 | 1.75 |  |  |  |  | … | [10 empty] | 1855 | [5 empty] | … | [30 empty] | 3.12 | N/A | … | N/A | … | … | 9 | 11 | 79.4 | N/A | 1759 | … | N/A | … | … | 222 | 273
ASME 16.1 | 125 | 66 (9) | 80 | 76 | 2 | 52 | 1.75 |  |  |  |  | … | [10 empty] | 2032 | [5 empty] | … | [30 empty] | 3.38 | N/A | … | N/A | … | … | 9.5 | 11.5 | 85.7 | N/A | 1930 | … | N/A | … | … | 241 | 292
ASME 16.1 | 125 | 72 (9) | 86.5 | 82.5 | 2 | 60 | 1.75 |  |  |  |  | … | [10 empty] | 2195 | [5 empty] | … | [30 empty] | 3.5 | N/A | … | N/A | … | … | 9.5 | 11.5 | 88.9 | N/A | 2096 | … | N/A | … | … | 241 | 292
ASME 16.1 | 125 | 78 (9) | 93 | 89 | 2.25 | 64 | 2 |  |  |  |  | … | [10 empty] | 2365 | [5 empty] | … | [30 empty] | 3.75 | N/A | … | N/A | … | … | 10.5 | 12.5 | 95.3 | N/A | 2261 | … | N/A | … | … | 267 | 318
ASME 16.1 | 125 | 84 (9) | 99.75 | 95.5 | 2.25 | 64 | 2 |  |  |  |  | … | [10 empty] | 2535 | [5 empty] | … | [30 empty] | 3.88 | N/A | … | N/A | … | … | 10.5 | 13 | 98.4 | N/A | 2426 | … | N/A | … | … | 267 | 324
ASME 16.1 | 125 | 90 (9) | 106.5 | 102 | 2.5 | 68 | 2.25 |  |  |  |  | … | [10 empty] | 2720 | [5 empty] | … | [30 empty] | 4.12 | N/A | … | N/A | … | … | 11.5 | 14 | 104.6 | N/A | 2591 | … | N/A | … | … | 292 | 357
ASME 16.1 | 125 | 96 (9) | 113.25 | 108.5 | 2.5 | 68 | 2.25 |  |  |  |  | … | [10 empty] | 2875 | [5 empty] | … | [30 empty] | 4.25 | N/A | … | N/A | … | … | 11.5 | 14 | 108 | N/A | 2756 | … | N/A | … | … | 292 | 356
ASME 16.1 | 250 | 1 | 4.88 | 3.5 | 0.75 | 4 | 0.62 |  |  | 0.69 |  | 2.06 | [10 empty] | 125 | [5 empty] | 52 | [30 empty] | 0.69 | 2.69 | 0.88 | 0.68 | 1 | … | 2.5 | … | 17.5 | 68 | 89 | 22 | 18 | 25 | … | 64 | …
ASME 16.1 | 250 | 1.25 | 5.25 | 3.88 | 0.75 | 4 | 0.62 |  |  | 0.75 |  | 2.5 | [10 empty] | 135 | [5 empty] | 64 | [30 empty] | 0.75 | 3.06 | 1 | 0.81 | 1.25 | … | 2.5 | … | 19 | 78 | 98 | 25 | 19 | 32 | … | 64 | …
ASME 16.1 | 250 | 1.5 | 6.12 | 4.5 | 0.875 | 4 | 0.75 |  |  | 0.81 |  | 2.75 | [10 empty] | 155 | [5 empty] | 70 | [30 empty] | 0.81 | 3.56 | 1.12 | 0.87 | 1.5 | … | 3 | … | 20.6 | 91 | 114 | 29 | 22 | 38 | … | 70 | …
ASME 16.1 | 250 | 2 | 6.5 | 5 | 0.75 | 8 | 0.62 |  |  | 0.88 |  | 3.31 | [10 empty] | 165 | [5 empty] | 84 | [30 empty] | 0.88 | 4.19 | 1.25 | 1 | 2 | .. | 3 | … | 22.2 | 106 | 127 | 32 | 25 | 51 | … | 70 | …
ASME 16.1 | 250 | 2.5 | 7.5 | 5.88 | 0.875 | 8 | 0.75 |  |  | 1 |  | 3.94 | [10 empty] | 190 | [5 empty] | 100 | [30 empty] | 1 | 4.94 | 1.43 | 1.13 | 2.5 | … | 3.5 | … | 25.4 | 125 | 149 | 37 | 29 | 64 | … | 83 | …
ASME 16.1 | 250 | 3 | 8.25 | 6.62 | 0.875 | 8 | 0.75 |  |  | 1.12 |  | 4.62 | [10 empty] | 210 | [5 empty] | 118 | [30 empty] | 1.12 | 5.69 | 1.56 | 1.19 | 3 | … | 3.5 | … | 28.6 | 144 | 168 | 40 | 31 | 76 | … | 89 | …
ASME 16.1 | 250 | 3.5 | 9 | 7.25 | 0.875 | 8 | 0.75 |  |  | 1.19 |  | 5.25 | [10 empty] | 230 | [5 empty] | 133 | [30 empty] | 1.19 | 6.31 | 1.62 | 1.25 | 3.5 | .. | 3.5 | … | 30.2 | 160 | 184 | 41 | 32 | 89 | … | 89 | …
ASME 16.1 | 250 | 4 | 10 | 7.88 | 0.875 | 8 | 0.75 |  |  | 1.25 |  | 5.75 | [10 empty] | 255 | [5 empty] | 146 | [30 empty] | 1.25 | 6.94 | 1.75 | 1.31 | 4 | … | 4 | … | 31.8 | 176 | 200 | 44 | 33 | 102 | … | 95 | …
ASME 16.1 | 250 | 5 | 11 | 9.25 | 0.875 | 8 | 0.75 |  |  | 1.38 |  | 7 | [10 empty] | 280 | [5 empty] | 178 | [30 empty] | 1.38 | 8.31 | 1.88 | 1.44 | 5 | … | 4 | … | 34.9 | 211 | 235 | 48 | 36 | 127 | … | 102 | …
ASME 16.1 | 250 | 6 | 12.5 | 10.62 | 0.875 | 12 | 0.75 |  |  | 1.44 |  | 8.12 | [10 empty] | 320 | [5 empty] | 206 | [30 empty] | 1.44 | 9.69 | 1.94 | 1.56 | 6 | .. | 4 | … | 36.5 | 246 | 270 | 49 | 39 | 152 | … | 102 | …
ASME 16.1 | 250 | 8 | 15 | 13 | 1.125 | 12 | 0.88 |  |  | 1.62 |  | 10.25 | [10 empty] | 380 | [5 empty] | 260 | [30 empty] | 1.62 | 11.94 | 2.19 | 1.75 | 8 | … | 4.5 | … | 41.3 | 303 | 330 | 56 | 43 | 203 | … | 114 | …
ASME 16.1 | 250 | 10 | 17.5 | 15.25 | 1.25 | 16 | 1 |  |  | 1.88 |  | 12.62 | [10 empty] | 445 | [5 empty] | 321 | [30 empty] | 1.88 | 14.06 | 2.38 | 1.94 | 10 | 0.94 | 5.5 | … | 47.6 | 357 | 387 | 60 | 49 | 254 | 23.8 | 131 | …
ASME 16.1 | 250 | 12 | 20.5 | 17.75 | 1.25 | 16 | 1.12 |  |  | 2 |  | 14.75 | [10 empty] | 520 | [5 empty] | 375 | [30 empty] | 2 | 16.44 | 2.56 | 2.19 | 12 | 1 | 5.5 | … | 50.8 | 418 | 451 | 65 | 54 | 305 | 25.4 | 140 | …
ASME 16.1 | 250 | 14 | 23 | 20.25 | 1.375 | 20 | 1.12 |  |  | 2.12 |  | 16.25 | [10 empty] | 585 | [5 empty] | 413 | [30 empty] | 2.12 | 18.94 | 2.69 | 2.25 | 13.25 | 1.12 | 6 | … | 54 | 481 | 514 | 68 | 57 | 337 | 28.6 | 152 | …
ASME 16.1 | 250 | 16 | 25 | 22.5 | 1.375 | 20 | 1.25 |  |  | 2.25 |  | 18.38 | [10 empty] | 650 | [5 empty] | 467 | [30 empty] | 2.25 | 21.06 | 2.88 | 2.5 | 15.25 | 1.25 | 6.5 | … | 57.2 | 535 | 572 | 73 | 62 | 387 | 31.8 | 159 | …
ASME 16.1 | 250 | 18 | 28 | 24.75 | 1.375 | 24 | 1.25 |  |  | 2.38 |  | … | [10 empty] | 710 | [5 empty] | … | [30 empty] | 2.38 | 23.31 | … | … | 17 | 1.38 | 6.5 | … | 60.3 | 592 | 629 | … | … | 432 | 34.9 | 165 | …
ASME 16.1 | 250 | 20 | 30.5 | 27 | 1.375 | 24 | 1.25 |  |  | 2.5 |  | … | [10 empty] | 775 | [5 empty] | … | [30 empty] | 2.5 | 25.56 | … | … | 19 | 1.5 | 7 | … | 63.5 | 649 | 686 | … | … | 483 | 38.1 | 172 | …
ASME 16.1 | 250 | 24 | 36 | 32 | 1.625 | 24 | 1.5 |  |  | 2.75 |  | … | [10 empty] | 915 | [5 empty] | … | [30 empty] | 2.75 | 30.31 | … | … | 23 | 1.62 | 7.5 | 9.5 | 69.8 | 770 | 813 | … | … | 584 | 41.3 | 191 | 241
ASME 16.1 | 250 | 30 | 43 | 39.25 | 2 | 28 | 1.75 |  |  | 3 |  | … | [10 empty] | 1090 | [5 empty] | … | [30 empty] | 3 | 37.19 | … | … | 29 | 2 | 8.5 | 10.5 | 76.2 | 945 | 997 | … | … | 737 | 50.8 | 216 | 268
ASME 16.1 | 250 | 36 (10) | 50 | 46 | 2.25 | 32 | 2 |  |  | 3.38 |  | … | [10 empty] | 1270 | [5 empty] | … | [30 empty] | 3.38 | 43.69 | … | … | … | … | 9.5 | 12 | 85.7 | 1110 | 1168 | … | … | … | … | 241 | 298
ASME 16.1 | 250 | 42 (10) | 57 | 52.75 | 2.25 | 36 | 2 |  |  | 3.69 |  | … | [10 empty] | 1450 | [5 empty] | … | [30 empty] | 3.69 | 50.44 | … | … | … | … | 10 | 12.5 | 93.7 | 1281 | 1340 | … | … | … | … | 254 | 318
ASME 16.1 | 250 | 48 (10) | 65 | 60.75 | 2.25 | 40 | 2 |  |  | 4 |  | … | [10 empty] | 1650 | [5 empty] | … | [30 empty] | 4 | 58.44 | … | … | … | … | 11 | 13 | 101.6 | 1484 | 1543 | … | … | … | … | 273 | 330
AWWA C207 | B | 4 | 9 | 7.5 |  | 8 | 0.625 |  |  | 0.625 |  | N/A |  |  |  | N/A |  | 4.57 | [30 empty] | N/A | [27 empty] | 0.625 | 86 | 129
AWWA C207 | B | 5 | 10 | 8.5 |  | 8 | 0.75 |  |  | 0.625 |  | N/A |  |  |  | N/A |  | 5.66 | [30 empty] | N/A | [27 empty] | 0.625 | 86 | 129
AWWA C207 | B | 6 | 11 | 9.5 |  | 8 | 0.75 |  |  | 0.688 |  | N/A |  |  |  | N/A |  | 6.72 | [30 empty] | N/A | [27 empty] | 0.688 | 86 | 129
AWWA C207 | B | 8 | 13.5 | 11.75 |  | 8 | 0.75 |  |  | 0.688 |  | N/A |  |  |  | N/A |  | 8.72 | [30 empty] | N/A | [27 empty] | 0.688 | 86 | 129
AWWA C207 | B | 10 | 16 | 14.25 |  | 12 | 0.875 |  |  | 0.688 |  | N/A |  |  |  | N/A |  | 10.88 | [30 empty] | N/A | [27 empty] | 0.688 | 86 | 129
AWWA C207 | B | 12 | 19 | 17 |  | 12 | 0.875 |  |  | 0.688 |  | N/A |  |  |  | N/A |  | 12.88 | [30 empty] | N/A | [27 empty] | 0.688 | 86 | 129
AWWA C207 | B | 14 | 21 | 18.75 |  | 12 | 1 |  |  | 0.688 |  | N/A |  |  |  | N/A |  | 14.19 | [30 empty] | N/A | [27 empty] | 0.688 | 86 | 129
AWWA C207 | B | 16 | 23.5 | 21.25 |  | 16 | 1 |  |  | 0.688 |  | N/A |  |  |  | N/A |  | 16.19 | [30 empty] | N/A | [27 empty] | 0.688 | 86 | 129
AWWA C207 | B | 18 | 25 | 22.75 |  | 16 | 1.125 |  |  | 0.688 |  | N/A |  |  |  | N/A |  | 18.19 | [30 empty] | N/A | [27 empty] | 0.688 | 86 | 129
AWWA C207 | B | 20 | 27.5 | 25 |  | 20 | 1.125 |  |  | 0.688 |  | N/A |  |  |  | N/A |  | 20.19 | [30 empty] | N/A | [27 empty] | 0.688 | 86 | 129
AWWA C207 | B | 22 | 29.5 | 27.25 |  | 20 | 1.25 |  |  | 0.75 |  | N/A |  |  |  | N/A |  | 22.19 | [30 empty] | N/A | [27 empty] | 0.75 | 86 | 129
AWWA C207 | B | 24 | 32 | 29.5 |  | 20 | 1.25 |  |  | 0.75 |  | N/A |  |  |  | N/A |  | 24.19 | [30 empty] | N/A | [27 empty] | 0.75 | 86 | 129
AWWA C207 | B | 26 | 34.25 | 31.75 |  | 24 | 1.25 |  |  | 0.812 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 0.812 | 86 | 129
AWWA C207 | B | 28 | 36.5 | 34 |  | 28 | 1.25 |  |  | 0.875 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 0.875 | 86 | 129
AWWA C207 | B | 30 | 38.75 | 36 |  | 28 | 1.25 |  |  | 0.875 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 0.875 | 86 | 129
AWWA C207 | B | 32 | 41.75 | 38.5 |  | 28 | 1.5 |  |  | 0.938 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 0.938 | 86 | 129
AWWA C207 | B | 34 | 43.75 | 40.5 |  | 32 | 1.5 |  |  | 0.938 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 0.938 | 86 | 129
AWWA C207 | B | 36 | 46 | 42.75 |  | 32 | 1.5 |  |  | 1 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 1 | 86 | 129
AWWA C207 | B | 38 | 48.75 | 45.25 |  | 32 | 1.5 |  |  | 1 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 1 | 86 | 129
AWWA C207 | B | 40 | 50.75 | 47.25 |  | 36 | 1.5 |  |  | 1 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 1 | 86 | 129
AWWA C207 | B | 42 | 53 | 49.5 |  | 36 | 1.5 |  |  | 1.125 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 1.125 | 86 | 129
AWWA C207 | B | 44 | 55.25 | 51.75 |  | 40 | 1.5 |  |  | 1.125 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 1.125 | 86 | 129
AWWA C207 | B | 46 | 57.25 | 53.75 |  | 40 | 1.5 |  |  | 1.125 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 1.125 | 86 | 129
AWWA C207 | B | 48 | 59.5 | 56 |  | 44 | 1.5 |  |  | 1.25 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 1.25 | 86 | 129
AWWA C207 | B | 50 | 61.75 | 58.25 |  | 44 | 1.75 |  |  | 1.25 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 1.25 | 86 | 129
AWWA C207 | B | 52 | 64 | 60.5 |  | 44 | 1.75 |  |  | 1.25 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 1.25 | 86 | 129
AWWA C207 | B | 54 | 66.25 | 62.75 |  | 44 | 1.75 |  |  | 1.375 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 1.375 | 86 | 129
AWWA C207 | B | 60 | 73 | 69.25 |  | 52 | 1.75 |  |  | 1.5 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 1.5 | 86 | 129
AWWA C207 | B | 66 | 80 | 76 |  | 52 | 1.75 |  |  | 1.625 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 1.625 | 86 | 129
AWWA C207 | B | 72 | 86.5 | 82.5 |  | 60 | 1.75 |  |  | 1.75 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 1.75 | 86 | 129
AWWA C207 | B | 78 | 93 | 89 |  | 64 | 2 |  |  | 2 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 2 | 86 | 129
AWWA C207 | B | 84 | 99.75 | 95.5 |  | 64 | 2 |  |  | 2 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 2 | 86 | 129
AWWA C207 | B | 90 | 106.5 | 102 |  | 68 | 2.25 |  |  | 2.25 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 2.25 | 86 | 129
AWWA C207 | B | 96 | 113.25 | 108.5 |  | 68 | 2.25 |  |  | 2.25 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 2.25 | 86 | 129
AWWA C207 | B | 102 | 120 | 114.5 |  | 72 | 2.5 |  |  | 2.5 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 2.5 | 86 | 129
AWWA C207 | B | 108 | 126.75 | 120.75 |  | 72 | 2.5 |  |  | 2.5 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 2.5 | 86 | 129
AWWA C207 | B | 114 | 133.5 | 126.75 |  | 76 | 2.75 |  |  | 2.75 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 2.75 | 86 | 129
AWWA C207 | B | 120 | 140.25 | 132.75 |  | 76 | 2.75 |  |  | 2.75 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 2.75 | 86 | 129
AWWA C207 | B | 126 | 147 | 139.25 |  | 80 | 3 |  |  | 3 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 3 | 86 | 129
AWWA C207 | B | 132 | 153.75 | 145.75 |  | 80 | 3 |  |  | 3 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 3 | 86 | 129
AWWA C207 | B | 144 | 167.25 | 158.25 |  | 84 | 3.25 |  |  | 3.25 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 3.25 | 86 | 129
AWWA C207 | D | 4 | 9 | 7.5 |  | 8 | 0.625 |  |  | 0.625 |  | 5.312 |  |  |  | 0.875 |  | 4.57 | [30 empty] | 0.5 | [27 empty] | 0.625 | 175-150 | 262.5
AWWA C207 | D | 5 | 10 | 8.5 |  | 8 | 0.75 |  |  | 0.65 |  | 6.312 |  |  |  | 1.25 |  | 5.66 | [30 empty] | 0.562 | [27 empty] | 0.625 | 175-150 | 262.5
AWWA C207 | D | 6 | 11 | 9.5 |  | 8 | 0.75 |  |  | 0.693 |  | 7.562 |  |  |  | 1.25 |  | 6.72 | [30 empty] | 0.562 | [27 empty] | 0.688 | 175-150 | 262.5
AWWA C207 | D | 8 | 13.5 | 11.75 |  | 8 | 0.75 |  |  | 0.812 |  | 9.688 |  |  |  | 1.25 |  | 8.72 | [30 empty] | 0.562 | [27 empty] | 0.688 | 175-150 | 262.5
AWWA C207 | D | 10 | 16 | 14.25 |  | 12 | 0.875 |  |  | 0.953 |  | 12 |  |  |  | 1.25 |  | 10.88 | [30 empty] | 0.688 | [27 empty] | 0.688 | 175-150 | 262.5
AWWA C207 | D | 12 | 19 | 17 |  | 12 | 0.875 |  |  | 1.117 |  | 14.375 |  |  |  | 1.25 |  | 12.88 | [30 empty] | 0.688 | [27 empty] | 0.812 | 175-150 | 262.5
AWWA C207 | D | 14 | 21 | 18.75 |  | 12 | 1 |  |  | 1.133 |  | 15.75 |  |  |  | 1.25 |  | 14.19 | [30 empty] | 0.75 | [27 empty] | 0.938 | 175-150 | 225
AWWA C207 | D | 16 | 23.5 | 21.25 |  | 16 | 1 |  |  | 1.265 |  | 18 |  |  |  | 1.25 |  | 16.19 | [30 empty] | 0.75 | [27 empty] | 1 | 175-150 | 225
AWWA C207 | D | 18 | 25 | 22.75 |  | 16 | 1.125 |  |  | 1.331 |  | 19.875 |  |  |  | 1.25 |  | 18.19 | [30 empty] | 0.75 | [27 empty] | 1.062 | 175-150 | 225
AWWA C207 | D | 20 | 27.5 | 25 |  | 20 | 1.125 |  |  | 1.448 |  | 22 |  |  |  | 1.25 |  | 20.19 | [30 empty] | 0.75 | [27 empty] | 1.125 | 175-150 | 225
AWWA C207 | D | 22 | 29.5 | 27.25 |  | 20 | 1.25 |  |  | 1.568 |  | 24.25 |  |  |  | 1.75 |  | 22.19 | [30 empty] | 1 | [27 empty] | 1.188 | 175-150 | 225
AWWA C207 | D | 24 | 32 | 29.5 |  | 20 | 1.25 |  |  | 1.661 |  | 26.125 |  |  |  | 1.75 |  | 24.19 | [30 empty] | 1 | [27 empty] | 1.25 | 175-150 | 225
AWWA C207 | D | 26 | 34.25 | 31.75 |  | 24 | 1.25 |  |  | 1.786 |  | 28.5 |  |  |  | 1.75 |  | - | [30 empty] | 1 | [27 empty] | 1.312 | 175-150 | 225
AWWA C207 | D | 28 | 36.5 | 34 |  | 28 | 1.25 |  |  | 1.906 |  | 30.5 |  |  |  | 1.75 |  | - | [30 empty] | 1 | [27 empty] | 1.312 | 175-150 | 225
AWWA C207 | D | 30 | 38.75 | 36 |  | 28 | 1.25 |  |  | 2.008 |  | 32.5 |  |  |  | 1.75 |  | - | [30 empty] | 1 | [27 empty] | 1.375 | 175-150 | 225
AWWA C207 | D | 32 | 41.75 | 38.5 |  | 28 | 1.5 |  |  | 2.15 |  | 34.75 |  |  |  | 1.75 |  | - | [30 empty] | 1.125 | [27 empty] | 1.5 | 175-150 | 225
AWWA C207 | D | 34 | 43.75 | 40.5 |  | 32 | 1.5 |  |  | 2.252 |  | 36.75 |  |  |  | 1.75 |  | - | [30 empty] | 1.125 | [27 empty] | 1.5 | 175-150 | 225
AWWA C207 | D | 36 | 46 | 42.75 |  | 32 | 1.5 |  |  | 2.37 |  | 38.75 |  |  |  | 1.75 |  | - | [30 empty] | 1.125 | [27 empty] | 1.625 | 175-150 | 225
AWWA C207 | D | 38 | 48.75 | 45.25 |  | 32 | 1.5 |  |  | 2.506 |  | 40.75 |  |  |  | 1.75 |  | - | [30 empty] | 1.125 | [27 empty] | 1.625 | 175-150 | 225
AWWA C207 | D | 40 | 50.75 | 47.25 |  | 36 | 1.5 |  |  | 2.609 |  | 43 |  |  |  | 1.75 |  | - | [30 empty] | 1.125 | [27 empty] | 1.625 | 175-150 | 225
AWWA C207 | D | 42 | 53 | 49.5 |  | 36 | 1.5 |  |  | 2.729 |  | 45 |  |  |  | 1.75 |  | - | [30 empty] | 1.25 | [27 empty] | 1.75 | 175-150 | 225
AWWA C207 | D | 44 | 55.25 | 51.75 |  | 40 | 1.5 |  |  | 2.849 |  | 47 |  |  |  | 2.25 |  | - | [30 empty] | 1.25 | [27 empty] | 1.75 | 175-150 | 225
AWWA C207 | D | 46 | 57.25 | 53.75 |  | 40 | 1.5 |  |  | 2.952 |  | 49 |  |  |  | 2.25 |  | - | [30 empty] | 1.25 | [27 empty] | 1.75 | 175-150 | 225
AWWA C207 | D | 48 | 59.5 | 56 |  | 44 | 1.5 |  |  | 3.072 |  | 51 |  |  |  | 2.5 |  | - | [30 empty] | 1.375 | [27 empty] | 1.875 | 175-150 | 225
AWWA C207 | D | 50 | 61.75 | 58.25 |  | 44 | 1.75 |  |  | 3.196 |  | 53 |  |  |  | 2.5 |  | - | [30 empty] | 1.375 | [27 empty] | 2 | 175-150 | 225
AWWA C207 | D | 52 | 64 | 60.5 |  | 44 | 1.75 |  |  | 3.315 |  | 55 |  |  |  | 2.5 |  | - | [30 empty] | 1.375 | [27 empty] | 2 | 175-150 | 225
AWWA C207 | D | 54 | 66.25 | 62.75 |  | 44 | 1.75 |  |  | 3.435 |  | 57 |  |  |  | 2.5 |  | - | [30 empty] | 1.375 | [27 empty] | 2.125 | 175-150 | 225
AWWA C207 | D | 60 | 73 | 69.25 |  | 52 | 1.75 |  |  | 3.779 |  | 63 |  |  |  | 2.75 |  | - | [30 empty] | 1.5 | [27 empty] | 2.25 | 175-150 | 225
AWWA C207 | D | 66 | 80 | 76 |  | 52 | 1.75 |  |  | 4.136 |  | 69 |  |  |  | 2.75 |  | - | [30 empty] | 1.5 | [27 empty] | 2.5 | 175-150 | 225
AWWA C207 | D | 72 | 86.5 | 82.5 |  | 60 | 1.75 |  |  | 4.48 |  | 75 |  |  |  | 2.75 |  | - | [30 empty] | 1.5 | [27 empty] | 2.625 | 175-150 | 225
AWWA C207 | D | 78 | 93 | 89 |  | 64 | 2 |  |  | - |  | 81.25 |  |  |  | 3 |  | - | [30 empty] | 1.75 | [27 empty] | 2.75 | 175-150 | 225
AWWA C207 | D | 84 | 99.75 | 95.5 |  | 64 | 2 |  |  | - |  | 87.5 |  |  |  | 3 |  | - | [30 empty] | 1.75 | [27 empty] | 2.875 | 175-150 | 225
AWWA C207 | D | 90 | 106.5 | 102 |  | 68 | 2.25 |  |  | - |  | 93.75 |  |  |  | 3.25 |  | - | [30 empty] | 2 | [27 empty] | 3 | 175-150 | 225
AWWA C207 | D | 96 | 113.25 | 108.5 |  | 68 | 2.25 |  |  | - |  | 100 |  |  |  | 3.25 |  | - | [30 empty] | 2 | [27 empty] | 3.25 | 175-150 | 225
AWWA C207 | D | 102 | 120 | 114.5 |  | 72 | 2.5 |  |  | - |  | - |  |  |  | - |  | - | [30 empty] | - | [27 empty] | 3.25 | 175-150 | 225
AWWA C207 | D | 108 | 126.75 | 120.75 |  | 72 | 2.5 |  |  | - |  | - |  |  |  | - |  | - | [30 empty] | - | [27 empty] | 3.375 | 175-150 | 225
AWWA C207 | D | 114 | 133.5 | 126.75 |  | 76 | 2.75 |  |  | - |  | - |  |  |  | - |  | - | [30 empty] | - | [27 empty] | 3.5 | 175-150 | 225
AWWA C207 | D | 120 | 140.25 | 132.75 |  | 76 | 2.75 |  |  | - |  | - |  |  |  | - |  | - | [30 empty] | - | [27 empty] | 3.5 | 175-150 | 225
AWWA C207 | D | 126 | 147 | 139.25 |  | 80 | 3 |  |  | - |  | - |  |  |  | - |  | - | [30 empty] | - | [27 empty] | 3.75 | 175-150 | 225
AWWA C207 | D | 132 | 153.75 | 145.75 |  | 80 | 3 |  |  | - |  | - |  |  |  | - |  | - | [30 empty] | - | [27 empty] | 3.875 | 175-150 | 225
AWWA C207 | D | 144 | 167.25 | 158.25 |  | 84 | 3.25 |  |  | - |  | - |  |  |  | - |  | - | [30 empty] | - | [27 empty] | 4.125 | 175-150 | 225
AWWA C207 | E | 4 | 9 | 7.5 |  | 8 | 0.625 |  |  | 1.125 |  | 5.312 |  |  |  | 1.312 |  | 4.57 | [30 empty] | 0.938 | [27 empty] | 1.125 | 275 | 412.5
AWWA C207 | E | 5 | 10 | 8.5 |  | 8 | 0.75 |  |  | 1.188 |  | 6.438 |  |  |  | 1.438 |  | 5.66 | [30 empty] | 0.938 | [27 empty] | 1.188 | 275 | 412.5
AWWA C207 | E | 6 | 11 | 9.5 |  | 8 | 0.75 |  |  | 1.313 |  | 7.562 |  |  |  | 1.562 |  | 6.72 | [30 empty] | 1 | [27 empty] | 1.313 | 275 | 412.5
AWWA C207 | E | 8 | 13.5 | 11.75 |  | 8 | 0.75 |  |  | 1.5 |  | 9.688 |  |  |  | 1.75 |  | 8.72 | [30 empty] | 1.125 | [27 empty] | 1.5 | 275 | 412.5
AWWA C207 | E | 10 | 16 | 14.25 |  | 12 | 0.875 |  |  | 1.563 |  | 12 |  |  |  | 1.938 |  | 10.88 | [30 empty] | 1.188 | [27 empty] | 1.563 | 275 | 412.5
AWWA C207 | E | 12 | 19 | 17 |  | 12 | 0.875 |  |  | 1.75 |  | 14.375 |  |  |  | 2.188 |  | 12.88 | [30 empty] | 1.25 | [27 empty] | 1.75 | 275 | 412.5
AWWA C207 | E | 14 | 21 | 18.75 |  | 12 | 1 |  |  | 1.875 |  | 15.75 |  |  |  | 2.25 |  | 14.19 | [30 empty] | 1.375 | [27 empty] | 1.875 | 275 | 412.5
AWWA C207 | E | 16 | 23.5 | 21.25 |  | 16 | 1 |  |  | 2 |  | 18 |  |  |  | 2.5 |  | 16.19 | [30 empty] | 1.438 | [27 empty] | 2 | 275 | 412.5
AWWA C207 | E | 18 | 25 | 22.75 |  | 16 | 1.125 |  |  | 2.125 |  | 19.875 |  |  |  | 2.688 |  | 18.19 | [30 empty] | 1.562 | [27 empty] | 2.125 | 275 | 412.5
AWWA C207 | E | 20 | 27.5 | 25 |  | 20 | 1.125 |  |  | 2.375 |  | 22 |  |  |  | 2.875 |  | 20.19 | [30 empty] | 1.688 | [27 empty] | 2.375 | 275 | 412.5
AWWA C207 | E | 22 | 29.5 | 27.25 |  | 20 | 1.25 |  |  | 2.5 |  | 24 |  |  |  | 3.125 |  | 22.19 | [30 empty] | 1.812 | [27 empty] | 2.5 | 275 | 412.5
AWWA C207 | E | 24 | 32 | 29.5 |  | 20 | 1.25 |  |  | 2.625 |  | 26.125 |  |  |  | 3.25 |  | 24.19 | [30 empty] | 1.875 | [27 empty] | 2.625 | 275 | 412.5
AWWA C207 | E | 26 | 34.25 | 31.75 |  | 24 | 1.25 |  |  | 2.75 |  | 28.5 |  |  |  | 3.375 |  | - | [30 empty] | 2 | [27 empty] | 2.75 | 275 | 412.5
AWWA C207 | E | 28 | 36.5 | 34 |  | 28 | 1.25 |  |  | 2.75 |  | 30.75 |  |  |  | 3.438 |  | - | [30 empty] | 2.062 | [27 empty] | 2.75 | 275 | 412.5
AWWA C207 | E | 30 | 38.75 | 36 |  | 28 | 1.25 |  |  | 2.875 |  | 32.75 |  |  |  | 3.5 |  | - | [30 empty] | 2.125 | [27 empty] | 2.875 | 275 | 412.5
AWWA C207 | E | 32 | 41.75 | 38.5 |  | 28 | 1.5 |  |  | 3 |  | 35 |  |  |  | 3.625 |  | - | [30 empty] | 2.25 | [27 empty] | 3 | 275 | 412.5
AWWA C207 | E | 34 | 43.75 | 40.5 |  | 32 | 1.5 |  |  | 3.05 |  | 37 |  |  |  | 3.688 |  | - | [30 empty] | 2.312 | [27 empty] | 3 | 275 | 412.5
AWWA C207 | E | 36 | 46 | 42.75 |  | 32 | 1.5 |  |  | 3.209 |  | 39.25 |  |  |  | 3.75 |  | - | [30 empty] | 2.375 | [27 empty] | 3.125 | 275 | 412.5
AWWA C207 | E | 38 | 48.75 | 45.25 |  | 32 | 1.5 |  |  | 3.394 |  | 41.75 |  |  |  | 3.75 |  | - | [30 empty] | 2.375 | [27 empty] | 3.125 | 275 | 412.5
AWWA C207 | E | 40 | 50.75 | 47.25 |  | 36 | 1.5 |  |  | 3.533 |  | 43.75 |  |  |  | 3.875 |  | - | [30 empty] | 2.5 | [27 empty] | 3.25 | 275 | 412.5
AWWA C207 | E | 42 | 53 | 49.5 |  | 36 | 1.5 |  |  | 3.695 |  | 46 |  |  |  | 4 |  | - | [30 empty] | 2.625 | [27 empty] | 3.375 | 275 | 412.5
AWWA C207 | E | 44 | 55.25 | 51.75 |  | 40 | 1.5 |  |  | 3.857 |  | 48 |  |  |  | 4 |  | - | [30 empty] | 2.625 | [27 empty] | 3.375 | 275 | 412.5
AWWA C207 | E | 46 | 57.25 | 53.75 |  | 40 | 1.5 |  |  | 3.997 |  | 50 |  |  |  | 4.062 |  | - | [30 empty] | 2.688 | [27 empty] | 3.438 | 275 | 412.5
AWWA C207 | E | 48 | 59.5 | 56 |  | 44 | 1.5 |  |  | 4.159 |  | 52.25 |  |  |  | 4.125 |  | - | [30 empty] | 2.75 | [27 empty] | 3.5 | 275 | 412.5
AWWA C207 | E | 50 | 61.75 | 58.25 |  | 44 | 1.75 |  |  | 4.327 |  | 54.25 |  |  |  | 4.125 |  | - | [30 empty] | 2.75 | [27 empty] | 3.5 | 275 | 412.5
AWWA C207 | E | 52 | 64 | 60.5 |  | 44 | 1.75 |  |  | 4.489 |  | 56.5 |  |  |  | 4.25 |  | - | [30 empty] | 2.875 | [27 empty] | 3.625 | 275 | 412.5
AWWA C207 | E | 54 | 66.25 | 62.75 |  | 44 | 1.75 |  |  | 4.651 |  | 58.75 |  |  |  | 4.375 |  | - | [30 empty] | 3 | [27 empty] | 3.75 | 275 | 412.5
AWWA C207 | E | 60 | 73 | 69.75 |  | 52 | 1.75 |  |  | 5.116 |  | 65.25 |  |  |  | 4.5 |  | - | [30 empty] | 3.125 | [27 empty] | 3.875 | 275 | 412.5
AWWA C207 | E | 66 | 80 | 76 |  | 52 | 1.75 |  |  | 5.601 |  | 71.5 |  |  |  | 4.875 |  | - | [30 empty] | 3.375 | [27 empty] | 4.25 | 275 | 412.5
AWWA C207 | E | 72 | 86.5 | 82.5 |  | 60 | 1.75 |  |  | 6.066 |  | 78.5 |  |  |  | 5 |  | - | [30 empty] | 3.5 | [27 empty] | 4.375 | 275 | 412.5
AWWA C207 | E | 78 | 93 | 89 |  | 64 | 2 |  |  | - |  | 84.5 |  |  |  | 5.375 |  | - | [30 empty] | 3.875 | [27 empty] | 4.75 | 275 | 412.5
AWWA C207 | E | 84 | 99.75 | 95.5 |  | 64 | 2 |  |  | - |  | 90.5 |  |  |  | 5.375 |  | - | [30 empty] | 3.875 | [27 empty] | 4.75 | 275 | 412.5
AWWA C207 | E | 90 | 106.5 | 102 |  | 68 | 2.25 |  |  | - |  | 96.75 |  |  |  | 5.75 |  | - | [30 empty] | 4.25 | [27 empty] | 5.125 | 275 | 412.5
AWWA C207 | E | 96 | 113.25 | 108.5 |  | 68 | 2.25 |  |  | - |  | 102.75 |  |  |  | 5.75 |  | - | [30 empty] | 4.25 | [27 empty] | 5.125 | 275 | 412.5
AWWA C207 | E | 102 | 120 | 114.5 |  | 72 | 2.5 |  |  | - |  | - |  |  |  | - |  | - | [30 empty] | - | [27 empty] | 5.5 | 275 | 412.5
AWWA C207 | E | 108 | 126.75 | 120.75 |  | 72 | 2.5 |  |  | - |  | - |  |  |  | - |  | - | [30 empty] | - | [27 empty] | 5.5 | 275 | 412.5
AWWA C207 | E | 114 | 133.5 | 126.75 |  | 76 | 2.75 |  |  | - |  | - |  |  |  | - |  | - | [30 empty] | - | [27 empty] | 5.875 | 275 | 412.5
AWWA C207 | E | 120 | 140.25 | 132.75 |  | 76 | 2.75 |  |  | - |  | - |  |  |  | - |  | - | [30 empty] | - | [27 empty] | 5.875 | 275 | 412.5
AWWA C207 | E | 126 | 147 | 139.25 |  | 80 | 3 |  |  | - |  | - |  |  |  | - |  | - | [30 empty] | - | [27 empty] | 6.25 | 275 | 412.5
AWWA C207 | E | 132 | 153.75 | 145.75 |  | 80 | 3 |  |  | - |  | - |  |  |  | - |  | - | [30 empty] | - | [27 empty] | 6.25 | 275 | 412.5
AWWA C207 | E | 144 | 167.25 | 158.25 |  | 84 | 3.25 |  |  | - |  | - |  |  |  | - |  | - | [30 empty] | - | [27 empty] | 6.75 | 275 | 412.5
AWWA C207 | F | 4 | 10 | 7.88 |  | 8 | 0.75 |  |  | 1.13 |  | N/A |  |  |  | N/A |  | 4.57 | [30 empty] | N/A | [27 empty] | 1.13 | 300 | 450
AWWA C207 | F | 5 | 11 | 9.25 |  | 8 | 0.75 |  |  | 1.21 |  | N/A |  |  |  | N/A |  | 5.66 | [30 empty] | N/A | [27 empty] | 1.21 | 300 | 450
AWWA C207 | F | 6 | 12.5 | 10.62 |  | 12 | 0.75 |  |  | 1.31 |  | N/A |  |  |  | N/A |  | 6.73 | [30 empty] | N/A | [27 empty] | 1.31 | 300 | 450
AWWA C207 | F | 8 | 15 | 13 |  | 12 | 0.875 |  |  | 1.31 |  | N/A |  |  |  | N/A |  | 8.73 | [30 empty] | N/A | [27 empty] | 1.31 | 300 | 450
AWWA C207 | F | 10 | 17.5 | 15.25 |  | 16 | 1 |  |  | 1.5 |  | N/A |  |  |  | N/A |  | 10.88 | [30 empty] | N/A | [27 empty] | 1.5 | 300 | 450
AWWA C207 | F | 12 | 20.5 | 17.75 |  | 16 | 1.125 |  |  | 1.63 |  | N/A |  |  |  | N/A |  | 12.88 | [30 empty] | N/A | [27 empty] | 1.63 | 300 | 450
AWWA C207 | F | 14 | 23 | 20.25 |  | 20 | 1.125 |  |  | 1.94 |  | N/A |  |  |  | N/A |  | 14.19 | [30 empty] | N/A | [27 empty] | 1.94 | 300 | 450
AWWA C207 | F | 16 | 25.5 | 22.5 |  | 20 | 1.25 |  |  | 2.14 |  | N/A |  |  |  | N/A |  | 16.19 | [30 empty] | N/A | [27 empty] | 2.14 | 300 | 450
AWWA C207 | F | 18 | 28 | 24.75 |  | 24 | 1.25 |  |  | 2.25 |  | N/A |  |  |  | N/A |  | 18.19 | [30 empty] | N/A | [27 empty] | 2.25 | 300 | 450
AWWA C207 | F | 20 | 30.5 | 27 |  | 24 | 1.25 |  |  | 2.33 |  | N/A |  |  |  | N/A |  | 20.19 | [30 empty] | N/A | [27 empty] | 2.33 | 300 | 450
AWWA C207 | F | 22 | 33 | 29.25 |  | 24 | 1.255 |  |  | 2.5 |  | N/A |  |  |  | N/A |  | 22.19 | [30 empty] | N/A | [27 empty] | 2.5 | 300 | 450
AWWA C207 | F | 24 | 36 | 32 |  | 24 | 1.5 |  |  | 2.69 |  | N/A |  |  |  | N/A |  | 24.19 | [30 empty] | N/A | [27 empty] | 2.69 | 300 | 450
AWWA C207 | F | 26 | 38.25 | 34.5 |  | 28 | 1.75 |  |  | 3 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 3 | 300 | 450
AWWA C207 | F | 28 | 40.75 | 37 |  | 28 | 1.75 |  |  | 3.13 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 3.13 | 300 | 450
AWWA C207 | F | 30 | 43 | 39.25 |  | 28 | 1.75 |  |  | 3.166 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 3.15 | 300 | 450
AWWA C207 | F | 32 | 45.25 | 41.5 |  | 28 | 1.75 |  |  | 3.332 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 3.25 | 300 | 450
AWWA C207 | F | 34 | 47.5 | 43.5 |  | 28 | 1.75 |  |  | 3.475 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 3.38 | 300 | 450
AWWA C207 | F | 36 | 50 | 46 |  | 32 | 2 |  |  | 3.671 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 3.46 | 300 | 450
AWWA C207 | F | 38 | 52.25 | 48 |  | 32 | 2 |  |  | 3.815 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 3.5 | 300 | 450
AWWA C207 | F | 40 | 54.25 | 50.25 |  | 36 | 2 |  |  | 3.982 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 3.63 | 300 | 450
AWWA C207 | F | 42 | 57 | 52.75 |  | 36 | 2 |  |  | 4.171 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 3.81 | 300 | 450
AWWA C207 | F | 44 | 59.25 | 55 |  | 36 | 2 |  |  | 4.338 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 4 | 300 | 450
AWWA C207 | F | 46 | 61.5 | 57.25 |  | 40 | 2 |  |  | 4.505 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 4.13 | 300 | 450
AWWA C207 | F | 48 | 65 | 60.75 |  | 40 | 2 |  |  | 4.781 |  | N/A |  |  |  | N/A |  | - | [30 empty] | N/A | [27 empty] | 4.5 | 300 | 450
Note on K2: James Dawley: Conflicts with column BD - need to verify
Note on K3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: B16.1 refers to this value as "Q" rather than "tf"
Note on K378: James Dawley: Need to confirm values - conflicts with columns BD

## Sheet1
Nominal Pipe Size/ Bore for LWN J | Outside Diameter O | Min. Thickness t f | Diameter of Raised Face R | Diameter of Hub X | Diameter Beginning of Chamefer Welding Neck A | Threaded Slip-on Socket Welding Y1 | Lapped Y2 | Welding Neck Y3 | Long Welding Neck Y4 | Minimum Thread Length Threaded T | Minimum Slip-On Socket Welding B1 | Minimum Lapped B2 | Welding Neck / Socket Welding B3 | Corner Bore Radius of Lapped Flange and Pipe r | Depth of Socket D | Minimum Counter- bore Threaded Flange Q | Bolt Circle Dia | Number of Holes | Diameter of Holes
½ | 3.75 | 0.56 | 1.38 | 1.5 | 0.84 | 0.88 | 0.88 | 2.06 | 9 | 0.62 | 0.88 | 0.9 | Note-3 | 0.12 | 0.38 | 0.93 | 2.62 | 4 | 0.63
¾ | 4.62 | 0.62 | 1.69 | 1.88 | 1.05 | 1 | 1 | 2.25 | 9 | 0.62 | 1.09 | 1.11 | Note-3 | 0.12 | 0.44 | 1.14 | 3.25 | 4 | 0.75
1 | 4.88 | 0.69 | 2 | 2.12 | 1.32 | 1.06 | 1.06 | 2.44 | 9 | 0.69 | 1.36 | 1.38 | Note-3 | 0.12 | 0.5 | 1.41 | 3.5 | 4 | 0.75
1¼ | 5.25 | 0.81 | 2.5 | 2.5 | 1.66 | 1.12 | 1.12 | 2.62 | 9 | 0.81 | 1.7 | 1.72 | Note-3 | 0.19 | 0.56 | 1.75 | 3.88 | 4 | 0.75
1½ | 6.12 | 0.88 | 2.88 | 2.75 | 1.9 | 1.25 | 1.25 | 2.75 | 9 | 0.88 | 1.95 | 1.97 | Note-3 | 0.25 | 0.62 | 1.99 | 4.5 | 4 | 0.88
2 | 6.5 | 1 | 3.62 | 3.31 | 2.38 | 1.44 | 1.44 | 2.88 | 9 | 1.12 | 2.44 | 2.46 | Note-3 | 0.31 | 0.69 | 2.5 | 5 | 8 | 0.75
2½ | 7.5 | 1.12 | 4.12 | 3.94 | 2.88 | 1.62 | 1.62 | 3.12 | 9 | 1.25 | 2.94 | 2.97 | Note-3 | 0.31 | 0.75 | 3 | 5.88 | 8 | 0.88
3 | 8.25 | 1.25 | 5 | 4.62 | 3.5 | 1.81 | 1.81 | 3.25 | 9 | 1.38 | 3.57 | 3.6 | Note-3 | 0.38 | 0.81 | 3.63 | 6.62 | 8 | 0.88
3½ | 9 | 1.38 | 5.5 | 5.25 | 4 | 1.94 | 1.94 | 3.38 | 9 | 1.56 | 4.07 | 4.1 | Note-3 | 0.38 | - | 4.13 | 7.25 | 8 | 1
4 | 10 | 1.38 | 6.19 | 5.75 | 4.5 | 2 | 2 | 3.5 | Note-3 | 1.44 | 4.57 | 4.6 | Note-3 | 0.44 | - | 4.63 | 7.88 | 8 | 1
5 | 11 | 1.5 | 7.31 | 7 | 5.56 | 2.12 | 2.12 | 4 | 12 | 1.69 | 5.66 | 5.69 | Note-3 | 0.44 | - | 5.69 | 9.25 | 8 | 1
6 | 12.5 | 1.62 | 8.5 | 8.12 | 6.63 | 2.25 | 2.25 | 4.06 | 12 | 1.81 | 6.72 | 6.75 | Note-3 | 0.5 | - | 6.75 | 10.62 | 12 | 1
8 | 15 | 1.88 | 10.62 | 10.25 | 8.63 | 2.69 | 2.69 | 4.62 | 12 | 2 | 8.72 | 8.75 | Note-3 | 0.5 | - | 8.75 | 13 | 12 | 1.13
10 | 17.5 | 2.12 | 12.75 | 12.62 | 10.75 | 2.88 | 4 | 4.88 | 12 | 2.19 | 10.88 | 10.92 | Note-3 | 0.5 | - | 10.88 | 15.25 | 16 | 1.25
12 | 20.5 | 2.25 | 15 | 14.75 | 12.75 | 3.12 | 4.25 | 5.38 | 12 | 2.38 | 12.88 | 12.92 | Note-3 | 0.5 | - | 12.94 | 17.75 | 16 | 1.38
14 | 23 | 2.38 | 16.25 | 16.75 | 14 | 3.31 | 4.62 | 5.88 | 12 | 2.5 | 14.14 | 14.18 | Note-3 | 0.5 | - | 14.19 | 20.25 | 20 | 1.38
16 | 25.5 | 2.5 | 18.5 | 19 | 16 | 3.69 | 5 | 6 | 12 | 2.69 | 16.16 | 16.19 | Note-3 | 0.5 | - | 16.19 | 22.5 | 20 | 1.5
18 | 28 | 2.62 | 21 | 21 | 18 | 3.88 | 5.38 | 6.5 | 12 | 2.75 | 18.18 | 18.2 | Note-3 | 0.5 | - | 18.19 | 24.75 | 24 | 1.5
20 | 30.5 | 2.75 | 23 | 23.12 | 20 | 4 | 5.75 | 6.62 | 12 | 2.88 | 20.2 | 20.25 | Note-3 | 0.5 | - | 20.19 | 27 | 24 | 1.63
22 | 33 | 2.88 | 25.25 | 25.25 | 22 | 4.25 | 6 | 6.75 | 12 | - | 22.22 | 22.25 | Note-3 | 0.5 | - | - | 29.25 | 24 | 1.75
24 | 36 | 3 | 27.25 | 27.62 | 24 | 4.5 | 6.25 | 6.88 | 12 | 3.25 | 24.25 | 24.25 | Note-3 | 0.5 | - | 24.19 | 32 | 24 | 1.88
Notes: