## Survey Results
HI Databook Review
Section IV - Piping Materials
Sub-Section Number | Title | Keep | Delete | Modify | Add | Comments 1 | Comments 2
IV A | Steel Pipe
1 | Pipe dimensions: wrought steel & stainless steel |  |  | x |  | Verify with current ANSI/ASTM/ASME standard | Update standards referenced. ASME/ANSI B36.10M-2015 for welded & seamless wrought steel pipe and B36.19M for welded & seamless wrought stainless steel pipe. We should explain the relative roughness values/column or replace with the Moody chart. I remember as a new engineer first learning to apply friction loss his took me some time to figure out how to use. New engineers may not even know what this is. Add weight per linear foot. Add water weight per linear foot.
2 | Specifications for wrought steel and stainless steel pipe |  | ? | x | ? | Verify with current ASME standards. Do we want to include any standards other than ASTM and API? | Update standards referenced. I'm not sure what the purpose is for this table. Would it be helpful to list common uses? (e.g. wrought pipe is suitable for both high and low temperature/pressure applications, ductile iron is suitable for Gravity sewer applications, etc.)
3 | API casting list |  |  | x |  | See API note | I had to recruit colleagues who work with API and high pressure pumpsfor help with these tables. I'll have feedback by next Wed. 4/26.
4 | API plain-end liner list |  |  | x |  | See API note
5 | API tubing list |  |  | x |  | See API note
6 | API drill pipe list |  |  | x |  | See API note
IV B | Iron Pipe
1 | Cast iron pipe dimensions |  |  | x |  | Verify & update with current ANSI/ASTM/ASME standards. Recommend keeping even though it is probably not used frequently. Most users do not realize cast iron and ductile iron pipe have different dimensions than steel pipe. | Is this still relevant or is ductile iron now the predominant choice? ASTM A74-16?
2 | Ductile iron pipe dimensions |  |  | x |  | Verify & update with current ANSI/ASTM/ASME standards. Recommend keeping even though it is probably not used frequently. Most users do not realize cast iron and ductile iron pipe have different dimensions than steel pipe. | Update standard to ASTM A746 - 09(2014)?
IV C | Non-Ferrous Pipe and Tubing
1 | Aluminum alloy seamless pipe and extruded tube | x |  |  |  | Verify with current ANSI/ASTM/ASME standard | Recruited help from another department. Will get feedback by Wed. 4/26.
2 | Aluminum alloy pipe - oil and gas transmission and distribution systems | x |  |  |  | Verify with current ANSI/ASTM/ASME standard
3 | Aluminum coiled tubing - instrument and oil lines, refrigeration services | x |  |  |  | Verify with current ANSI/ASTM/ASME standard
4 | Seamless copper and seamless red brass pipe | x |  |  |  | Verify with current ANSI/ASTM/ASME standard
5 | Threadless copper pipe | x |  |  |  | Verify with current ANSI/ASTM/ASME standard
6 | Seamless copper water tube | x |  |  |  | Verify with current ANSI/ASTM/ASME standard
7 | Wrought seamless copper and copper alloy tube | x |  |  |  | Verify with current ANSI/ASTM/ASME standard
8 | Copper capillary tube, hard-drawn | x |  |  |  | Verify with current ANSI/ASTM/ASME standard
9 | Seamless copper - nickel pipe and tube | x |  |  |  | Verify with current ANSI/ASTM/ASME standard
IV D | Plastic Line Pipe
1 | Thermosetting resin line pipe, glass fiber reinforced |  |  | x |  | See API note | replace with ASTM D3517 - 14 reference? Note, commonly referred to as "Fiberglass"
2 | Thermoplastic line pipe (PVC) |  |  | x |  | See API note | replace with ASTM D2665 - 14 reference?
IV E | Flanges
1 | Steel pipe flanges and flanged fittings - 150 to 2500 lb |  |  | x | x | Verify with current ANSI/ASTM/ASME standard | Update reference. Prior to dimensional tables, add a note of about selecting appropriate flange type, face, and material (cast iron vs. steel & SS). I found a good article online that addresses some basic questions. http://www.whatispiping.com/selection-of-various-types-of-flanges I'd also like to see something that describes the flange type with a picture. Here's an example. http://www.coastalflange.com/pipe-flanges.html ASME B16.5 for steel flanges NPS 1/2 to NPS 24. What about sizes over 24"? I have used AWWA C207, but there is ASME B16.47 for size NPS 26 to NPS 60.
2 | Steel flange facings, lapped joints |  |  | x | x | Verify with current ANSI/ASTM/ASME standard | I find this section very confusing. I think it would be helpful to first show the pictures with explainations of the different face types prior to dimensioning. For example http://www.sunnysteel.com/blog/index.php/flange-face/ Also the formating requires a lot of flipping back and forth. I'd prefer to have in flange face and dimensions on the same page even if that means more pages.
3 | Dimensions of facings - other than ring joints |  |  | x |  | Verify with current ANSI/ASTM/ASME standard | See comment above.
4 | Dimensions of ring joint facings | x |  |  |  | Verify with current ANSI/ASTM/ASME standard | This is much easier to read.
5 | API type 6B flanges |  |  | x |  | See API note | Recruited help from another department. Will get feedback by Wed. 4/26.
6 | API type 6BX integral flanges |  |  | x |  | See API note
7 | API type 6BX welding neck flanges |  |  | x |  | See API note
8 | Welding ends for welding neck flanges |  |  | x | x | See API note. Need to improve drawing. Add reference to applicable ASME/ANSI standards (B16.5?) | I really don't like this drawing. It takes me too long to figure out what I am looking at. I'd much rather see both sides of the flange like shown to the right. (www.coastalflange.com/pdf/welding_ends.pdf)
9 | API type 6BX blind and test flanges |  |  | x |  | See API note | Recruited help from another department. Will get feedback by Wed. 4/26.
10 | Test and gage connections for 15,000 LB Christmas trees |  |  | x |  | See API note | Does this really belong here? Anyone messing with a 15,000 lb connection, probably won't be looking at a general engineering handbook.
11 | API type 6B thread flange, counterbore dimensions |  |  | x |  | See API note | Recruited help from another department. Will get feedback by Wed. 4/26.
12 | Cast iron flange dimensions and drilling templates |  |  | x | x | Verify with current ANSI/ASTM/ASME standard | ASME B16.1-2015 update reference. Should we add a note about pressure ratings based on pipe size and temperature? I don't understand the last column, length of machine bolts 25 lb to 125 lb flg. Delete 800 lb cast iron flange page. I don't this is applicable any more. Add AWWA C110-12 ?
13 | Assembly of steel RF flanges to cast iron, brass, bronze or stainless steel | x |  |  |  | Verify with current ANSI/ASTM/ASME standard
API Note - There are many API references. At a minimum they need to be verified and updated. Need to evaluate usefulness (would users seeking API data look at the HI reference or use API references?)
Sub-Section Number | Title | Keep | Delete | Modify | Add | Comments 1 | Comments 2
[5 empty] | x |  | Define NPS (Nominal Pipe Size) inches and DN (Nominal Diameter) mm
[5 empty] | x |  | Add dimensional comparison table of cast iron Class 125 B16.1 to EN 1092-2, PN10.
[5 empty] | x |  | Pipe thread standard ANSI/ASME B1.20.1 (NPT). I believe that this standard does not permit sch 5 and 10 to have pipe thread.
Hydraulics |  |  |  |  | x | Add basic information on pump hydraulics - pump head, suction head/lift, head vs pressure, NPSH
Hydraulics |  |  |  |  | x | Add info on specific speed and suction specific speed
Hydraulics |  |  |  |  | x | Add info on operating pumps in series and in parallel
Hydraulics |  |  |  |  | x | Add info on pump efficiency and wire-to-water efficiency
Hydraulics |  |  |  |  | x | Add info on affinity laws
Regulation |  |  |  |  | x | Add info on DOE regulations
General |  |  |  |  | x | Add info on pump classification
Flanges |  |  |  |  | x | Add tables for flange pressure-temperature ratings such as one from ANSI B16.5.
Flanges |  |  |  |  | x | Add charts for other flange designations? (DIN, JIS, etc.)
Fittings |  |  |  |  | x | Add dimension data of cast iron pipe fittings? (elbows, tees, crosses, etc.)
Fittings |  |  |  |  | x | Add dimension data of weld neck pipe fittings? (elbows, tees, etc.)
All Sections |  |  |  |  | x | Add references to HI standards where more information can be obtained on data provided in the data book
IIID-1 Nozzles |  |  |  |  | x | Add data on calculating flow through orifices and nozzles (see Camerons)

## Pipe-Tube Data
Date last modified: 31-OCT-2023 (J. DAWLEY)
ADDED LINE |  |  | Size and Type Removed/Deleted
Corrections/Changes Highlighted | [39 empty] | Type Of Thread | Type Of Thread | Type Of Thread | Type Of Thread
EDB Section | Section Name | Group | Group Name | Sub-Division | Sub-Division Name | Nominal Size | Nominal Size (DN) | Outside Diameter, inches | Outside Diameter (Min) | Outside Diameter (Max) | Average Outside Diameter Tolerance in. | Identification | Pipe Schedule | Wall Thickness, inches | Pressure Class | Preferred Size | Wall Thickness, in. Min | Wall Thickness, in. Maxc | Min Reinforced Wall Thickness, in. | Wall Thickness Tolerance +/- | Wall Thickness Tolerance, in, all plus | Wall Thickness Tolerance, Average Outside Diameter, all minus | Internal Diameter, inches | Internal Area Square Inches | Internal Diameter, feet | Internal Area, square feet | e/D, Relative Roughness | e, Absolute Roughness, feet | t/D, Ratio of Nominal Wall Thickness to Nominal Outside Diameter | Diameter Roundness Tolerances, percent of outside diameter (Expressed to the nearest 0.001 in. Nearest 0.01 mm. | Diameter Roundness Tolerances, (Expressed to the nearest 0.001 in. Nearest 0.01 mm.) | Out of Roundness Max. & Min. In. (+/-) | Nominal Weight, Threads and Coupling, lb. per ft. | Plain-End Weight lb/ft Nom | Plain-End Weight lb/ft Max | Plain-End Weight lb/100 ft | Types of Ends | Upset Ends, Foe Weld-on Tool Joints | Grade | Short | Long | Buttress | Extreme Line | Form | Type | Maximum Allowable Residue, grams per linear foot | ALLOY | Nominal Composition, Copper, percent | Nominal Composition, Nickel, percent | Reference Page number(s) | Reference Table/figure number | STANDARD 1 | STANDARD 2 | STANDARD 3 | ANSI | ANSI-Sub | ASTM | ASTM-Sub | API | OTHER | TITLE | Footnote 1 | Footnote 2 | Footnote 3 | Note a | Note b | Note c | Note d
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 0.125 |  | 0.405 | 0.374 | 0.42 |  |  | 40 | 0.068 |  |  | 0.06 | -- |  |  |  |  | 0.269 | 0.056832 | 0.022417 | 0.00039467 | 0.00022305 | 5e-06 | [5 empty] | 0.085 | 0.091 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 0.125 |  | 0.405 | 0.374 | 0.42 |  |  | 80 | 0.095 |  |  | 0.083 | -- |  |  |  |  | 0.215 | 0.036305 | 0.017917 | 0.00025212 | 0.00027907 | 5e-06 | [5 empty] | 0.109 | 0.118 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 0.25 |  | 0.54 | 0.509 | 0.555 |  |  | 40 | 0.088 |  |  | 0.077 | -- |  |  |  |  | 0.364 | 0.10406 | 0.030333 | 0.00072265 | 0.00016484 | 5e-06 | [5 empty] | 0.147 | 0.159 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 0.25 |  | 0.54 | 0.509 | 0.555 |  |  | 80 | 0.119 |  |  | 0.104 | -- |  |  |  |  | 0.302 | 0.071631 | 0.025167 | 0.00049744 | 0.00019868 | 5e-06 | [5 empty] | 0.185 | 0.2 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 0.375 |  | 0.675 | 0.644 | 0.69 |  |  | 40 | 0.091 |  |  | 0.08 | -- |  |  |  |  | 0.493 | 0.19089 | 0.041083 | 0.0013256 | 0.0001217 | 5e-06 | [5 empty] | 0.196 | 0.212 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 0.375 |  | 0.675 | 0.644 | 0.69 |  |  | 80 | 0.126 |  |  | 0.11 | -- |  |  |  |  | 0.423 | 0.14053 | 0.03525 | 0.00097591 | 0.00014184 | 5e-06 | [5 empty] | 0.256 | 0.276 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 0.5 |  | 0.84 | 0.809 | 0.855 |  |  | 5 | 0.065 |  |  | 0.053 | 0.077 |  |  |  |  | 0.71 | 0.39592 | 0.059167 | 0.0027494 | 8.4507e-05 | 5e-06 | [5 empty] | 0.186 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 0.5 |  | 0.84 | 0.809 | 0.855 |  |  | 10 | 0.083 |  |  | 0.071 | 0.095 |  |  |  |  | 0.674 | 0.35679 | 0.056167 | 0.0024777 | 8.9021e-05 | 5e-06 | [5 empty] | 0.232 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 0.5 |  | 0.84 | 0.809 | 0.855 |  |  | 40 | 0.109 |  |  | 0.095 | -- |  |  |  |  | 0.622 | 0.30386 | 0.051833 | 0.0021101 | 9.6463e-05 | 5e-06 | [5 empty] | 0.294 | 0.318 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 0.5 |  | 0.84 | 0.809 | 0.855 |  |  | 80 | 0.147 |  |  | 0.129 | -- |  |  |  |  | 0.546 | 0.23414 | 0.0455 | 0.001626 | 0.00010989 | 5e-06 | [5 empty] | 0.376 | 0.406 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 0.5 |  | 0.84 | 0.809 | 0.855 |  |  | 160 | 0.188 |  |  | 0.164 | -- |  |  |  |  | 0.464 | 0.16909 | 0.038667 | 0.0011743 | 0.00012931 | 5e-06 | [5 empty] | 0.453 | 0.489 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 0.75 |  | 1.05 | 1.019 | 1.065 |  |  | 5 | 0.065 |  |  | 0.053 | 0.077 |  |  |  |  | 0.92 | 0.66476 | 0.076667 | 0.0046164 | 6.5217e-05 | 5e-06 | [5 empty] | 0.237 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 0.75 |  | 1.05 | 1.019 | 1.065 |  |  | 10 | 0.083 |  |  | 0.071 | 0.095 |  |  |  |  | 0.884 | 0.61375 | 0.073667 | 0.0042622 | 6.7873e-05 | 5e-06 | [5 empty] | 0.297 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 0.75 |  | 1.05 | 1.019 | 1.065 |  |  | 40 | 0.113 |  |  | 0.099 | -- |  |  |  |  | 0.824 | 0.53327 | 0.068667 | 0.0037032 | 7.2816e-05 | 5e-06 | [5 empty] | 0.391 | 0.422 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 0.75 |  | 1.05 | 1.019 | 1.065 |  |  | 80 | 0.154 |  |  | 0.135 | -- |  |  |  |  | 0.742 | 0.43241 | 0.061833 | 0.0030029 | 8.0863e-05 | 5e-06 | [5 empty] | 0.51 | 0.551 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 0.75 |  | 1.05 | 1.019 | 1.065 |  |  | 160 | 0.219 |  |  | 0.192 | -- |  |  |  |  | 0.612 | 0.29417 | 0.051 | 0.0020428 | 9.8039e-05 | 5e-06 | [5 empty] | 0.672 | 0.726 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 1 |  | 1.315 | 1.284 | 1.33 |  |  | 5 | 0.065 |  |  | 0.053 | 0.077 |  |  |  |  | 1.185 | 1.1029 | 0.09875 | 0.0076589 | 5.0633e-05 | 5e-06 | [5 empty] | 0.3 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 1 |  | 1.315 | 1.284 | 1.33 |  |  | 10 | 0.109 |  |  | 0.095 | 0.123 |  |  |  |  | 1.097 | 0.94516 | 0.091417 | 0.0065636 | 5.4695e-05 | 5e-06 | [5 empty] | 0.486 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 1 |  | 1.315 | 1.284 | 1.33 |  |  | 40 | 0.133 |  |  | 0.116 | -- |  |  |  |  | 1.049 | 0.86425 | 0.087417 | 0.0060018 | 5.7197e-05 | 5e-06 | [5 empty] | 0.581 | 0.627 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 1 |  | 1.315 | 1.284 | 1.33 |  |  | 80 | 0.179 |  |  | 0.157 | -- |  |  |  |  | 0.957 | 0.71931 | 0.07975 | 0.0049952 | 6.2696e-05 | 5e-06 | [5 empty] | 0.751 | 0.811 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 1 |  | 1.315 | 1.284 | 1.33 |  |  | 160 | 0.25 |  |  | 0.219 | -- |  |  |  |  | 0.815 | 0.52168 | 0.067917 | 0.0036228 | 7.362e-05 | 5e-06 | [5 empty] | 0.984 | 1.062 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 1.25 |  | 1.66 | 1.629 | 1.675 |  |  | 5 | 0.065 |  |  | 0.053 | 0.077 |  |  |  |  | 1.53 | 1.8385 | 0.1275 | 0.012768 | 3.9216e-05 | 5e-06 | [5 empty] | 0.383 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 1.25 |  | 1.66 | 1.629 | 1.675 |  |  | 10 | 0.109 |  |  | 0.095 | 0.123 |  |  |  |  | 1.442 | 1.6331 | 0.12017 | 0.011341 | 4.1609e-05 | 5e-06 | [5 empty] | 0.625 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 1.25 |  | 1.66 | 1.629 | 1.675 |  |  | 40 | 0.14 |  |  | 0.122 | -- |  |  |  |  | 1.38 | 1.4957 | 0.115 | 0.010387 | 4.3478e-05 | 5e-06 | [5 empty] | 0.786 | 0.849 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 1.25 |  | 1.66 | 1.629 | 1.675 |  |  | 80 | 0.191 |  |  | 0.167 | -- |  |  |  |  | 1.278 | 1.2828 | 0.1065 | 0.0089082 | 4.6948e-05 | 5e-06 | [5 empty] | 1.037 | 1.12 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 1.25 |  | 1.66 | 1.629 | 1.675 |  |  | 160 | 0.25 |  |  | 0.219 | -- |  |  |  |  | 1.16 | 1.0568 | 0.096667 | 0.0073391 | 5.1724e-05 | 5e-06 | [5 empty] | 1.302 | 1.407 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 1.5 |  | 1.9 | 1.869 | 1.915 |  |  | 5 | 0.065 |  |  | 0.053 | 0.077 |  |  |  |  | 1.77 | 2.4606 | 0.1475 | 0.017087 | 3.3898e-05 | 5e-06 | [5 empty] | 0.41 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 1.5 |  | 1.9 | 1.869 | 1.915 |  |  | 10 | 0.109 |  |  | 0.095 | 0.123 |  |  |  |  | 1.682 | 2.222 | 0.14017 | 0.01543 | 3.5672e-05 | 5e-06 | [5 empty] | 0.721 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 1.5 |  | 1.9 | 1.869 | 1.915 |  |  | 40 | 0.145 |  |  | 0.127 | -- |  |  |  |  | 1.61 | 2.0358 | 0.13417 | 0.014138 | 3.7267e-05 | 5e-06 | [5 empty] | 0.94 | 1.015 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 1.5 |  | 1.9 | 1.869 | 1.915 |  |  | 80 | 0.2 |  |  | 0.175 | -- |  |  |  |  | 1.5 | 1.7671 | 0.125 | 0.012272 | 4e-05 | 5e-06 | [5 empty] | 1.256 | 1.357 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 1.5 |  | 1.9 | 1.869 | 1.915 |  |  | 160 | 0.281 |  |  | 0.246 | -- |  |  |  |  | 1.338 | 1.4061 | 0.1115 | 0.0097643 | 4.4843e-05 | 5e-06 | [5 empty] | 1.681 | 1.815 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 2 |  | 2.375 | 2.344 | 2.406 |  |  | 5 | 0.065 |  |  | 0.053 | 0.077 |  |  |  |  | 2.245 | 3.9584 | 0.18708 | 0.027489 | 2.6726e-05 | 5e-06 | [5 empty] | 0.555 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 2 |  | 2.375 | 2.344 | 2.406 |  |  | 10 | 0.109 |  |  | 0.095 | 0.123 |  |  |  |  | 2.157 | 3.6542 | 0.17975 | 0.025376 | 2.7816e-05 | 5e-06 | [5 empty] | 0.913 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 2 |  | 2.375 | 2.351 | 2.399 |  |  | 40 | 0.154 |  |  | 0.135 | -- |  |  |  |  | 2.067 | 3.3556 | 0.17225 | 0.023303 | 2.9028e-05 | 5e-06 | [5 empty] | 1.264 | 1.365 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 2 |  | 2.375 | 2.351 | 2.399 |  |  | 80 | 0.218 |  |  | 0.191 | -- |  |  |  |  | 1.939 | 2.9529 | 0.16158 | 0.020506 | 3.0944e-05 | 5e-06 | [5 empty] | 1.737 | 1.876 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 2 |  | 2.375 | 2.351 | 2.399 |  |  | 160 | 0.344 |  |  | 0.301 | -- |  |  |  |  | 1.687 | 2.2352 | 0.14058 | 0.015522 | 3.5566e-05 | 5e-06 | [5 empty] | 2.581 | 2.788 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 2.5 |  | 2.375 | 2.844 | 2.906 |  |  | 5 | 0.083 |  |  | 0.071 | 0.095 |  |  |  |  | 2.209 | 3.8325 | 0.18408 | 0.026615 | 2.7162e-05 | 5e-06 | [5 empty] | 0.856 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 2.5 |  | 2.375 | 2.844 | 2.906 |  |  | 10 | 0.12 |  |  | 0.105 | 0.135 |  |  |  |  | 2.135 | 3.58 | 0.17792 | 0.024861 | 2.8103e-05 | 5e-06 | [5 empty] | 1.221 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 2.5 |  | 2.375 | 2.846 | 2.904 |  |  | 40 | 0.203 |  |  | 0.178 | -- |  |  |  |  | 1.969 | 3.045 | 0.16408 | 0.021146 | 3.0472e-05 | 5e-06 | [5 empty] | 2.004 | 2.164 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 2.5 |  | 2.375 | 2.846 | 2.904 |  |  | 80 | 0.276 |  |  | 0.242 | -- |  |  |  |  | 1.823 | 2.6101 | 0.15192 | 0.018126 | 3.2913e-05 | 5e-06 | [5 empty] | 2.65 | 2.862 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 2.5 |  | 2.375 | 2.846 | 2.904 |  |  | 160 | 0.375 |  |  | 0.328 | -- |  |  |  |  | 1.625 | 2.0739 | 0.13542 | 0.014402 | 3.6923e-05 | 5e-06 | [5 empty] | 3.464 | 3.741 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 3 |  | 3.5 | 3.469 | 3.531 |  |  | 5 | 0.083 |  |  | 0.071 | 0.095 |  |  |  |  | 3.334 | 8.7301 | 0.27783 | 0.060626 | 1.7996e-05 | 5e-06 | [5 empty] | 1.048 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 3 |  | 3.5 | 3.469 | 3.531 |  |  | 10 | 0.12 |  |  | 0.105 | 0.135 |  |  |  |  | 3.26 | 8.3469 | 0.27167 | 0.057965 | 1.8405e-05 | 5e-06 | [5 empty] | 1.498 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 3 |  | 3.5 | 3.465 | 3.535 |  |  | 40 | 0.216 |  |  | 0.189 | -- |  |  |  |  | 3.068 | 7.3927 | 0.25567 | 0.051338 | 1.9557e-05 | 5e-06 | [5 empty] | 2.621 | 0.283 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 3 |  | 3.5 | 3.465 | 3.535 |  |  | 80 | 0.3 |  |  | 0.262 | -- |  |  |  |  | 2.9 | 6.6052 | 0.24167 | 0.045869 | 2.069e-05 | 5e-06 | [5 empty] | 3.547 | 3.83 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 3 |  | 3.5 | 3.465 | 3.535 |  |  | 160 | 0.438 |  |  | 0.383 | -- |  |  |  |  | 2.624 | 5.4078 | 0.21867 | 0.037554 | 2.2866e-05 | 5e-06 | [5 empty] | 4.955 | 5.351 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 3.5 |  | 4 | 3.969 | 4.031 |  |  | 5 | 0.083 |  |  | 0.071 | 0.095 |  |  |  |  | 3.834 | 11.545 | 0.3195 | 0.080174 | 1.5649e-05 | 5e-06 | [5 empty] | 1.201 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 3.5 |  | 4 | 3.969 | 4.031 |  |  | 10 | 0.12 |  |  | 0.105 | 0.135 |  |  |  |  | 3.76 | 11.1036 | 0.31333 | 0.077109 | 1.5957e-05 | 5e-06 | [5 empty] | 1.72 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 3.5 |  | 4 | 3.96 | 4.04 |  |  | 40 | 0.226 |  |  | 0.198 | -- |  |  |  |  | 3.548 | 9.8868 | 0.29567 | 0.068659 | 1.6911e-05 | 5e-06 | [5 empty] | 3.151 | 3.403 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 3.5 |  | 4 | 3.96 | 4.04 |  |  | 80 | 0.318 |  |  | 0.278 | -- |  |  |  |  | 3.364 | 8.888 | 0.28033 | 0.061722 | 1.7836e-05 | 5e-06 | [5 empty] | 4.326 | 4.672 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 4 | 100 | 4.5 |  |  |  |  | 5 | 0.083 | [8 empty] | 4.334 | 14.7526 | 0.36117 | 0.10245 | 1.3844e-05 | 5e-06 | [5 empty] | 1.354 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 4 | 100 | 4.5 |  |  |  |  | 10 | 0.12 | [8 empty] | 4.26 | 14.2531 | 0.355 | 0.09898 | 1.4085e-05 | 5e-06 | [5 empty] | 3.733 | 4.031 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 4 | 100 | 4.5 |  |  |  |  | 40 | 0.237 | [8 empty] | 4.026 | 12.7303 | 0.3355 | 0.088405 | 1.4903e-05 | 5e-06 | [5 empty] | 9.353 | 10.1 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 4 | 100 | 4.5 |  |  |  |  | 80 | 0.337 | [8 empty] | 3.826 | 11.4969 | 0.31883 | 0.079839 | 1.5682e-05 | 5e-06 | [5 empty] | 6.564 | 7.089 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 4 | 100 | 4.5 |  |  |  |  | 120 | 0.438 | [8 empty] | 3.624 | 10.3149 | 0.302 | 0.071631 | 1.6556e-05 | 5e-06 | [5 empty] | 9.884 | 10.67 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 4 | 100 | 4.5 |  |  |  |  | 160 | 0.531 | [8 empty] | 3.438 | 9.2833 | 0.2865 | 0.064467 | 1.7452e-05 | 5e-06 | [5 empty] | 12.59 | 13.6 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 5 | 125 | 5.563 |  |  |  |  | 5 | 0.109 | [8 empty] | 5.345 | 22.4381 | 0.44542 | 0.15582 | 1.1225e-05 | 5e-06 | [5 empty] | 4.635 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 5 | 125 | 5.563 |  |  |  |  | 10 | 0.134 | [8 empty] | 5.295 | 22.0202 | 0.44125 | 0.15292 | 1.1331e-05 | 5e-06 | [5 empty] | 8.543 | 9.227 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 5 | 125 | 5.563 |  |  |  | STD | 40 | 0.258 | [8 empty] | 5.047 | 20.0058 | 0.42058 | 0.13893 | 1.1888e-05 | 5e-06 | [5 empty] | 17.62 | 19.03 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 5 | 125 | 5.563 |  |  |  | XS | 80 | 0.375 | [8 empty] | 4.813 | 18.1937 | 0.40108 | 0.12635 | 1.2466e-05 | 5e-06 | [5 empty] | 5.256 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 5 | 125 | 5.563 |  |  |  |  | 120 | 0.5 | [8 empty] | 4.563 | 16.3528 | 0.38025 | 0.11356 | 1.3149e-05 | 5e-06 | [5 empty] | 6.453 | -- | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 5 | 125 | 5.563 |  |  |  |  | 160 | 0.625 | [8 empty] | 4.313 | 14.61 | 0.35942 | 0.10146 | 1.3911e-05 | 5e-06 | [5 empty] | 9.698 | 10.47 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 6 | 150 | 6.625 |  |  |  |  | 5 | 0.109 | [8 empty] | 6.407 | 32.2403 | 0.53392 | 0.22389 | 9.3648e-06 | 5e-06 | [5 empty] | 18.93 | 20.45 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 6 | 150 | 6.625 |  |  |  |  | 10 | 0.134 | [8 empty] | 6.357 | 31.7391 | 0.52975 | 0.22041 | 9.4384e-06 | 5e-06 | [5 empty] | 26.65 | 28.78 | [14 empty] | Page 45-46 | TABLE 12.55 | ANSI H35.2-2017 | ANSI H35.2M-2017 |  | ANSI H35.2 | [9 empty] | Schedule 40 is also designated "standard" pipe and schedule 80 is also designated as "extra heavy" pipe. | For schedules 5 and 10 these values apply to mean outside diameter. | For schedules other than 5 and 10, maximum wall thickness is controlled by weight tolerance. | Based on a density of 0.098 lb per cu in. the density of 6061 and 6063 alloys, and on nominal dimensions and plain ends. For 3003 alloy multiply b 1.01 for 5083, 5086, and 5456 alloys multiply by 0.098; for 5454 alloy multiply by 0.099.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 6 | 150 | 6.625 |  |  |  | STD | 40 | 0.28 | [5 empty] | 0.004 |  |  | 6.065 | 28.8903 | 0.50542 | 0.20063 | 9.8928e-06 | 5e-06 | [5 empty] | 0.259 | [15 empty] | Page 4 | Table 3 | ANSI H35.2-2017
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 6 | 150 | 6.625 |  |  |  | XS | 80 | 0.432 | [5 empty] | 0.006 |  |  | 5.761 | 26.0667 | 0.48008 | 0.18102 | 1.0415e-05 | 5e-06 | [5 empty] | 1.3 | [15 empty] | Page 4 | Table 3 | ANSI H35.2-2017 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 6 | 150 | 6.625 |  |  |  |  | 120 | 0.562 | [5 empty] | 0.008 |  |  | 5.501 | 23.7669 | 0.45842 | 0.16505 | 1.0907e-05 | 5e-06 | [5 empty] | 2.69 | [15 empty] | Page 4 | Table 3 | ANSI H35.2-2017 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 6 | 150 | 6.625 |  |  |  |  | 160 | 0.719 | [5 empty] | 0.009 |  |  | 5.187 | 21.1311 | 0.43225 | 0.14674 | 1.1567e-05 | 5e-06 | [5 empty] | 4.22 | [15 empty] | Page 4 | Table 3 | ANSI H35.2-2017 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 8 | 200 | 8.625 |  |  |  |  | 5 | 0.109 | [5 empty] | 0.014 |  |  | 8.407 | 55.5101 | 0.70058 | 0.38549 | 7.1369e-06 | 5e-06 | [5 empty] | 12.9 | [15 empty] | Page 4 | Table 3 | ANSI H35.2-2017 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 8 | 200 | 8.625 |  |  |  |  | 10 | 0.148 | [5 empty] | 0.014 |  |  | 8.329 | 54.4848 | 0.69408 | 0.37837 | 7.2037e-06 | 5e-06 | [5 empty] | 19.4 | [15 empty] | Page 4 | Table 3 | ANSI H35.2-2017 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 8 | 200 | 8.625 |  |  |  |  | 20 | 0.25 | [5 empty] | 0.007 |  |  | 8.125 | 51.8486 | 0.67708 | 0.36006 | 7.3846e-06 | 5e-06 | [5 empty] | 0.625 | [15 empty] | Page 4 | Table 3 | ANSI H35.2-2017 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 8 | 200 | 8.625 |  |  |  | STD | 40 | 0.322 | [5 empty] | 0.009 |  |  | 7.981 | 50.027 | 0.66508 | 0.34741 | 7.5179e-06 | 5e-06 | [5 empty] | 1.71 | [15 empty] | Page 4 | Table 3 | ANSI H35.2-2017 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 8 | 200 | 8.625 |  |  |  |  | 60 | 0.406 | [5 empty] | 0.011 |  |  | 7.813 | 47.943 | 0.65108 | 0.33294 | 7.6795e-06 | 5e-06 | [5 empty] | 4.19 | [15 empty] | Page 4 | Table 3 | ANSI H35.2-2017 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 8 | 200 | 8.625 |  |  |  | XS | 80 | 0.5 | [5 empty] | 0.015 |  |  | 7.625 | 45.6635 | 0.63542 | 0.31711 | 7.8689e-06 | 5e-06 | [5 empty] | 8.85 | [15 empty] | Page 4 | Table 3 | ANSI H35.2-2017 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 8 | 200 | 8.625 |  |  |  |  | 100 | 0.594 | [5 empty] | 0.017 |  |  | 7.437 | 43.4396 | 0.61975 | 0.30166 | 8.0678e-06 | 5e-06 | [5 empty] | 14.4 | [15 empty] | Page 4 | Table 3 | ANSI H35.2-2017 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 8 | 200 | 8.625 |  |  |  |  | 120 | 0.719 | [5 empty] | 0.019 |  |  | 7.187 | 40.5681 | 0.59892 | 0.28172 | 8.3484e-06 | 5e-06 | [5 empty] | 23.7 | [15 empty] | Page 4 | Table 3 | ANSI H35.2-2017 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 8 | 200 | 8.625 |  |  |  |  | 140 | 0.812 | [5 empty] | 0.035 |  |  | 7.001 | 38.4955 | 0.58342 | 0.26733 | 8.5702e-06 | 5e-06 | [5 empty] | 49.5 | [15 empty] | Page 4 | Table 3 | ANSI H35.2-2017 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 8 | 200 | 8.625 |  |  |  |  | 160 | 0.906 | [5 empty] | - |  |  | 6.813 | 36.4558 | 0.56775 | 0.25317 | 8.8067e-06 | 5e-06 | [5 empty] | Not available in this size | [15 empty] | Page 4 | Table 3 | ANSI H35.2-2017 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 10 | 250 | 10.75 |  |  |  |  | 5 | 0.134 | [5 empty] | 0.005 |  |  | 10.482 | 86.2935 | 0.8735 | 0.59926 | 5.7241e-06 | 5e-06 | [5 empty] | 0.447 | [15 empty] | Page 2 | Table 1 | ANSI H35.2-2017 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 10 | 250 | 10.75 |  |  |  |  | 10 | 0.165 | [5 empty] | 0.006 |  |  | 10.42 | 85.2757 | 0.86833 | 0.59219 | 5.7582e-06 | 5e-06 | [5 empty] | 0.934 | [15 empty] | Page 2 | Table 1 | ANSI H35.2-2017 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 10 | 250 | 10.75 |  |  |  |  | 20 | 0.25 | [5 empty] | 0.008 |  |  | 10.25 | 82.5159 | 0.85417 | 0.57303 | 5.8537e-06 | 5e-06 | [5 empty] | 3.13 | [15 empty] | Page 2 | Table 1 | ANSI H35.2-2017 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 10 | 250 | 10.75 |  |  |  |  | 30 | 0.307 | [5 empty] | 0.01 |  |  | 10.136 | 80.6906 | 0.84467 | 0.56035 | 5.9195e-06 | 5e-06 | [5 empty] | 5.99 | [15 empty] | Page 2 | Table 1 | ANSI H35.2-2017 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 10 | 250 | 10.75 |  |  |  | STD | 40 | 0.365 | [5 empty] | 0.013 |  |  | 10.02 | 78.8543 | 0.835 | 0.5476 | 5.988e-06 | 5e-06 | [5 empty] | 11.2 | [15 empty] | Page 2 | Table 1 | ANSI H35.2-2017 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 10 | 250 | 10.75 |  |  |  | XS | 60 | 0.5 | [5 empty] | 0.014 |  |  | 9.75 | 74.6619 | 0.8125 | 0.51849 | 6.1538e-06 | 5e-06 | [5 empty] | 15.8 | [15 empty] | Page 2 | Table 1 | ANSI H35.2-2017 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 10 | 250 | 10.75 |  |  |  |  | 80 | 0.594 | [5 empty] | 0.022 |  |  | 9.562 | 71.8104 | 0.79683 | 0.49868 | 6.2748e-06 | 5e-06 | [5 empty] | 30.9 | [15 empty] | Page 2 | Table 1 | ANSI H35.2-2017 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 10 | 250 | 10.75 |  |  |  |  | 100 | 0.719 | [5 empty] | 0.03 |  |  | 9.312 | 68.1045 | 0.776 | 0.47295 | 6.4433e-06 | 5e-06 | [5 empty] | 55.3 | [15 empty] | Page 2 | Table 1 | ANSI H35.2-2017 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 12 | 300 | 12.75 |  |  |  |  | 5 | 0.156 | [5 empty] | 0.011 |  |  | 12.438 | 121.5041 | 1.0365 | 0.84378 | 4.8239e-06 | 5e-06 | [5 empty] | 4.1 | [15 empty] | Page 2 | Table 1 | ANSI H35.2-2017 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 12 | 300 | 12.75 |  |  |  |  | 10 | 0.18 | [5 empty] | 0.015 |  |  | 12.39 | 120.5681 | 1.0325 | 0.83728 | 4.8426e-06 | 5e-06 | [5 empty] | 8.66 | [15 empty] | Page 2 | Table 1 | ANSI H35.2-2017 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 12 | 300 | 12.75 |  |  |  |  | 20 | 0.25 | [5 empty] | 0.019 |  |  | 12.25 | 117.8588 | 1.0208 | 0.81846 | 4.898e-06 | 5e-06 | [5 empty] | 23.2 | [15 empty] | Page 2 | Table 1 | ANSI H35.2-2017 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 12 | 300 | 12.75 |  |  |  |  | 30 | 0.33 | [5 empty] | 0.04 |  |  | 12.09 | 114.8002 | 1.0075 | 0.79722 | 4.9628e-06 | 5e-06 | [5 empty] | 61.1 | [15 empty] | Page 2 | Table 1 | ANSI H35.2-2017 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 12 | 300 | 12.75 |  |  |  |  | 40 | 0.406 | [5 empty] | 0.004 |  | 0.004 | 11.938 | 111.9317 | 0.99483 | 0.7773 | 5.026e-06 | 5e-06 | 0.031843 | 0.01 | 0.1275 |  |  |  | 0.483 | [14 empty] | Page 2 | Table 1 | ANSI H35.2-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 12 | 300 | 12.75 |  |  |  |  | 60 | 0.562 | [5 empty] | 0.004 |  | 0.005 | 11.626 | 106.1575 | 0.96883 | 0.7372 | 5.1608e-06 | 5e-06 | 0.044078 | 0.01 | 0.1275 |  |  |  | 0.989 | [14 empty] | Page 2 | Table 1 | ANSI H35.2-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 1 | Aluminum alloy pipe - extruded | 12 | 300 | 12.75 |  |  |  |  | 80 | 0.688 | [5 empty] | 0.004 |  | 0.006 | 11.374 | 101.6053 | 0.94783 | 0.70559 | 5.2752e-06 | 5e-06 | 0.053961 | 0.008 | 0.102 |  |  |  | 1.45 | [14 empty] | Page 2 | Table 1 | ANSI H35.2-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 0.125 |  | 0.405 | 0.401 | 0.405 |  |  |  | 0.062 | Regular |  |  |  |  | 0.004 |  |  | 0.281 | 0.062016 | 0.023417 | 0.00043067 | 0.00021352 | 5e-06 | [5 empty] | 0.253 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 0.125 |  | 0.405 | 0.401 | 0.405 |  |  |  | 0.1 | Extra Strong |  |  |  |  | 0.006 |  |  | 0.205 | 0.033006 | 0.017083 | 0.00022921 | 0.00029268 | 5e-06 | [5 empty] | 0.363 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 0.25 |  | 0.54 | 0.536 | 0.54 |  |  |  | 0.082 | Regular |  |  |  |  | 0.005 |  |  | 0.376 | 0.11104 | 0.031333 | 0.00077109 | 0.00015957 | 5e-06 | [5 empty] | 0.447 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 0.25 |  | 0.54 | 0.536 | 0.54 |  |  |  | 0.123 | Extra Strong |  |  |  |  | 0.007 |  |  | 0.294 | 0.067887 | 0.0245 | 0.00047144 | 0.00020408 | 5e-06 | [5 empty] | 0.611 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 0.375 |  | 0.675 | 0.67 | 0.675 |  |  |  | 0.09 | Regular |  |  |  |  | 0.005 |  |  | 0.495 | 0.19244 | 0.04125 | 0.0013364 | 0.00012121 | 5e-06 | [5 empty] | 0.627 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 0.375 |  | 0.675 | 0.67 | 0.675 |  |  |  | 0.127 | Extra Strong |  |  |  |  | 0.007 |  |  | 0.421 | 0.1392 | 0.035083 | 0.0009667 | 0.00014252 | 5e-06 | [5 empty] | 0.829 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 0.5 |  | 0.84 | 0.835 | 0.84 |  |  |  | 0.107 | Regular |  |  |  |  | 0.006 |  |  | 0.626 | 0.30778 | 0.052167 | 0.0021374 | 9.5847e-05 | 5e-06 | [5 empty] | 0.934 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 0.5 |  | 0.84 | 0.835 | 0.84 |  |  |  | 0.149 | Extra Strong |  |  |  |  | 0.008 |  |  | 0.542 | 0.23072 | 0.045167 | 0.0016022 | 0.0001107 | 5e-06 | [5 empty] | 1.23 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 0.75 |  | 1.05 | 1.044 | 1.05 |  |  |  | 0.114 | Regular |  |  |  |  | 0.006 |  |  | 0.822 | 0.53068 | 0.0685 | 0.0036853 | 7.2993e-05 | 5e-06 | [5 empty] | 1.27 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 0.75 |  | 1.05 | 1.044 | 1.05 |  |  |  | 0.157 | Extra Strong |  |  |  |  | 0.009 |  |  | 0.736 | 0.42545 | 0.061333 | 0.0029545 | 8.1522e-05 | 5e-06 | [5 empty] | 1.67 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 1 |  | 1.315 | 1.309 | 1.315 |  |  |  | 0.126 | Regular |  |  |  |  | 0.007 |  |  | 1.063 | 0.88748 | 0.088583 | 0.006163 | 5.6444e-05 | 5e-06 | [5 empty] | 1.78 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 1 |  | 1.315 | 1.309 | 1.315 |  |  |  | 0.182 | Extra Strong |  |  |  |  | 0.01 |  |  | 0.951 | 0.71031 | 0.07925 | 0.0049327 | 6.3091e-05 | 5e-06 | [5 empty] | 2.46 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 1.25 |  | 1.66 | 1.654 | 1.66 |  |  |  | 0.146 | Regular |  |  |  |  | 0.008 |  |  | 1.368 | 1.4698 | 0.114 | 0.010207 | 4.386e-05 | 5e-06 | [5 empty] | 2.63 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 1.25 |  | 1.66 | 1.654 | 1.66 |  |  |  | 0.194 | Extra Strong |  |  |  |  | 0.01 |  |  | 1.272 | 1.2708 | 0.106 | 0.0088247 | 4.717e-05 | 5e-06 | [5 empty] | 3.39 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 1.5 |  | 1.9 | 1.894 | 1.9 |  |  |  | 0.15 | Regular |  |  |  |  | 0.008 |  |  | 1.6 | 2.0106 | 0.13333 | 0.013963 | 3.75e-05 | 5e-06 | [5 empty] | 3.13 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 1.5 |  | 1.9 | 1.894 | 1.9 |  |  |  | 0.203 | Extra Strong |  |  |  |  | 0.011 |  |  | 1.494 | 1.753 | 0.1245 | 0.012174 | 4.0161e-05 | 5e-06 | [5 empty] | 4.1 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 2 |  | 2.375 | 2.367 | 2.375 |  |  |  | 0.156 | Regular |  |  |  |  | 0.009 |  |  | 2.063 | 3.3426 | 0.17192 | 0.023213 | 2.9084e-05 | 5e-06 | [5 empty] | 4.12 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 2 |  | 2.375 | 2.367 | 2.375 |  |  |  | 0.221 | Extra Strong |  |  |  |  | 0.012 |  |  | 1.933 | 2.9346 | 0.16108 | 0.020379 | 3.104e-05 | 5e-06 | [5 empty] | 5.67 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 2.5 |  | 2.875 | 2.867 | 2.875 |  |  |  | 0.187 | Regular |  |  |  |  | 0.01 |  |  | 2.501 | 4.9127 | 0.20842 | 0.034116 | 2.399e-05 | 5e-06 | [5 empty] | 5.99 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 2.5 |  | 2.875 | 2.867 | 2.875 |  |  |  | 0.28 | Extra Strong |  |  |  |  | 0.015 |  |  | 2.315 | 4.2091 | 0.19292 | 0.02923 | 2.5918e-05 | 5e-06 | [5 empty] | 8.66 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 3 |  | 3.5 | 3.49 | 3.5 |  |  |  | 0.219 | Regular |  |  |  |  | 0.012 |  |  | 3.062 | 7.3638 | 0.25517 | 0.051137 | 1.9595e-05 | 5e-06 | [5 empty] | 8.56 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 3 |  | 3.5 | 3.49 | 3.5 |  |  |  | 0.304 | Extra Strong |  |  |  |  | 0.016 |  |  | 2.892 | 6.5688 | 0.241 | 0.045617 | 2.0747e-05 | 5e-06 | [5 empty] | 11.6 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 3.5 |  | 4 | 3.99 | 4 |  |  |  | 0.25 | Regular |  |  |  |  | 0.013 |  |  | 3.5 | 9.6211 | 0.29167 | 0.066813 | 1.7143e-05 | 5e-06 | [5 empty] | 11.2 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 3.5 |  | 4 | 3.99 | 4 |  |  |  | 0.321 | Extra Strong |  |  |  |  | 0.017 |  |  | 3.358 | 8.8563 | 0.27983 | 0.061502 | 1.7868e-05 | 5e-06 | [5 empty] | 14.1 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 4 |  | 4.5 | 4.488 | 4.5 |  |  |  | 0.25 | Regular |  |  |  |  | 0.014 |  |  | 4 | 12.5664 | 0.33333 | 0.087266 | 1.5e-05 | 5e-06 | [5 empty] | 12.7 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 4 |  | 4.5 | 4.488 | 4.5 |  |  |  | 0.341 | Extra Strong |  |  |  |  | 0.018 |  |  | 3.818 | 11.4488 | 0.31817 | 0.079506 | 1.5715e-05 | 5e-06 | [5 empty] | 16.9 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 5 |  | 5.562 | 5.548 | 5.562 |  |  |  | 0.25 | Regular |  |  |  |  | 0.014 |  |  | 5.062 | 20.1249 | 0.42183 | 0.13976 | 1.1853e-05 | 5e-06 | [5 empty] | 15.8 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 5 |  | 5.562 | 5.548 | 5.562 |  |  |  | 0.375 | Extra Strong |  |  |  |  | 0.019 |  |  | 4.812 | 18.1862 | 0.401 | 0.12629 | 1.2469e-05 | 5e-06 | [5 empty] | 23.2 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 6 |  | 6.625 | 6.609 | 6.625 |  |  |  | 0.25 | Regular |  |  |  |  | 0.014 |  |  | 6.125 | 29.4647 | 0.51042 | 0.20462 | 9.7959e-06 | 5e-06 | [5 empty] | 19 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 6 |  | 6.625 | 6.609 | 6.625 |  |  |  | 0.437 | Extra Strong |  |  |  |  | 0.027 |  |  | 5.751 | 25.9763 | 0.47925 | 0.18039 | 1.0433e-05 | 5e-06 | [5 empty] | 32.2 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 8 |  | 8.625 | 8.605 | 8.625 |  |  |  | 0.312 | Regular |  |  |  |  | 0.022 |  |  | 8.001 | 50.278 | 0.66675 | 0.34915 | 7.4991e-06 | 5e-06 | [5 empty] | 30.9 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 8 |  | 8.625 | 8.605 | 8.625 |  |  |  | 0.5 | Extra Strong |  |  |  |  | 0.035 |  |  | 7.625 | 45.6635 | 0.63542 | 0.31711 | 7.8689e-06 | 5e-06 | [5 empty] | 48.4 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 10 |  | 10.75 | 10.728 | 10.75 |  |  |  | 0.365 | Regular |  |  |  |  | 0.03 |  |  | 10.02 | 78.8543 | 0.835 | 0.5476 | 5.988e-06 | 5e-06 | [5 empty] | 45.2 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 10 |  | 10.75 | 10.728 | 10.75 |  |  |  | 0.5 | Extra Strong |  |  |  |  | 0.04 |  |  | 9.75 | 74.6619 | 0.8125 | 0.51849 | 6.1538e-06 | 5e-06 | [5 empty] | 61.1 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 12 |  | 12.75 | 12.726 | 12.75 |  |  |  | 0.375 | Regular |  |  |  |  | 0.03 |  |  | 12 | 113.0973 | 1 | 0.7854 | 5e-06 | 5e-06 | [5 empty] | 55.3 | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Brass (red brass) pipe - seamless | 12 |  | 12.75 | 12.726 | 12.75 |  |  |  | - | Extra Strong |  |  |  |  | - |  |  | Not an available size | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5e-06 | [5 empty] | Not an available size | [15 empty] | Page 2 | Table 1 | ASTM B43-20 |  |  |  |  | ASTM B43-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.072 |  | 0.072 | [5 empty] | 0.023 | [8 empty] | 0.026 | 0.00053093 | 0.0021667 | 3.687e-06 | 0.0023077 | 5e-06 | [5 empty] | 0.01373 | [11 empty] | 0.0002 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.072 |  | 0.072 | [5 empty] | 0.022 | [8 empty] | 0.028 | 0.00061575 | 0.0023333 | 4.2761e-06 | 0.0021429 | 5e-06 | [5 empty] | 0.134 | [11 empty] | 0.00021 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.081 |  | 0.081 | [5 empty] | 0.025 | [8 empty] | 0.031 | 0.00075477 | 0.0025833 | 5.2414e-06 | 0.0019355 | 5e-06 | [5 empty] | 0.01705 | [11 empty] | 0.00023 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.081 |  | 0.081 | [5 empty] | 0.024 | [8 empty] | 0.033 | 0.0008553 | 0.00275 | 5.9396e-06 | 0.0018182 | 5e-06 | [5 empty] | 0.01666 | [11 empty] | 0.00025 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.087 |  | 0.087 | [5 empty] | 0.0255 | [8 empty] | 0.036 | 0.0010179 | 0.003 | 7.0686e-06 | 0.0016667 | 5e-06 | [5 empty] | 0.0191 | [11 empty] | 0.00027 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.087 |  | 0.087 | [5 empty] | 0.024 | [8 empty] | 0.039 | 0.0011946 | 0.00325 | 8.2958e-06 | 0.0015385 | 5e-06 | [5 empty] | 0.01842 | [11 empty] | 0.00029 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.093 |  | 0.093 | [5 empty] | 0.0255 | [8 empty] | 0.042 | 0.0013854 | 0.0035 | 9.6211e-06 | 0.0014286 | 5e-06 | [5 empty] | 0.02096 | [11 empty] | 0.00032 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.097 |  | 0.097 | [5 empty] | 0.025 | [8 empty] | 0.046 | 0.0016619 | 0.0038333 | 1.1541e-05 | 0.0013043 | 5e-06 | [5 empty] | 0.02221 | [11 empty] | 0.00035 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.099 |  | 0.099 | [5 empty] | 0.025 | [8 empty] | 0.049 | 0.0018857 | 0.0040833 | 1.3095e-05 | 0.0012245 | 5e-06 | [5 empty] | 0.02253 | [11 empty] | 0.00037 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.106 |  | 0.106 | [5 empty] | 0.026 | [8 empty] | 0.054 | 0.0022902 | 0.0045 | 1.5904e-05 | 0.0011111 | 5e-06 | [5 empty] | 0.02533 | [11 empty] | 0.00041 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.112 |  | 0.112 | [5 empty] | 0.0265 | [8 empty] | 0.059 | 0.002734 | 0.0049167 | 1.8986e-05 | 0.0010169 | 5e-06 | [5 empty] | 0.0276 | [11 empty] | 0.00044 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.125 |  | 0.125 | [5 empty] | 0.0305 | [8 empty] | 0.064 | 0.003217 | 0.0053333 | 2.234e-05 | 0.0009375 | 5e-06 | [5 empty] | 0.03511 | [11 empty] | 0.00048 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.125 |  | 0.125 | [5 empty] | 0.0275 | [8 empty] | 0.07 | 0.0038485 | 0.0058333 | 2.6725e-05 | 0.00085714 | 5e-06 | [5 empty] | 0.03266 | [11 empty] | 0.00053 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.125 |  | 0.125 | [5 empty] | 0.025 | [8 empty] | 0.075 | 0.0044179 | 0.00625 | 3.068e-05 | 0.0008 | 5e-06 | [5 empty] | 0.03045 | [11 empty] | 0.00057 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.145 |  | 0.145 | [5 empty] | 0.0325 | [8 empty] | 0.08 | 0.0050265 | 0.0066667 | 3.4907e-05 | 0.00075 | 5e-06 | [5 empty] | 0.04453 | [11 empty] | 0.0006 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.145 |  | 0.145 | [5 empty] | 0.03 | [8 empty] | 0.085 | 0.0056745 | 0.0070833 | 3.9406e-05 | 0.00070588 | 5e-06 | [5 empty] | 0.04202 | [11 empty] | 0.00064 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.145 |  | 0.145 | [5 empty] | 0.0275 | [8 empty] | 0.09 | 0.0063617 | 0.0075 | 4.4179e-05 | 0.00066667 | 5e-06 | [5 empty] | 0.03936 | [11 empty] | 0.00068 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.16 |  | 0.16 | [5 empty] | 0.03 | [8 empty] | 0.1 | 0.007854 | 0.0083333 | 5.4542e-05 | 0.0006 | 5e-06 | [5 empty] | 0.0475 | [11 empty] | 0.00075 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.16 |  | 0.16 | [5 empty] | 0.025 | [8 empty] | 0.11 | 0.0095033 | 0.0091667 | 6.5995e-05 | 0.00054545 | 5e-06 | [5 empty] | 0.04111 | [11 empty] | 0.00083 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.188 |  | 0.188 | [5 empty] | 0.034 | [8 empty] | 0.12 | 0.01131 | 0.01 | 7.854e-05 | 0.0005 | 5e-06 | [5 empty] | 0.06377 | [11 empty] | 0.0009 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.188 |  | 0.188 | [5 empty] | 0.029 | [8 empty] | 0.13 | 0.013273 | 0.010833 | 9.2175e-05 | 0.00046154 | 5e-06 | [5 empty] | 0.05616 | [11 empty] | 0.00098 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.2 |  | 0.2 | [5 empty] | 0.0275 | [8 empty] | 0.145 | 0.016513 | 0.012083 | 0.00011467 | 0.00041379 | 5e-06 | [5 empty] | 0.05779 | [11 empty] | 0.00109 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.22 |  | 0.22 | [5 empty] | 0.03 | [8 empty] | 0.16 | 0.020106 | 0.013333 | 0.00013963 | 0.000375 | 5e-06 | [5 empty] | 0.06943 | [11 empty] | 0.00121 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 8 | Copper capillary tube - hard drawn | 0.24 |  | 0.24 | [5 empty] | 0.0325 | [8 empty] | 0.175 | 0.024053 | 0.014583 | 0.00016703 | 0.00034286 | 5e-06 | [5 empty] | 0.08107 | [11 empty] | 0.00132 |  |  |  | Page 2 | Table 2 | ASTM B360-20 |  |  |  |  | ASTM B360 |  |  |  | STANDARD DIMENSIONS AND RESIDUE LIMITS OF INTERIOR SURFACE FOR CAPILLARY TUBES
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 0.125 |  | 0.405 | 0.401 | 0.405 |  |  |  | 0.062 | Regular |  |  |  |  | 0.004 |  |  | 0.281 | 0.062016 | 0.023417 | 0.00043067 | 0.00021352 | 5e-06 | [5 empty] | 0.259 | [15 empty] | Page 4 | Table 3 | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 0.125 |  | 0.405 | 0.401 | 0.405 |  |  |  | 0.1 | Extra Strong |  |  |  |  | 0.006 |  |  | 0.205 | 0.033006 | 0.017083 | 0.00022921 | 0.00029268 | 5e-06 | [5 empty] | 0.371 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 0.25 |  | 0.54 | 0.536 | 0.54 |  |  |  | 0.082 | Regular |  |  |  |  | 0.005 |  |  | 0.376 | 0.11104 | 0.031333 | 0.00077109 | 0.00015957 | 5e-06 | [5 empty] | 0.457 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 0.25 |  | 0.54 | 0.536 | 0.54 |  |  |  | 0.123 | Extra Strong |  |  |  |  | 0.007 |  |  | 0.294 | 0.067887 | 0.0245 | 0.00047144 | 0.00020408 | 5e-06 | [5 empty] | 0.625 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 0.375 |  | 0.675 | 0.67 | 0.675 |  |  |  | 0.09 | Regular |  |  |  |  | 0.005 |  |  | 0.495 | 0.19244 | 0.04125 | 0.0013364 | 0.00012121 | 5e-06 | [5 empty] | 0.641 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 0.375 |  | 0.675 | 0.67 | 0.675 |  |  |  | 0.127 | Extra Strong |  |  |  |  | 0.007 |  |  | 0.421 | 0.1392 | 0.035083 | 0.0009667 | 0.00014252 | 5e-06 | [5 empty] | 0.847 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 0.5 |  | 0.84 | 0.835 | 0.84 |  |  |  | 0.107 | Regular |  |  |  |  | 0.006 |  |  | 0.626 | 0.30778 | 0.052167 | 0.0021374 | 9.5847e-05 | 5e-06 | [5 empty] | 0.955 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 0.5 |  | 0.84 | 0.835 | 0.84 |  |  |  | 0.149 | Extra Strong |  |  |  |  | 0.008 |  |  | 0.542 | 0.23072 | 0.045167 | 0.0016022 | 0.0001107 | 5e-06 | [5 empty] | 1.25 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 0.75 |  | 1.05 | 1.044 | 1.05 |  |  |  | 0.114 | Regular |  |  |  |  | 0.006 |  |  | 0.822 | 0.53068 | 0.0685 | 0.0036853 | 7.2993e-05 | 5e-06 | [5 empty] | 1.3 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 0.75 |  | 1.05 | 1.044 | 1.05 |  |  |  | 0.157 | Extra Strong |  |  |  |  | 0.009 |  |  | 0.736 | 0.42545 | 0.061333 | 0.0029545 | 8.1522e-05 | 5e-06 | [5 empty] | 1.71 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 1 |  | 1.315 | 1.309 | 1.315 |  |  |  | 0.126 | Regular |  |  |  |  | 0.007 |  |  | 1.063 | 0.88748 | 0.088583 | 0.006163 | 5.6444e-05 | 5e-06 | [5 empty] | 1.82 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 1 |  | 1.315 | 1.309 | 1.315 |  |  |  | 0.182 | Extra Strong |  |  |  |  | 0.01 |  |  | 0.951 | 0.71031 | 0.07925 | 0.0049327 | 6.3091e-05 | 5e-06 | [5 empty] | 2.51 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 1.25 |  | 1.66 | 1.654 | 1.66 |  |  |  | 0.146 | Regular |  |  |  |  | 0.008 |  |  | 1.368 | 1.4698 | 0.114 | 0.010207 | 4.386e-05 | 5e-06 | [5 empty] | 2.69 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 1.25 |  | 1.66 | 1.654 | 1.66 |  |  |  | 0.194 | Extra Strong |  |  |  |  | 0.01 |  |  | 1.272 | 1.2708 | 0.106 | 0.0088247 | 4.717e-05 | 5e-06 | [5 empty] | 3.46 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 1.5 |  | 1.9 | 1.894 | 1.9 |  |  |  | 0.15 | Regular |  |  |  |  | 0.008 |  |  | 1.6 | 2.0106 | 0.13333 | 0.013963 | 3.75e-05 | 5e-06 | [5 empty] | 3.2 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 1.5 |  | 1.9 | 1.894 | 1.9 |  |  |  | 0.203 | Extra Strong |  |  |  |  | 0.011 |  |  | 1.494 | 1.753 | 0.1245 | 0.012174 | 4.0161e-05 | 5e-06 | [5 empty] | 4.19 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 2 |  | 2.375 | 2.367 | 2.375 |  |  |  | 0.156 | Regular |  |  |  |  | 0.009 |  |  | 2.063 | 3.3426 | 0.17192 | 0.023213 | 2.9084e-05 | 5e-06 | [5 empty] | 4.22 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 2 |  | 2.375 | 2.367 | 2.375 |  |  |  | 0.221 | Extra Strong |  |  |  |  | 0.012 |  |  | 1.933 | 2.9346 | 0.16108 | 0.020379 | 3.104e-05 | 5e-06 | [5 empty] | 5.8 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 2.5 |  | 2.875 | 2.867 | 2.875 |  |  |  | 0.187 | Regular |  |  |  |  | 0.01 |  |  | 2.501 | 4.9127 | 0.20842 | 0.034116 | 2.399e-05 | 5e-06 | [5 empty] | 6.12 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 2.5 |  | 2.875 | 2.867 | 2.875 |  |  |  | 0.28 | Extra Strong |  |  |  |  | 0.015 |  |  | 2.315 | 4.2091 | 0.19292 | 0.02923 | 2.5918e-05 | 5e-06 | [5 empty] | 8.85 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 3 |  | 3.5 | 3.49 | 3.5 |  |  |  | 0.219 | Regular |  |  |  |  | 0.012 |  |  | 3.062 | 7.3638 | 0.25517 | 0.051137 | 1.9595e-05 | 5e-06 | [5 empty] | 8.76 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 3 |  | 3.5 | 3.49 | 3.5 |  |  |  | 0.304 | Extra Strong |  |  |  |  | 0.016 |  |  | 2.892 | 6.5688 | 0.241 | 0.045617 | 2.0747e-05 | 5e-06 | [5 empty] | 11.8 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 3.5 |  | 4 | 3.99 | 4 |  |  |  | 0.25 | Regular |  |  |  |  | 0.013 |  |  | 3.5 | 9.6211 | 0.29167 | 0.066813 | 1.7143e-05 | 5e-06 | [5 empty] | 11.4 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 3.5 |  | 4 | 3.99 | 4 |  |  |  | 0.321 | Extra Strong |  |  |  |  | 0.017 |  |  | 3.358 | 8.8563 | 0.27983 | 0.061502 | 1.7868e-05 | 5e-06 | [5 empty] | 14.4 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 4 |  | 4.5 | 4.488 | 4.5 |  |  |  | 0.25 | Regular |  |  |  |  | 0.014 |  |  | 4 | 12.5664 | 0.33333 | 0.087266 | 1.5e-05 | 5e-06 | [5 empty] | 12.9 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 4 |  | 4.5 | 4.488 | 4.5 |  |  |  | 0.341 | Extra Strong |  |  |  |  | 0.018 |  |  | 3.818 | 11.4488 | 0.31817 | 0.079506 | 1.5715e-05 | 5e-06 | [5 empty] | 17.3 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 5 |  | 5.562 | 5.548 | 5.562 |  |  |  | 0.25 | Regular |  |  |  |  | 0.014 |  |  | 5.062 | 20.1249 | 0.42183 | 0.13976 | 1.1853e-05 | 5e-06 | [5 empty] | 16.2 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 5 |  | 5.562 | 5.548 | 5.562 |  |  |  | 0.375 | Extra Strong |  |  |  |  | 0.019 |  |  | 4.812 | 18.1862 | 0.401 | 0.12629 | 1.2469e-05 | 5e-06 | [5 empty] | 23.7 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 6 |  | 6.625 | 6.609 | 6.625 |  |  |  | 0.25 | Regular |  |  |  |  | 0.014 |  |  | 6.125 | 29.4647 | 0.51042 | 0.20462 | 9.7959e-06 | 5e-06 | [5 empty] | 19.4 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 6 |  | 6.625 | 6.609 | 6.625 |  |  |  | 0.437 | Extra Strong |  |  |  |  | 0.027 |  |  | 5.751 | 25.9763 | 0.47925 | 0.18039 | 1.0433e-05 | 5e-06 | [5 empty] | 32.9 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 8 |  | 8.625 | 8.605 | 8.625 |  |  |  | 0.312 | Regular |  |  |  |  | 0.022 |  |  | 8.001 | 50.278 | 0.66675 | 0.34915 | 7.4991e-06 | 5e-06 | [5 empty] | 31.6 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 8 |  | 8.625 | 8.605 | 8.625 |  |  |  | 0.5 | Extra Strong |  |  |  |  | 0.035 |  |  | 7.625 | 45.6635 | 0.63542 | 0.31711 | 7.8689e-06 | 5e-06 | [5 empty] | 49.5 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 10 |  | 10.75 | 10.728 | 10.75 |  |  |  | 0.365 | Regular |  |  |  |  | 0.03 |  |  | 10.02 | 78.8543 | 0.835 | 0.5476 | 5.988e-06 | 5e-06 | [5 empty] | 46.2 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 10 |  | 10.75 | 10.728 | 10.75 |  |  |  | 0.5 | Extra Strong |  |  |  |  | 0.04 |  |  | 9.75 | 74.6619 | 0.8125 | 0.51849 | 6.1538e-06 | 5e-06 | [5 empty] | 62.4 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 12 |  | 12.75 | 12.726 | 12.75 |  |  |  | 0.375 | Regular |  |  |  |  | 0.03 |  |  | 12 | 113.0973 | 1 | 0.7854 | 5e-06 | 5e-06 | [5 empty] | 56.5 | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 4 | Copper pipe - seamless | 12 |  | 12.75 | 12.726 | 12.75 |  |  |  | - | Extra Strong |  |  |  |  | - |  |  | Not an available size | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5e-06 | [5 empty] | Not available in this size | [15 empty] | Page 4 | Table 3 | ASTM B42-20 |  |  |  |  | ASTM B42-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 5 | Copper pipe - threadless - seamless - deoxidized for brazed joint assembly | 0.25 |  | 0.54 | [5 empty] | 0.065 | [5 empty] | 0.0035 |  | 0.004 | 0.41 | 0.13203 | 0.034167 | 0.00091684 | 0.00014634 | 5e-06 | 0.12037 | 0.007 | 0.00378 |  |  |  | 0.376 | [14 empty] | Page 2 | Table 1 | ASTM B302-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 5 | Copper pipe - threadless - seamless - deoxidized for brazed joint assembly | 0.375 |  | 0.675 | [5 empty] | 0.065 | [5 empty] | 0.004 |  | 0.004 | 0.545 | 0.23328 | 0.045417 | 0.00162 | 0.00011009 | 5e-06 | 0.096296 | 0.008 | 0.0054 |  |  |  | 0.483 | [14 empty] | Page 2 | Table 1 | ASTM B302-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 5 | Copper pipe - threadless - seamless - deoxidized for brazed joint assembly | 0.5 |  | 0.84 | [5 empty] | 0.065 | [5 empty] | 0.004 |  | 0.005 | 0.71 | 0.39592 | 0.059167 | 0.0027494 | 8.4507e-05 | 5e-06 | 0.077381 | 0.008 | 0.00672 |  |  |  | 0.613 | [14 empty] | Page 2 | Table 1 | ASTM B302-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 5 | Copper pipe - threadless - seamless - deoxidized for brazed joint assembly | 0.75 |  | 1.05 | [5 empty] | 0.065 | [5 empty] | 0.004 |  | 0.005 | 0.92 | 0.66476 | 0.076667 | 0.0046164 | 6.5217e-05 | 5e-06 | 0.061905 | 0.008 | 0.0084 |  |  |  | 0.78 | [14 empty] | Page 2 | Table 1 | ASTM B302-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 5 | Copper pipe - threadless - seamless - deoxidized for brazed joint assembly | 1 |  | 1.315 | [5 empty] | 0.065 | [5 empty] | 0.004 |  | 0.005 | 1.185 | 1.1029 | 0.09875 | 0.0076589 | 5.0633e-05 | 5e-06 | 0.04943 | 0.01 | 0.01315 |  |  |  | 0.989 | [14 empty] | Page 2 | Table 1 | ASTM B302-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 5 | Copper pipe - threadless - seamless - deoxidized for brazed joint assembly | 1.25 |  | 1.66 | [5 empty] | 0.065 | [5 empty] | 0.004 |  | 0.006 | 1.53 | 1.8385 | 0.1275 | 0.012768 | 3.9216e-05 | 5e-06 | 0.039157 | 0.01 | 0.0166 |  |  |  | 1.26 | [14 empty] | Page 2 | Table 1 | ASTM B302-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 5 | Copper pipe - threadless - seamless - deoxidized for brazed joint assembly | 1.5 |  | 1.9 | [5 empty] | 0.065 | [5 empty] | 0.004 |  | 0.006 | 1.77 | 2.4606 | 0.1475 | 0.017087 | 3.3898e-05 | 5e-06 | 0.034211 | 0.01 | 0.019 |  |  |  | 1.45 | [14 empty] | Page 2 | Table 1 | ASTM B302-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 5 | Copper pipe - threadless - seamless - deoxidized for brazed joint assembly | 2 |  | 2.375 | [5 empty] | 0.065 | [5 empty] | 0.006 |  | 0.007 | 2.245 | 3.9584 | 0.18708 | 0.027489 | 2.6726e-05 | 5e-06 | 0.027368 | 0.015 | 0.035625 |  |  |  | 1.83 | [14 empty] | Page 2 | Table 1 | ASTM B302-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 5 | Copper pipe - threadless - seamless - deoxidized for brazed joint assembly | 2.5 |  | 2.875 | [5 empty] | 0.065 | [5 empty] | 0.006 |  | 0.007 | 2.745 | 5.918 | 0.22875 | 0.041097 | 2.1858e-05 | 5e-06 | 0.022609 | 0.015 | 0.043125 |  |  |  | 2.22 | [14 empty] | Page 2 | Table 1 | ASTM B302-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 5 | Copper pipe - threadless - seamless - deoxidized for brazed joint assembly | 3 |  | 3.5 | [5 empty] | 0.083 | [5 empty] | 0.007 |  | 0.008 | 3.334 | 8.7301 | 0.27783 | 0.060626 | 1.7996e-05 | 5e-06 | 0.023714 | 0.015 | 0.0525 |  |  |  | 3.45 | [14 empty] | Page 2 | Table 1 | ASTM B302-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 5 | Copper pipe - threadless - seamless - deoxidized for brazed joint assembly | 3.5 |  | 4 | [5 empty] | 0.095 | [5 empty] | 0.007 |  | 0.008 | 3.81 | 11.4009 | 0.3175 | 0.079173 | 1.5748e-05 | 5e-06 | 0.02375 | 0.015 | 0.06 |  |  |  | 4.52 | [14 empty] | Page 2 | Table 1 | ASTM B302-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 5 | Copper pipe - threadless - seamless - deoxidized for brazed joint assembly | 4 |  | 4.5 | [5 empty] | 0.107 | [5 empty] | 0.009 |  | 0.01 | 4.286 | 14.4276 | 0.35717 | 0.10019 | 1.3999e-05 | 5e-06 | 0.023778 | 0.015 | 0.0675 |  |  |  | 5.72 | [14 empty] | Page 2 | Table 1 | ASTM B302-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 5 | Copper pipe - threadless - seamless - deoxidized for brazed joint assembly | 5 |  | 5.562 | [5 empty] | 0.132 | [5 empty] | 0.01 |  | 0.012 | 5.298 | 22.0452 | 0.4415 | 0.15309 | 1.1325e-05 | 5e-06 | 0.023732 | 0.015 | 0.08343 |  |  |  | 8.73 | [14 empty] | Page 2 | Table 1 | ASTM B302-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 5 | Copper pipe - threadless - seamless - deoxidized for brazed joint assembly | 6 |  | 6.625 | [5 empty] | 0.158 | [5 empty] | 0.01 |  | 0.014 | 6.309 | 31.2616 | 0.52575 | 0.21709 | 9.5102e-06 | 5e-06 | 0.023849 | 0.015 | 0.099375 |  |  |  | 12.4 | [14 empty] | Page 2 | Table 1 | ASTM B302-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 5 | Copper pipe - threadless - seamless - deoxidized for brazed joint assembly | 8 |  | 8.625 | [5 empty] | 0.205 | [5 empty] | 0.014 |  | 0.018 | 8.215 | 53.0036 | 0.68458 | 0.36808 | 7.3037e-06 | 5e-06 | 0.023768 | 0.015 | 0.12937 |  |  |  | 21 | [14 empty] | Page 2 | Table 1 | ASTM B302-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 5 | Copper pipe - threadless - seamless - deoxidized for brazed joint assembly | 10 |  | 10.75 | [5 empty] | 0.256 | [5 empty] | 0.016 |  | 0.018 | 10.238 | 82.3228 | 0.85317 | 0.57169 | 5.8605e-06 | 5e-06 | 0.023814 | 0.015 | 0.16125 |  |  |  | 32.7 | [14 empty] | Page 2 | Table 1 | ASTM B302-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 5 | Copper pipe - threadless - seamless - deoxidized for brazed joint assembly | 12 |  | 12.75 | [5 empty] | 0.313 | [5 empty] | 0.02 |  | 0.018 | 12.124 | 115.4468 | 1.0103 | 0.80171 | 4.9489e-06 | 5e-06 | 0.024549 | 0.015 | 0.19125 |  |  |  | 47.4 | [14 empty] | Page 2 | Table 1 | ASTM B302-2017 |  |  |  |  | ASTM B302-2017 | [7 empty] | The Average outside diameter of a tube is the average of the maximum and minimum outside diameters, as determined at any one cross-section of the tube.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.25 |  | 0.375 |  |  | 0.002 |  |  | 0.035 | [5 empty] | 0.0035 |  |  | 0.305 | 0.073062 | 0.025417 | 0.00050737 | 0.00019672 | 5e-06 | 0.093333 | 0.008 | 0.003 |  |  | 0.145 | [9 empty] | Annealed | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.25 |  | 0.375 |  |  | 0.001 |  |  | 0.035 | [5 empty] | 0.0035 |  |  | 0.305 | 0.073062 | 0.025417 | 0.00050737 | 0.00019672 | 5e-06 | 0.093333 | 0.008 | 0.003 |  |  | 0.145 | [9 empty] | Drawn | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.25 |  | 0.375 |  |  | 0.002 |  |  | 0.03 | [5 empty] | 0.003 |  |  | 0.315 | 0.077931 | 0.02625 | 0.00054119 | 0.00019048 | 5e-06 | 0.08 | 0.008 | 0.003 |  |  | 0.126 | [9 empty] | Annealed | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.25 |  | 0.375 |  |  | 0.001 |  |  | 0.03 | [5 empty] | 0.003 |  |  | 0.315 | 0.077931 | 0.02625 | 0.00054119 | 0.00019048 | 5e-06 | 0.08 | 0.008 | 0.003 |  |  | 0.126 | [9 empty] | Drawn | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.25 |  | 0.375 |  |  | 0.001 |  |  | c | [5 empty] | c |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5e-06 | #VALUE! | #VALUE! | #VALUE! |  |  | c | [9 empty] | Drawn | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.375 |  | 0.5 |  |  | 0.0025 |  |  | 0.049 | [5 empty] | 0.005 |  |  | 0.402 | 0.12692 | 0.0335 | 0.00088141 | 0.00014925 | 5e-06 | 0.098 | 0.008 | 0.004 |  |  | 0.269 | [9 empty] | Annealed | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.375 |  | 0.5 |  |  | 0.001 |  |  | 0.049 | [5 empty] | 0.005 |  |  | 0.402 | 0.12692 | 0.0335 | 0.00088141 | 0.00014925 | 5e-06 | 0.098 | 0.008 | 0.004 |  |  | 0.269 | [9 empty] | Drawn | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.375 |  | 0.5 |  |  | 0.0025 |  |  | 0.035 | [5 empty] | 0.004 |  |  | 0.43 | 0.14522 | 0.035833 | 0.0010085 | 0.00013953 | 5e-06 | 0.07 | 0.008 | 0.004 |  |  | 0.198 | [9 empty] | Annealed | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.375 |  | 0.5 |  |  | 0.001 |  |  | 0.035 | [5 empty] | 0.004 |  |  | 0.43 | 0.14522 | 0.035833 | 0.0010085 | 0.00013953 | 5e-06 | 0.07 | 0.008 | 0.004 |  |  | 0.198 | [9 empty] | Drawn | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.375 |  | 0.5 |  |  | 0.0025 |  |  | 0.025 | [5 empty] | 0.002 |  |  | 0.45 | 0.15904 | 0.0375 | 0.0011045 | 0.00013333 | 5e-06 | 0.05 | 0.01 | 0.005 |  |  | 0.145 | [9 empty] | Annealed | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.375 |  | 0.5 |  |  | 0.001 |  |  | 0.025 | [5 empty] | 0.002 |  |  | 0.45 | 0.15904 | 0.0375 | 0.0011045 | 0.00013333 | 5e-06 | 0.05 | 0.01 | 0.005 |  |  | 0.145 | [9 empty] | Drawn | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.5 |  | 0.625 |  |  | 0.0025 |  |  | 0.049 | [5 empty] | 0.005 |  |  | 0.527 | 0.21813 | 0.043917 | 0.0015148 | 0.00011385 | 5e-06 | 0.0784 | 0.008 | 0.005 |  |  | 0.344 | [9 empty] | Annealed | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.5 |  | 0.625 |  |  | 0.001 |  |  | 0.049 | [5 empty] | 0.005 |  |  | 0.527 | 0.21813 | 0.043917 | 0.0015148 | 0.00011385 | 5e-06 | 0.0784 | 0.008 | 0.005 |  |  | 0.344 | [9 empty] | Drawn | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.5 |  | 0.625 |  |  | 0.0025 |  |  | 0.04 | [5 empty] | 0.004 |  |  | 0.545 | 0.23328 | 0.045417 | 0.00162 | 0.00011009 | 5e-06 | 0.064 | 0.008 | 0.005 |  |  | 0.285 | [9 empty] | Annealed | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.5 |  | 0.625 |  |  | 0.001 |  |  | 0.04 | [5 empty] | 0.004 |  |  | 0.545 | 0.23328 | 0.045417 | 0.00162 | 0.00011009 | 5e-06 | 0.064 | 0.008 | 0.005 |  |  | 0.285 | [9 empty] | Drawn | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.5 |  | 0.625 |  |  | 0.0025 |  |  | 0.028 | [5 empty] | 0.002 |  |  | 0.569 | 0.25428 | 0.047417 | 0.0017658 | 0.00010545 | 5e-06 | 0.0448 | 0.01 | 0.00625 |  |  | 0.204 | [9 empty] | Annealed | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.5 |  | 0.625 |  |  | 0.001 |  |  | 0.028 | [5 empty] | 0.003 |  |  | 0.569 | 0.25428 | 0.047417 | 0.0017658 | 0.00010545 | 5e-06 | 0.0448 | 0.01 | 0.00625 |  |  | 0.204 | [9 empty] | Drawn | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.625 |  | 0.75 |  |  | 0.0025 |  |  | 0.049 | [5 empty] | 0.005 |  |  | 0.652 | 0.33388 | 0.054333 | 0.0023186 | 9.2025e-05 | 5e-06 | 0.065333 | 0.008 | 0.006 |  |  | 0.418 | [9 empty] | Annealed | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.625 |  | 0.75 |  |  | 0.001 |  |  | 0.049 | [5 empty] | 0.005 |  |  | 0.652 | 0.33388 | 0.054333 | 0.0023186 | 9.2025e-05 | 5e-06 | 0.065333 | 0.008 | 0.006 |  |  | 0.418 | [9 empty] | Drawn | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.625 |  | 0.75 |  |  | 0.0025 |  |  | 0.042 | [5 empty] | 0.004 |  |  | 0.666 | 0.34837 | 0.0555 | 0.0024192 | 9.009e-05 | 5e-06 | 0.056 | 0.008 | 0.006 |  |  | 0.362 | [9 empty] | Annealed | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.625 |  | 0.75 |  |  | 0.001 |  |  | 0.042 | [5 empty] | 0.004 |  |  | 0.666 | 0.34837 | 0.0555 | 0.0024192 | 9.009e-05 | 5e-06 | 0.056 | 0.008 | 0.006 |  |  | 0.362 | [9 empty] | Drawn | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.625 |  | 0.75 |  |  | 0.001 |  |  | c | [5 empty] | c |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5e-06 | #VALUE! | #VALUE! | #VALUE! |  |  | c | [9 empty] | Drawn | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.75 |  | 0.875 |  |  | 0.003 |  |  | 0.065 | [5 empty] | 0.006 |  |  | 0.745 | 0.43592 | 0.062083 | 0.0030272 | 8.0537e-05 | 5e-06 | 0.074286 | 0.008 | 0.007 |  |  | 0.641 | [9 empty] | Annealed | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.75 |  | 0.875 |  |  | 0.001 |  |  | 0.065 | [5 empty] | 0.006 |  |  | 0.745 | 0.43592 | 0.062083 | 0.0030272 | 8.0537e-05 | 5e-06 | 0.074286 | 0.008 | 0.007 |  |  | 0.641 | [9 empty] | Drawn | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.75 |  | 0.875 |  |  | 0.003 |  |  | 0.045 | [5 empty] | 0.004 |  |  | 0.785 | 0.48398 | 0.065417 | 0.003361 | 7.6433e-05 | 5e-06 | 0.051429 | 0.008 | 0.007 |  |  | 0.455 | [9 empty] | Annealed | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.75 |  | 0.875 |  |  | 0.001 |  |  | 0.045 | [5 empty] | 0.004 |  |  | 0.785 | 0.48398 | 0.065417 | 0.003361 | 7.6433e-05 | 5e-06 | 0.051429 | 0.008 | 0.007 |  |  | 0.455 | [9 empty] | Drawn | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.75 |  | 0.875 |  |  | 0.003 |  |  | 0.032 | [5 empty] | 0.003 |  |  | 0.811 | 0.51657 | 0.067583 | 0.0035873 | 7.3983e-05 | 5e-06 | 0.036571 | 0.01 | 0.00875 |  |  | 0.328 | [9 empty] | Annealed | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 0.75 |  | 0.875 |  |  | 0.001 |  |  | 0.032 | [5 empty] | 0.003 |  |  | 0.811 | 0.51657 | 0.067583 | 0.0035873 | 7.3983e-05 | 5e-06 | 0.036571 | 0.01 | 0.00875 |  |  | 0.328 | [9 empty] | Drawn | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 1 |  | 1.125 |  |  | 0.0035 |  |  | 0.065 | [5 empty] | 0.006 |  |  | 0.995 | 0.77756 | 0.082917 | 0.0053997 | 6.0302e-05 | 5e-06 | 0.057778 | 0.008 | 0.009 |  |  | 0.839 | [9 empty] | Annealed | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 1 |  | 1.125 |  |  | 0.0015 |  |  | 0.065 | [5 empty] | 0.006 |  |  | 0.995 | 0.77756 | 0.082917 | 0.0053997 | 6.0302e-05 | 5e-06 | 0.057778 | 0.008 | 0.009 |  |  | 0.839 | [9 empty] | Drawn | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 1 |  | 1.125 |  |  | 0.0035 |  |  | 0.05 | [5 empty] | 0.005 |  |  | 1.025 | 0.82516 | 0.085417 | 0.0057303 | 5.8537e-05 | 5e-06 | 0.044444 | 0.01 | 0.01125 |  |  | 0.655 | [9 empty] | Annealed | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 1 |  | 1.125 |  |  | 0.0015 |  |  | 0.05 | [5 empty] | 0.005 |  |  | 1.025 | 0.82516 | 0.085417 | 0.0057303 | 5.8537e-05 | 5e-06 | 0.044444 | 0.01 | 0.01125 |  |  | 0.655 | [9 empty] | Drawn | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 1 |  | 1.125 |  |  | 0.0035 |  |  | 0.035 | [5 empty] | 0.004 |  |  | 1.055 | 0.87417 | 0.087917 | 0.0060706 | 5.6872e-05 | 5e-06 | 0.031111 | 0.01 | 0.01125 |  |  | 0.465 | [9 empty] | Annealed | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 1 |  | 1.125 |  |  | 0.0015 |  |  | 0.035 | [5 empty] | 0.004 |  |  | 1.055 | 0.87417 | 0.087917 | 0.0060706 | 5.6872e-05 | 5e-06 | 0.031111 | 0.01 | 0.01125 |  |  | 0.465 | [9 empty] | Drawn | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 1.25 |  | 1.375 |  |  | 0.004 |  |  | 0.065 | [5 empty] | 0.006 |  |  | 1.245 | 1.2174 | 0.10375 | 0.0084541 | 4.8193e-05 | 5e-06 | 0.047273 | 0.01 | 0.01375 |  |  | 1.04 | [9 empty] | Annealed | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 1.25 |  | 1.375 |  |  | 0.0015 |  |  | 0.065 | [5 empty] | 0.006 |  |  | 1.245 | 1.2174 | 0.10375 | 0.0084541 | 4.8193e-05 | 5e-06 | 0.047273 | 0.01 | 0.01375 |  |  | 1.04 | [9 empty] | Drawn | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 1.25 |  | 1.375 |  |  | 0.004 |  |  | 0.05 | [5 empty] | 0.006 |  |  | 1.275 | 1.2768 | 0.10625 | 0.0088664 | 4.7059e-05 | 5e-06 | 0.036364 | 0.01 | 0.01375 |  |  | 0.884 | [9 empty] | Annealed | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 1.25 |  | 1.375 |  |  | 0.0015 |  |  | 0.055 | [5 empty] | 0.006 |  |  | 1.265 | 1.2568 | 0.10542 | 0.0087279 | 4.7431e-05 | 5e-06 | 0.04 | 0.01 | 0.01375 |  |  | 0.884 | [9 empty] | Drawn | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 1.25 |  | 1.375 |  |  | 0.004 |  |  | 0.042 | [5 empty] | 0.004 |  |  | 1.291 | 1.309 | 0.10758 | 0.0090903 | 4.6476e-05 | 5e-06 | 0.030545 | 0.01 | 0.01375 |  |  | 0.682 | [9 empty] | Annealed | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 1.25 |  | 1.375 |  |  | 0.0015 |  |  | 0.042 | [5 empty] | 0.004 |  |  | 1.291 | 1.309 | 0.10758 | 0.0090903 | 4.6476e-05 | 5e-06 | 0.030545 | 0.01 | 0.01375 |  |  | 0.682 | [9 empty] | Drawn | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 1.5 |  | 1.625 |  |  | 0.0045 |  |  | 0.072 | [5 empty] | 0.007 |  |  | 1.481 | 1.7227 | 0.12342 | 0.011963 | 4.0513e-05 | 5e-06 | 0.044308 | 0.01 | 0.01625 |  |  | 1.36 | [9 empty] | Annealed | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 1.5 |  | 1.625 |  |  | 0.002 |  |  | 0.072 | [5 empty] | 0.007 |  |  | 1.481 | 1.7227 | 0.12342 | 0.011963 | 4.0513e-05 | 5e-06 | 0.044308 | 0.01 | 0.01625 |  |  | 1.36 | [9 empty] | Drawn | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 1.5 |  | 1.625 |  |  | 0.0045 |  |  | 0.06 | [5 empty] | 0.006 |  |  | 1.505 | 1.7789 | 0.12542 | 0.012354 | 3.9867e-05 | 5e-06 | 0.036923 | 0.01 | 0.01625 |  |  | 1.14 | [9 empty] | Annealed | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 1.5 |  | 1.625 |  |  | 0.002 |  |  | 0.06 | [5 empty] | 0.006 |  |  | 1.505 | 1.7789 | 0.12542 | 0.012354 | 3.9867e-05 | 5e-06 | 0.036923 | 0.01 | 0.01625 |  |  | 1.14 | [9 empty] | Drawn | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 1.5 |  | 1.625 |  |  | 0.0045 |  |  | 0.049 | [5 empty] | 0.005 |  |  | 1.527 | 1.8313 | 0.12725 | 0.012718 | 3.9293e-05 | 5e-06 | 0.030154 | 0.01 | 0.01625 |  |  | 0.94 | [9 empty] | Annealed | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 1.5 |  | 1.625 |  |  | 0.002 |  |  | 0.049 | [5 empty] | 0.005 |  |  | 1.527 | 1.8313 | 0.12725 | 0.012718 | 3.9293e-05 | 5e-06 | 0.030154 | 0.01 | 0.01625 |  |  | 0.94 | [9 empty] | Drawn | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 2 |  | 2.125 |  |  | 0.005 |  |  | 0.083 | [5 empty] | 0.008 |  |  | 1.959 | 3.0141 | 0.16325 | 0.020931 | 3.0628e-05 | 5e-06 | 0.039059 | 0.01 | 0.02125 |  |  | 2.06 | [9 empty] | Annealed | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 2 |  | 2.125 |  |  | 0.002 |  |  | 0.083 | [5 empty] | 0.008 |  |  | 1.959 | 3.0141 | 0.16325 | 0.020931 | 3.0628e-05 | 5e-06 | 0.039059 | 0.01 | 0.02125 |  |  | 2.06 | [9 empty] | Drawn | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 2 |  | 2.125 |  |  | 0.005 |  |  | 0.07 | [5 empty] | 0.007 |  |  | 1.985 | 3.0946 | 0.16542 | 0.021491 | 3.0227e-05 | 5e-06 | 0.032941 | 0.01 | 0.02125 |  |  | 1.75 | [9 empty] | Annealed | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 2 |  | 2.125 |  |  | 0.002 |  |  | 0.07 | [5 empty] | 0.007 |  |  | 1.985 | 3.0946 | 0.16542 | 0.021491 | 3.0227e-05 | 5e-06 | 0.032941 | 0.01 | 0.02125 |  |  | 1.75 | [9 empty] | Drawn | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 2 |  | 2.125 |  |  | 0.005 |  |  | 0.058 | [5 empty] | 0.006 |  |  | 2.009 | 3.1699 | 0.16742 | 0.022013 | 2.9866e-05 | 5e-06 | 0.027294 | 0.015 | 0.031875 |  |  | 1.46 | [9 empty] | Annealed | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 2 |  | 2.125 |  |  | 0.002 |  |  | 0.058 | [5 empty] | 0.006 |  |  | 2.009 | 3.1699 | 0.16742 | 0.022013 | 2.9866e-05 | 5e-06 | 0.027294 | 0.015 | 0.031875 |  |  | 1.46 | [9 empty] | Drawn | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 2.5 |  | 2.625 |  |  | 0.005 |  |  | 0.095 | [5 empty] | 0.01 |  |  | 2.435 | 4.6568 | 0.20292 | 0.032339 | 2.4641e-05 | 5e-06 | 0.03619 | 0.01 | 0.02625 |  |  | 2.93 | [9 empty] | Annealed | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 2.5 |  | 2.625 |  |  | 0.002 |  |  | 0.095 | [5 empty] | 0.01 |  |  | 2.435 | 4.6568 | 0.20292 | 0.032339 | 2.4641e-05 | 5e-06 | 0.03619 | 0.01 | 0.02625 |  |  | 2.93 | [9 empty] | Drawn | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 2.5 |  | 2.625 |  |  | 0.005 |  |  | 0.08 | [5 empty] | 0.008 |  |  | 2.465 | 4.7723 | 0.20542 | 0.033141 | 2.4341e-05 | 5e-06 | 0.030476 | 0.01 | 0.02625 |  |  | 2.48 | [9 empty] | Annealed | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 2.5 |  | 2.625 |  |  | 0.002 |  |  | 0.08 | [5 empty] | 0.008 |  |  | 2.465 | 4.7723 | 0.20542 | 0.033141 | 2.4341e-05 | 5e-06 | 0.030476 | 0.01 | 0.02625 |  |  | 2.48 | [9 empty] | Drawn | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 2.5 |  | 2.625 |  |  | 0.005 |  |  | 0.065 | [5 empty] | 0.006 |  |  | 2.495 | 4.8891 | 0.20792 | 0.033952 | 2.4048e-05 | 5e-06 | 0.024762 | 0.015 | 0.039375 |  |  | 2.03 | [9 empty] | Annealed | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 2.5 |  | 2.625 |  |  | 0.002 |  |  | 0.065 | [5 empty] | 0.006 |  |  | 2.495 | 4.8891 | 0.20792 | 0.033952 | 2.4048e-05 | 5e-06 | 0.024762 | 0.015 | 0.039375 |  |  | 2.03 | [9 empty] | Drawn | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 3 |  | 3.125 |  |  | 0.005 |  |  | 0.109 | [5 empty] | 0.011 |  |  | 2.907 | 6.6371 | 0.24225 | 0.046091 | 2.064e-05 | 5e-06 | 0.03488 | 0.01 | 0.03125 |  |  | 4 | [9 empty] | Annealed | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 3 |  | 3.125 |  |  | 0.002 |  |  | 0.109 | [5 empty] | 0.011 |  |  | 2.907 | 6.6371 | 0.24225 | 0.046091 | 2.064e-05 | 5e-06 | 0.03488 | 0.01 | 0.03125 |  |  | 4 | [9 empty] | Drawn | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 3 |  | 3.125 |  |  | 0.005 |  |  | 0.09 | [5 empty] | 0.009 |  |  | 2.945 | 6.8118 | 0.24542 | 0.047304 | 2.0374e-05 | 5e-06 | 0.0288 | 0.015 | 0.046875 |  |  | 3.33 | [9 empty] | Annealed | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 3 |  | 3.125 |  |  | 0.002 |  |  | 0.09 | [5 empty] | 0.009 |  |  | 2.945 | 6.8118 | 0.24542 | 0.047304 | 2.0374e-05 | 5e-06 | 0.0288 | 0.015 | 0.046875 |  |  | 3.33 | [9 empty] | Drawn | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 3 |  | 3.125 |  |  | 0.005 |  |  | 0.072 | [5 empty] | 0.007 |  |  | 2.981 | 6.9793 | 0.24842 | 0.048468 | 2.0127e-05 | 5e-06 | 0.02304 | 0.015 | 0.046875 |  |  | 2.68 | [9 empty] | Annealed | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 3 |  | 3.125 |  |  | 0.002 |  |  | 0.072 | [5 empty] | 0.007 |  |  | 2.981 | 6.9793 | 0.24842 | 0.048468 | 2.0127e-05 | 5e-06 | 0.02304 | 0.015 | 0.046875 |  |  | 2.68 | [9 empty] | Drawn | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 3.5 |  | 6.625 |  |  | 0.005 |  |  | 0.12 | [5 empty] | 0.012 |  |  | 6.385 | 32.0193 | 0.53208 | 0.22236 | 9.397e-06 | 5e-06 | 0.018113 | 0.015 | 0.099375 |  |  | 5.12 | [9 empty] | Annealed | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 3.5 |  | 6.625 |  |  | 0.002 |  |  | 0.12 | [5 empty] | 0.012 |  |  | 6.385 | 32.0193 | 0.53208 | 0.22236 | 9.397e-06 | 5e-06 | 0.018113 | 0.015 | 0.099375 |  |  | 5.12 | [9 empty] | Drawn | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 3.5 |  | 6.625 |  |  | 0.005 |  |  | 0.1 | [5 empty] | 0.01 |  |  | 6.425 | 32.4217 | 0.53542 | 0.22515 | 9.3385e-06 | 5e-06 | 0.015094 | 0.015 | 0.099375 |  |  | 4.29 | [9 empty] | Annealed | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 3.5 |  | 6.625 |  |  | 0.002 |  |  | 0.1 | [5 empty] | 0.01 |  |  | 6.425 | 32.4217 | 0.53542 | 0.22515 | 9.3385e-06 | 5e-06 | 0.015094 | 0.015 | 0.099375 |  |  | 4.29 | [9 empty] | Drawn | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 3.5 |  | 6.625 |  |  | 0.005 |  |  | 0.083 | [5 empty] | 0.008 |  |  | 6.459 | 32.7658 | 0.53825 | 0.22754 | 9.2894e-06 | 5e-06 | 0.012528 | 0.015 | 0.099375 |  |  | 3.58 | [9 empty] | Annealed | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 3.5 |  | 6.625 |  |  | 0.002 |  |  | 0.083 | [5 empty] | 0.008 |  |  | 6.459 | 32.7658 | 0.53825 | 0.22754 | 9.2894e-06 | 5e-06 | 0.012528 | 0.015 | 0.099375 |  |  | 3.58 | [9 empty] | Drawn | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 4 |  | 4.125 |  |  | 0.005 |  |  | 0.134 | [5 empty] | 0.013 |  |  | 3.857 | 11.6839 | 0.32142 | 0.081138 | 1.5556e-05 | 5e-06 | 0.032485 | 0.01 | 0.04125 |  |  | 6.51 | [9 empty] | Annealed | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 4 |  | 4.125 |  |  | 0.002 |  |  | 0.134 | [5 empty] | 0.013 |  |  | 3.857 | 11.6839 | 0.32142 | 0.081138 | 1.5556e-05 | 5e-06 | 0.032485 | 0.01 | 0.04125 |  |  | 6.51 | [9 empty] | Drawn | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 4 |  | 4.125 |  |  | 0.005 |  |  | 0.11 | [5 empty] | 0.011 |  |  | 3.905 | 11.9766 | 0.32542 | 0.083171 | 1.5365e-05 | 5e-06 | 0.026667 | 0.015 | 0.061875 |  |  | 5.38 | [9 empty] | Annealed | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 4 |  | 4.125 |  |  | 0.002 |  |  | 0.11 | [5 empty] | 0.011 |  |  | 3.905 | 11.9766 | 0.32542 | 0.083171 | 1.5365e-05 | 5e-06 | 0.026667 | 0.015 | 0.061875 |  |  | 5.38 | [9 empty] | Drawn | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 4 |  | 4.125 |  |  | 0.005 |  |  | 0.095 | [5 empty] | 0.01 |  |  | 3.935 | 12.1613 | 0.32792 | 0.084453 | 1.5248e-05 | 5e-06 | 0.02303 | 0.015 | 0.061875 |  |  | 4.66 | [9 empty] | Annealed | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 4 |  | 4.125 |  |  | 0.002 |  |  | 0.095 | [5 empty] | 0.01 |  |  | 3.935 | 12.1613 | 0.32792 | 0.084453 | 1.5248e-05 | 5e-06 | 0.02303 | 0.015 | 0.061875 |  |  | 4.66 | [9 empty] | Drawn | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 5 |  | 5.125 |  |  | 0.005 |  |  | 0.16 | [5 empty] | 0.016 |  |  | 4.805 | 18.1333 | 0.40042 | 0.12593 | 1.2487e-05 | 5e-06 | 0.03122 | 0.01 | 0.05125 |  |  | 9.67 | [9 empty] | Annealed | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 5 |  | 5.125 |  |  | 0.002 |  |  | 0.16 | [5 empty] | 0.016 |  |  | 4.805 | 18.1333 | 0.40042 | 0.12593 | 1.2487e-05 | 5e-06 | 0.03122 | 0.01 | 0.05125 |  |  | 9.67 | [9 empty] | Drawn | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 5 |  | 5.125 |  |  | 0.005 |  |  | 0.125 | [5 empty] | 0.012 |  |  | 4.875 | 18.6655 | 0.40625 | 0.12962 | 1.2308e-05 | 5e-06 | 0.02439 | 0.015 | 0.076875 |  |  | 7.61 | [9 empty] | Annealed | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 5 |  | 5.125 |  |  | 0.002 |  |  | 0.125 | [5 empty] | 0.012 |  |  | 4.875 | 18.6655 | 0.40625 | 0.12962 | 1.2308e-05 | 5e-06 | 0.02439 | 0.015 | 0.076875 |  |  | 7.61 | [9 empty] | Drawn | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 5 |  | 5.125 |  |  | 0.005 |  |  | 0.109 | [5 empty] | 0.011 |  |  | 4.907 | 18.9113 | 0.40892 | 0.13133 | 1.2227e-05 | 5e-06 | 0.021268 | 0.015 | 0.076875 |  |  | 6.66 | [9 empty] | Annealed | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 5 |  | 5.125 |  |  | 0.002 |  |  | 0.109 | [5 empty] | 0.011 |  |  | 4.907 | 18.9113 | 0.40892 | 0.13133 | 1.2227e-05 | 5e-06 | 0.021268 | 0.015 | 0.076875 |  |  | 6.66 | [9 empty] | Drawn | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 6 |  | 6.125 |  |  | 0.005 |  |  | 0.192 | [5 empty] | 0.019 |  |  | 5.741 | 25.886 | 0.47842 | 0.17976 | 1.0451e-05 | 5e-06 | 0.031347 | 0.01 | 0.06125 |  |  | 13.9 | [9 empty] | Annealed | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 6 |  | 6.125 |  |  | 0.002 |  |  | 0.192 | [5 empty] | 0.019 |  |  | 5.741 | 25.886 | 0.47842 | 0.17976 | 1.0451e-05 | 5e-06 | 0.031347 | 0.01 | 0.06125 |  |  | 13.9 | [9 empty] | Drawn | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 6 |  | 6.125 |  |  | 0.005 |  |  | 0.14 | [5 empty] | 0.014 |  |  | 5.845 | 26.8324 | 0.48708 | 0.18634 | 1.0265e-05 | 5e-06 | 0.022857 | 0.015 | 0.091875 |  |  | 10.2 | [9 empty] | Annealed | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 6 |  | 6.125 |  |  | 0.002 |  |  | 0.14 | [5 empty] | 0.014 |  |  | 5.845 | 26.8324 | 0.48708 | 0.18634 | 1.0265e-05 | 5e-06 | 0.022857 | 0.015 | 0.091875 |  |  | 10.2 | [9 empty] | Drawn | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 6 |  | 6.125 |  |  | 0.005 |  |  | 0.122 | [5 empty] | 0.012 |  |  | 5.881 | 27.1639 | 0.49008 | 0.18864 | 1.0202e-05 | 5e-06 | 0.019918 | 0.015 | 0.091875 |  |  | 8.92 | [9 empty] | Annealed | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 6 |  | 6.125 |  |  | 0.002 |  |  | 0.122 | [5 empty] | 0.012 |  |  | 5.881 | 27.1639 | 0.49008 | 0.18864 | 1.0202e-05 | 5e-06 | 0.019918 | 0.015 | 0.091875 |  |  | 8.92 | [9 empty] | Drawn | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 8 |  | 8.125 |  |  | 0.006 |  |  | 0.271 | [5 empty] | 0.027 |  |  | 7.583 | 45.1619 | 0.63192 | 0.31362 | 7.9124e-06 | 5e-06 | 0.033354 | 0.01 | 0.08125 |  |  | 25.9 | [9 empty] | Annealed | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 8 |  | 8.125 |  |  | +0.002 / -0.004 |  |  | 0.271 | [5 empty] | 0.027 |  |  | 7.583 | 45.1619 | 0.63192 | 0.31362 | 7.9124e-06 | 5e-06 | 0.033354 | 0.01 | 0.08125 |  |  | 25.9 | [9 empty] | Drawn | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 8 |  | 8.125 |  |  | 0.006 |  |  | 0.2 | [5 empty] | 0.02 |  |  | 7.725 | 46.8691 | 0.64375 | 0.32548 | 7.767e-06 | 5e-06 | 0.024615 | 0.015 | 0.12187 |  |  | 19.3 | [9 empty] | Annealed | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 8 |  | 8.125 |  |  | +0.002 / -0.004 |  |  | 0.2 | [5 empty] | 0.02 |  |  | 7.725 | 46.8691 | 0.64375 | 0.32548 | 7.767e-06 | 5e-06 | 0.024615 | 0.015 | 0.12187 |  |  | 19.3 | [9 empty] | Drawn | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 8 |  | 8.125 |  |  | 0.006 |  |  | 0.17 | [5 empty] | 0.017 |  |  | 7.785 | 47.6 | 0.64875 | 0.33056 | 7.7071e-06 | 5e-06 | 0.020923 | 0.015 | 0.12187 |  |  | 16.5 | [9 empty] | Annealed | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 8 |  | 8.125 |  |  | +0.002 / -0.004 |  |  | 0.17 | [5 empty] | 0.017 |  |  | 7.785 | 47.6 | 0.64875 | 0.33056 | 7.7071e-06 | 5e-06 | 0.020923 | 0.015 | 0.12187 |  |  | 16.5 | [9 empty] | Drawn | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 10 |  | 10.125 |  |  | 0.008 |  |  | 0.338 | [5 empty] | 0.034 |  |  | 9.449 | 70.1232 | 0.78742 | 0.48697 | 6.3499e-06 | 5e-06 | 0.033383 | 0.01 | 0.10125 |  |  | 40.3 | [9 empty] | Annealed | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 10 |  | 10.125 |  |  | +0.002 / -0.005 |  |  | 0.338 | [5 empty] | 0.034 |  |  | 9.449 | 70.1232 | 0.78742 | 0.48697 | 6.3499e-06 | 5e-06 | 0.033383 | 0.01 | 0.10125 |  |  | 40.3 | [9 empty] | Drawn | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 10 |  | 10.125 |  |  | 0.008 |  |  | 0.25 | [5 empty] | 0.025 |  |  | 9.625 | 72.7598 | 0.80208 | 0.50528 | 6.2338e-06 | 5e-06 | 0.024691 | 0.015 | 0.15187 |  |  | 30.1 | [9 empty] | Annealed | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 10 |  | 10.125 |  |  | +0.002 / -0.006 |  |  | 0.25 | [5 empty] | 0.025 |  |  | 9.625 | 72.7598 | 0.80208 | 0.50528 | 6.2338e-06 | 5e-06 | 0.024691 | 0.015 | 0.15187 |  |  | 30.1 | [9 empty] | Drawn | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 10 |  | 10.125 |  |  | 0.008 |  |  | 0.212 | [5 empty] | 0.021 |  |  | 9.701 | 73.9134 | 0.80842 | 0.51329 | 6.1849e-06 | 5e-06 | 0.020938 | 0.015 | 0.15187 |  |  | 25.6 | [9 empty] | Annealed | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 10 |  | 10.125 |  |  | +0.002 / -0.006 |  |  | 0.212 | [5 empty] | 0.021 |  |  | 9.701 | 73.9134 | 0.80842 | 0.51329 | 6.1849e-06 | 5e-06 | 0.020938 | 0.015 | 0.15187 |  |  | 25.6 | [9 empty] | Drawn | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 12 |  | 12.125 |  |  | 0.008 |  |  | 0.405 | [5 empty] | 0.04 |  |  | 11.315 | 100.5539 | 0.94292 | 0.69829 | 5.3027e-06 | 5e-06 | 0.033402 | 0.01 | 0.12125 |  |  | 57.8 | [9 empty] | Annealed | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 12 |  | 12.125 |  |  | +0.002 / -0.006 |  |  | 0.405 | [5 empty] | 0.04 |  |  | 11.315 | 100.5539 | 0.94292 | 0.69829 | 5.3027e-06 | 5e-06 | 0.033402 | 0.01 | 0.12125 |  |  | 57.8 | [9 empty] | Drawn | K |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 12 |  | 12.125 |  |  | 0.008 |  |  | 0.28 | [5 empty] | 0.028 |  |  | 11.565 | 105.0464 | 0.96375 | 0.72949 | 5.1881e-06 | 5e-06 | 0.023093 | 0.015 | 0.18187 |  |  | 40.4 | [9 empty] | Annealed | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 12 |  | 12.125 |  |  | +0.002 / -0.006 |  |  | 0.28 | [5 empty] | 0.028 |  |  | 11.565 | 105.0464 | 0.96375 | 0.72949 | 5.1881e-06 | 5e-06 | 0.023093 | 0.015 | 0.18187 |  |  | 40.4 | [9 empty] | Drawn | L |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 12 |  | 12.125 |  |  | 0.008 |  |  | 0.254 | [5 empty] | 0.025 |  |  | 11.617 | 105.9932 | 0.96808 | 0.73606 | 5.1648e-06 | 5e-06 | 0.020948 | 0.015 | 0.18187 |  |  | 36.7 | [9 empty] | Annealed | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 6 | Copper water tube - seamless - plumbing and fluid conveyance tubing | 12 |  | 12.125 |  |  | +0.002 / -0.006 |  |  | 0.254 | [5 empty] | 0.025 |  |  | 11.617 | 105.9932 | 0.96808 | 0.73606 | 5.1648e-06 | 5e-06 | 0.020948 | 0.015 | 0.18187 |  |  | 36.7 | [9 empty] | Drawn | M |  |  |  |  | Page 2 | Table 1 | ASTM B88-22 |  |  |  |  | ASTM A88-20 | [7 empty] | The average outside diameter of the tube is the average of the maximum and minimum outside diameter, as determined at any one cross section of the tube. | Maximum deviation at any one point | Indicates that the material is not generally available or that no tolerance has been established.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.125 |  | 0.405 | [5 empty] | 0.058 | Special 1 | [7 empty] | 0.289 | 0.065597 | 0.024083 | 0.00045554 | 0.00020761 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.125 |  | 0.405 | [5 empty] | 0.062 | Regular | [7 empty] | 0.281 | 0.062016 | 0.023417 | 0.00043067 | 0.00021352 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.125 |  | 0.405 | [5 empty] | 0.1 | Extra Strong | [7 empty] | 0.205 | 0.033006 | 0.017083 | 0.00022921 | 0.00029268 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.25 |  | 0.54 | [5 empty] | 0.065 | Special 1 | [7 empty] | 0.41 | 0.13203 | 0.034167 | 0.00091684 | 0.00014634 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.25 |  | 0.54 | [5 empty] | 0.072 | Special 2 | [7 empty] | 0.396 | 0.12316 | 0.033 | 0.0008553 | 0.00015152 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.25 |  | 0.54 | [5 empty] | 0.082 | Regular | [7 empty] | 0.376 | 0.11104 | 0.031333 | 0.00077109 | 0.00015957 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.25 |  | 0.54 | [5 empty] | 0.123 | Extra Strong | [7 empty] | 0.294 | 0.067887 | 0.0245 | 0.00047144 | 0.00020408 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.375 |  | 0.675 | [5 empty] | 0.065 | Special 1 | [7 empty] | 0.545 | 0.23328 | 0.045417 | 0.00162 | 0.00011009 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.375 |  | 0.675 | [5 empty] | 0.072 | Special 2 | [7 empty] | 0.531 | 0.22145 | 0.04425 | 0.0015379 | 0.00011299 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.375 |  | 0.675 | [5 empty] | 0.095 | Special 3 | [7 empty] | 0.485 | 0.18475 | 0.040417 | 0.001283 | 0.00012371 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.375 |  | 0.675 | [5 empty] | 0.148 | Special 4 | [7 empty] | 0.379 | 0.11282 | 0.031583 | 0.00078344 | 0.00015831 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.375 |  | 0.675 | [5 empty] | 0.09 | Regular | [7 empty] | 0.495 | 0.19244 | 0.04125 | 0.0013364 | 0.00012121 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.375 |  | 0.675 | [5 empty] | 0.127 | Extra Strong | [7 empty] | 0.421 | 0.1392 | 0.035083 | 0.0009667 | 0.00014252 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.5 |  | 0.84 | [5 empty] | 0.065 | Special 1 | [7 empty] | 0.71 | 0.39592 | 0.059167 | 0.0027494 | 8.4507e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.5 |  | 0.84 | [5 empty] | 0.072 | Special 2 | [7 empty] | 0.696 | 0.38046 | 0.058 | 0.0026421 | 8.6207e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.5 |  | 0.84 | [5 empty] | 0.12 | Special 3 | [7 empty] | 0.6 | 0.28274 | 0.05 | 0.0019635 | 0.0001 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.5 |  | 0.84 | [5 empty] | 0.203 | Special 4 | [7 empty] | 0.434 | 0.14793 | 0.036167 | 0.0010273 | 0.00013825 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.5 |  | 0.84 | [5 empty] | 0.107 | Regular | [7 empty] | 0.626 | 0.30778 | 0.052167 | 0.0021374 | 9.5847e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.5 |  | 0.84 | [5 empty] | 0.149 | Extra Strong | [7 empty] | 0.542 | 0.23072 | 0.045167 | 0.0016022 | 0.0001107 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.75 |  | 1.05 | [5 empty] | 0.065 | Special 1 | [7 empty] | 0.92 | 0.66476 | 0.076667 | 0.0046164 | 6.5217e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.75 |  | 1.05 | [5 empty] | 0.083 | Special 2 | [7 empty] | 0.884 | 0.61375 | 0.073667 | 0.0042622 | 6.7873e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.75 |  | 1.05 | [5 empty] | 0.148 | Special 3 | [7 empty] | 0.754 | 0.44651 | 0.062833 | 0.0031008 | 7.9576e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.75 |  | 1.05 | [5 empty] | 0.238 | Special 4 | [7 empty] | 0.574 | 0.25877 | 0.047833 | 0.001797 | 0.00010453 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.75 |  | 1.05 | [5 empty] | 0.114 | Regular | [7 empty] | 0.822 | 0.53068 | 0.0685 | 0.0036853 | 7.2993e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 0.75 |  | 1.05 | [5 empty] | 0.157 | Extra Strong | [7 empty] | 0.736 | 0.42545 | 0.061333 | 0.0029545 | 8.1522e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1 |  | 1.315 | [5 empty] | 0.065 | Special 1 | [7 empty] | 1.185 | 1.1029 | 0.09875 | 0.0076589 | 5.0633e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1 |  | 1.315 | [5 empty] | 0.095 | Special 2 | [7 empty] | 1.125 | 0.99402 | 0.09375 | 0.0069029 | 5.3333e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1 |  | 1.315 | [5 empty] | 0.203 | Special 3 | [7 empty] | 0.909 | 0.64896 | 0.07575 | 0.0045067 | 6.6007e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1 |  | 1.315 | [5 empty] | 0.34 | Special 4 | [7 empty] | 0.635 | 0.31669 | 0.052917 | 0.0021993 | 9.4488e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1 |  | 1.315 | [5 empty] | 0.126 | Regular | [7 empty] | 1.063 | 0.88748 | 0.088583 | 0.006163 | 5.6444e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1 |  | 1.315 | [5 empty] | 0.182 | Extra Strong | [7 empty] | 0.951 | 0.71031 | 0.07925 | 0.0049327 | 6.3091e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1.125 |  | 1.66 | [5 empty] | 0.072 | Special 1 | [7 empty] | 1.516 | 1.805 | 0.12633 | 0.012535 | 3.9578e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1.125 |  | 1.66 | [5 empty] | 0.095 | Special 2 | [7 empty] | 1.47 | 1.6972 | 0.1225 | 0.011786 | 4.0816e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1.125 |  | 1.66 | [5 empty] | 0.12 | Special 3 | [7 empty] | 1.42 | 1.5837 | 0.11833 | 0.010998 | 4.2254e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1.125 |  | 1.66 | [5 empty] | 0.22 | Special 4 | [7 empty] | 1.22 | 1.169 | 0.10167 | 0.008118 | 4.918e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1.125 |  | 1.66 | [5 empty] | 0.38 | Special 5 | [7 empty] | 0.9 | 0.63617 | 0.075 | 0.0044179 | 6.6667e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1.125 |  | 1.66 | [5 empty] | 0.146 | Regular | [7 empty] | 1.368 | 1.4698 | 0.114 | 0.010207 | 4.386e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1.125 |  | 1.66 | [5 empty] | 0.194 | Extra Strong | [7 empty] | 1.272 | 1.2708 | 0.106 | 0.0088247 | 4.717e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1.5 |  | 1.9 | [5 empty] | 0.072 | Special 1 | [7 empty] | 1.756 | 2.4218 | 0.14633 | 0.016818 | 3.4169e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1.5 |  | 1.9 | [5 empty] | 0.109 | Special 2 | [7 empty] | 1.682 | 2.222 | 0.14017 | 0.01543 | 3.5672e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1.5 |  | 1.9 | [5 empty] | 0.134 | Special 3 | [7 empty] | 1.632 | 2.0918 | 0.136 | 0.014527 | 3.6765e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1.5 |  | 1.9 | [5 empty] | 0.25 | Special 4 | [7 empty] | 1.4 | 1.5394 | 0.11667 | 0.01069 | 4.2857e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1.5 |  | 1.9 | [5 empty] | 0.425 | Special 5 | [7 empty] | 1.05 | 0.8659 | 0.0875 | 0.0060132 | 5.7143e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1.5 |  | 1.9 | [5 empty] | 0.15 | Regular | [7 empty] | 1.6 | 2.0106 | 0.13333 | 0.013963 | 3.75e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 1.5 |  | 1.9 | [5 empty] | 0.203 | Extra Strong | [7 empty] | 1.494 | 1.753 | 0.1245 | 0.012174 | 4.0161e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 2 |  | 2.375 | [5 empty] | 0.083 | Special 1 | [7 empty] | 2.209 | 3.8325 | 0.18408 | 0.026615 | 2.7162e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 2 |  | 2.375 | [5 empty] | 0.12 | Special 2 | [7 empty] | 2.135 | 3.58 | 0.17792 | 0.024861 | 2.8103e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 2 |  | 2.375 | [5 empty] | 0.165 | Special 3 | [7 empty] | 2.045 | 3.2846 | 0.17042 | 0.022809 | 2.934e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 2 |  | 2.375 | [5 empty] | 0.34 | Special 4 | [7 empty] | 1.695 | 2.2565 | 0.14125 | 0.01567 | 3.5398e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 2 |  | 2.375 | [5 empty] | 0.52 | Special 5 | [7 empty] | 1.335 | 1.3998 | 0.11125 | 0.0097205 | 4.4944e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 2 |  | 2.375 | [5 empty] | 0.156 | Regular | [7 empty] | 2.063 | 3.3426 | 0.17192 | 0.023213 | 2.9084e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 2 |  | 2.375 | [5 empty] | 0.221 | Extra Strong | [7 empty] | 1.933 | 2.9346 | 0.16108 | 0.020379 | 3.104e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 2.5 |  | 2.875 | [5 empty] | 0.083 | Special 1 | [7 empty] | 2.709 | 5.7638 | 0.22575 | 0.040026 | 2.2148e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 2.5 |  | 2.875 | [5 empty] | 0.134 | Special 2 | [7 empty] | 2.607 | 5.3379 | 0.21725 | 0.037069 | 2.3015e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 2.5 |  | 2.875 | [5 empty] | 0.203 | Special 3 | [7 empty] | 2.469 | 4.7878 | 0.20575 | 0.033248 | 2.4301e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 2.5 |  | 2.875 | [5 empty] | 0.38 | Special 4 | [7 empty] | 2.115 | 3.5133 | 0.17625 | 0.024398 | 2.8369e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 2.5 |  | 2.875 | [5 empty] | 0.187 | Regular | [7 empty] | 2.501 | 4.9127 | 0.20842 | 0.034116 | 2.399e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 2.5 |  | 2.875 | [5 empty] | 0.28 | Extra Strong | [7 empty] | 2.315 | 4.2091 | 0.19292 | 0.02923 | 2.5918e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 3 |  | 3.5 | [5 empty] | 0.095 | Special 1 | [7 empty] | 3.31 | 8.6049 | 0.27583 | 0.059756 | 1.8127e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 3 |  | 3.5 | [5 empty] | 0.165 | Special 2 | [7 empty] | 3.17 | 7.8924 | 0.26417 | 0.054808 | 1.8927e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 3 |  | 3.5 | [5 empty] | 0.25 | Special 3 | [7 empty] | 3 | 7.0686 | 0.25 | 0.049087 | 2e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 3 |  | 3.5 | [5 empty] | 0.458 | Special 4 | [7 empty] | 2.584 | 5.2441 | 0.21533 | 0.036418 | 2.322e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 3 |  | 3.5 | [5 empty] | 0.219 | Regular | [7 empty] | 3.062 | 7.3638 | 0.25517 | 0.051137 | 1.9595e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 3 |  | 3.5 | [5 empty] | 0.304 | Extra Strong | [7 empty] | 2.892 | 6.5688 | 0.241 | 0.045617 | 2.0747e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 3.5 |  | 4 | [5 empty] | 0.095 | Special 1 | [7 empty] | 3.81 | 11.4009 | 0.3175 | 0.079173 | 1.5748e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 3.5 |  | 4 | [5 empty] | 0.18 | Special 2 | [7 empty] | 3.64 | 10.4062 | 0.30333 | 0.072265 | 1.6484e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 3.5 |  | 4 | [5 empty] | 0.284 | Special 3 | [7 empty] | 3.432 | 9.2509 | 0.286 | 0.064242 | 1.7483e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 3.5 |  | 4 | [5 empty] | 0.25 | Regular | [7 empty] | 3.5 | 9.6211 | 0.29167 | 0.066813 | 1.7143e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 3.5 |  | 4 | [5 empty] | 0.321 | Extra Strong | [7 empty] | 3.358 | 8.8563 | 0.27983 | 0.061502 | 1.7868e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 4 |  | 4.5 | [5 empty] | 0.109 | Special 1 | [7 empty] | 4.282 | 14.4007 | 0.35683 | 0.1 | 1.4012e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 4 |  | 4.5 | [5 empty] | 0.203 | Special 2 | [7 empty] | 4.094 | 13.1639 | 0.34117 | 0.091416 | 1.4656e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 4 |  | 4.5 | [5 empty] | 0.34 | Special 3 | [7 empty] | 3.82 | 11.4608 | 0.31833 | 0.079589 | 1.5707e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 4 |  | 4.5 | [5 empty] | 0.25 | Regular | [7 empty] | 4 | 12.5664 | 0.33333 | 0.087266 | 1.5e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 4 |  | 4.5 | [5 empty] | 0.341 | Extra Strong | [7 empty] | 3.818 | 11.4488 | 0.31817 | 0.079506 | 1.5715e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 5 |  | 5.562 | [5 empty] | 0.125 | Special 1 | [7 empty] | 5.312 | 22.1619 | 0.44267 | 0.1539 | 1.1295e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 5 |  | 5.562 | [5 empty] | 0.22 | Special 2 | [7 empty] | 5.122 | 20.6048 | 0.42683 | 0.14309 | 1.1714e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 5 |  | 5.562 | [5 empty] | 0.425 | Special 3 | [7 empty] | 4.712 | 17.4382 | 0.39267 | 0.1211 | 1.2733e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 5 |  | 5.562 | [5 empty] | 0.25 | Regular | [7 empty] | 5.062 | 20.1249 | 0.42183 | 0.13976 | 1.1853e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 5 |  | 5.562 | [5 empty] | 0.375 | Extra Strong | [7 empty] | 4.812 | 18.1862 | 0.401 | 0.12629 | 1.2469e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 6 |  | 6.625 | [5 empty] | 0.134 | Special 1 | [7 empty] | 6.357 | 31.7391 | 0.52975 | 0.22041 | 9.4384e-06 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 6 |  | 6.625 | [5 empty] | 0.259 | Special 2 | [7 empty] | 6.107 | 29.2918 | 0.50892 | 0.20342 | 9.8248e-06 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 6 |  | 6.625 | [5 empty] | 0.457 | Special 3 | [7 empty] | 5.711 | 25.6162 | 0.47592 | 0.17789 | 1.0506e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 6 |  | 6.625 | [5 empty] | 0.25 | Regular | [7 empty] | 6.125 | 29.4647 | 0.51042 | 0.20462 | 9.7959e-06 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | C | Non-Ferrous Pipe and Tubing | 9 | Copper-Nickel pipe and tube - seamless | 6 |  | 6.625 | [5 empty] | 0.437 | Extra Strong | [7 empty] | 5.751 | 25.9763 | 0.47925 | 0.18039 | 1.0433e-05 | 5e-06 | [21 empty] | Page 4 | Table X1.1 | ASTM B466-18 |  |  |  |  | ASTM B466-86 & B466M-86 |  |  |  | PREFERRED WALL THICKNESSES OF DRAWN SEAMLESS PIPE, BASED ON SPS DIAMETERS |  |  |  | Note - The values stated in U.S. customary units are intended to be regarded as the standard. The metric equivalents of the U.S. customary units may be appropriate.
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 3 |  | 3.96 | [5 empty] | 0.25 | 350 | [7 empty] | 3.46 | 9.4025 | 0.28833 | 0.065295 | 0.002948 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 4 |  | 4.8 | [5 empty] | 0.25 | 350 | [7 empty] | 4.3 | 14.522 | 0.35833 | 0.10085 | 0.0023721 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 6 |  | 6.9 | [5 empty] | 0.25 | 350 | [7 empty] | 6.4 | 32.1699 | 0.53333 | 0.2234 | 0.0015937 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 8 |  | 9.05 | [5 empty] | 0.25 | 350 | [7 empty] | 8.55 | 57.4146 | 0.7125 | 0.39871 | 0.001193 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 10 |  | 11.1 | [5 empty] | 0.26 | 350 | [7 empty] | 10.58 | 87.9146 | 0.88167 | 0.61052 | 0.00096408 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 12 |  | 13.2 | [5 empty] | 0.28 | 350 | [7 empty] | 12.64 | 125.4828 | 1.0533 | 0.87141 | 0.00080696 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 14 |  | 15.3 | [5 empty] | 0.28 | 250 | [7 empty] | 14.74 | 170.6416 | 1.2283 | 1.185 | 0.00069199 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 14 |  | 15.3 | [5 empty] | 0.3 | 300 | [7 empty] | 14.7 | 169.7167 | 1.225 | 1.1786 | 0.00069388 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 14 |  | 15.3 | [5 empty] | 0.31 | 350 | [7 empty] | 14.68 | 169.2552 | 1.2233 | 1.1754 | 0.00069482 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 16 |  | 17.4 | [5 empty] | 0.3 | 250 | [7 empty] | 16.8 | 221.6708 | 1.4 | 1.5394 | 0.00060714 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 16 |  | 17.4 | [5 empty] | 0.32 | 300 | [7 empty] | 16.76 | 220.6165 | 1.3967 | 1.5321 | 0.00060859 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 16 |  | 17.4 | [5 empty] | 0.34 | 350 | [7 empty] | 16.72 | 219.5647 | 1.3933 | 1.5248 | 0.00061005 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 18 |  | 19.5 | [5 empty] | 0.31 | 250 | [7 empty] | 18.88 | 279.9586 | 1.5733 | 1.9442 | 0.00054025 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 18 |  | 19.5 | [5 empty] | 0.34 | 300 | [7 empty] | 18.82 | 278.1821 | 1.5683 | 1.9318 | 0.00054198 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 18 |  | 19.5 | [5 empty] | 0.36 | 350 | [7 empty] | 18.78 | 277.0008 | 1.565 | 1.9236 | 0.00054313 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 20 |  | 21.6 | [5 empty] | 0.33 | 250 | [7 empty] | 20.94 | 344.3842 | 1.745 | 2.3916 | 0.00048711 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 20 |  | 21.6 | [5 empty] | 0.36 | 300 | [7 empty] | 20.88 | 342.4135 | 1.74 | 2.3779 | 0.00048851 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 20 |  | 21.6 | [5 empty] | 0.38 | 350 | [7 empty] | 20.84 | 341.1028 | 1.7367 | 2.3688 | 0.00048944 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 24 |  | 25.8 | [5 empty] | 0.33 | 200 | [7 empty] | 25.14 | 496.387 | 2.095 | 3.4471 | 0.00040573 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 24 |  | 25.8 | [5 empty] | 0.37 | 250 | [7 empty] | 25.06 | 493.2329 | 2.0883 | 3.4252 | 0.00040702 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 24 |  | 25.8 | [5 empty] | 0.4 | 300 | [7 empty] | 25 | 490.8739 | 2.0833 | 3.4088 | 0.000408 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 24 |  | 25.8 | [5 empty] | 0.43 | 350 | [7 empty] | 24.94 | 488.5205 | 2.0783 | 3.3925 | 0.00040898 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 30 |  | 32 | [5 empty] | 0.34 | 150 | [7 empty] | 31.32 | 770.4304 | 2.61 | 5.3502 | 0.00032567 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 30 |  | 32 | [5 empty] | 0.38 | 200 | [7 empty] | 31.24 | 766.4996 | 2.6033 | 5.3229 | 0.0003265 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 30 |  | 32 | [5 empty] | 0.42 | 250 | [7 empty] | 31.16 | 762.5789 | 2.5967 | 5.2957 | 0.00032734 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 30 |  | 32 | [5 empty] | 0.45 | 300 | [7 empty] | 31.1 | 759.645 | 2.5917 | 5.2753 | 0.00032797 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 30 |  | 32 | [5 empty] | 0.49 | 350 | [7 empty] | 31.02 | 755.7418 | 2.585 | 5.2482 | 0.00032882 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 36 |  | 38.3 | [5 empty] | 0.38 | 150 | [7 empty] | 37.54 | 1106.8236 | 3.1283 | 7.6863 | 0.00027171 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 36 |  | 38.3 | [5 empty] | 0.42 | 200 | [7 empty] | 37.46 | 1102.1112 | 3.1217 | 7.6536 | 0.00027229 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 36 |  | 38.3 | [5 empty] | 0.47 | 250 | [7 empty] | 37.36 | 1096.2349 | 3.1133 | 7.6127 | 0.00027302 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 36 |  | 38.3 | [5 empty] | 0.51 | 300 | [7 empty] | 37.28 | 1091.5451 | 3.1067 | 7.5802 | 0.00027361 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 36 |  | 38.3 | [5 empty] | 0.56 | 350 | [7 empty] | 37.18 | 1085.697 | 3.0983 | 7.5396 | 0.00027434 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 42 |  | 44.5 | [5 empty] | 0.41 | 150 | [7 empty] | 43.68 | 1498.4945 | 3.64 | 10.4062 | 0.00023352 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 42 |  | 44.5 | [5 empty] | 0.47 | 200 | [7 empty] | 43.56 | 1490.2723 | 3.63 | 10.3491 | 0.00023416 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 42 |  | 44.5 | [5 empty] | 0.52 | 250 | [7 empty] | 43.46 | 1483.4377 | 3.6217 | 10.3017 | 0.0002347 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 42 |  | 44.5 | [5 empty] | 0.57 | 300 | [7 empty] | 43.36 | 1476.6189 | 3.6133 | 10.2543 | 0.00023524 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 42 |  | 44.5 | [5 empty] | 0.63 | 350 | [7 empty] | 43.24 | 1468.4571 | 3.6033 | 10.1976 | 0.00023589 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 48 |  | 50.8 | [5 empty] | 0.46 | 150 | [7 empty] | 49.88 | 1954.0819 | 4.1567 | 13.57 | 0.00020449 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 48 |  | 50.8 | [5 empty] | 0.52 | 200 | [7 empty] | 49.76 | 1944.6911 | 4.1467 | 13.5048 | 0.00020498 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 48 |  | 50.8 | [5 empty] | 0.58 | 250 | [7 empty] | 49.64 | 1935.3229 | 4.1367 | 13.4397 | 0.00020548 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 48 |  | 50.8 | [5 empty] | 0.64 | 300 | [7 empty] | 49.52 | 1925.9773 | 4.1267 | 13.3748 | 0.00020598 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 48 |  | 50.8 | [5 empty] | 0.7 | 350 | [7 empty] | 49.4 | 1916.6543 | 4.1167 | 13.3101 | 0.00020648 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 54 |  | 57.56 | [5 empty] | 0.51 | 150 | [7 empty] | 56.54 | 2510.7385 | 4.7117 | 17.4357 | 0.0001804 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 54 |  | 57.56 | [5 empty] | 0.58 | 200 | [7 empty] | 56.4 | 2498.3201 | 4.7 | 17.3494 | 0.00018085 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 54 |  | 57.56 | [5 empty] | 0.65 | 250 | [7 empty] | 56.26 | 2485.9325 | 4.6883 | 17.2634 | 0.0001813 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 54 |  | 57.56 | [5 empty] | 0.72 | 300 | [7 empty] | 56.12 | 2473.5757 | 4.6767 | 17.1776 | 0.00018175 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 54 |  | 57.56 | [5 empty] | 0.79 | 350 | [7 empty] | 55.98 | 2461.2497 | 4.665 | 17.092 | 0.00018221 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 60 |  | 61.61 | [5 empty] | 0.54 | 150 | [7 empty] | 60.53 | 2877.6053 | 5.0442 | 19.9834 | 0.00016851 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 60 |  | 61.61 | [5 empty] | 0.61 | 200 | [7 empty] | 60.39 | 2864.3095 | 5.0325 | 19.891 | 0.0001689 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 60 |  | 61.61 | [5 empty] | 0.68 | 250 | [7 empty] | 60.25 | 2851.0444 | 5.0208 | 19.7989 | 0.00016929 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 60 |  | 61.61 | [5 empty] | 0.76 | 300 | [7 empty] | 60.09 | 2835.9221 | 5.0075 | 19.6939 | 0.00016975 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 60 |  | 61.61 | [5 empty] | 0.83 | 350 | [7 empty] | 59.95 | 2822.723 | 4.9958 | 19.6022 | 0.00017014 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 64 |  | 65.67 | [5 empty] | 0.56 | 150 | [7 empty] | 64.55 | 3272.5205 | 5.3792 | 22.7258 | 0.00015802 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 64 |  | 65.67 | [5 empty] | 0.64 | 200 | [7 empty] | 64.39 | 3256.3174 | 5.3658 | 22.6133 | 0.00015841 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 64 |  | 65.67 | [5 empty] | 0.72 | 250 | [7 empty] | 64.23 | 3240.1545 | 5.3525 | 22.5011 | 0.0001588 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 64 |  | 65.67 | [5 empty] | 0.8 | 300 | [7 empty] | 64.07 | 3224.0319 | 5.3392 | 22.3891 | 0.0001592 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | B | Iron Pipe | 2 | Iron (Ductile) pipe | 64 |  | 65.67 | [5 empty] | 0.87 | 350 | [7 empty] | 63.93 | 3209.9576 | 5.3275 | 22.2914 | 0.00015955 | 0.00085 | [21 empty] | Pages 12-13 | Table 1 | AWWA C151/A21.51-17 | [7 empty] | Handbook of Cast Iron Pipe
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.125 |  | 0.405 |  |  |  |  | 5S | -- | [8 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5e-05 | [21 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.125 |  | 0.405 |  |  |  |  | 10S | 0.049 | [8 empty] | 0.307 | 0.074023 | 0.025583 | 0.00051405 | 0.0019544 | 5e-05 | [5 empty] | 0.19 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.125 |  | 0.405 |  |  |  |  | 40S | 0.068 | [8 empty] | 0.269 | 0.056832 | 0.022417 | 0.00039467 | 0.0022305 | 5e-05 | [5 empty] | 0.24 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.125 |  | 0.405 |  |  |  |  | 80S | 0.095 | [8 empty] | 0.215 | 0.036305 | 0.017917 | 0.00025212 | 0.0027907 | 5e-05 | [5 empty] | 0.31 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.25 |  | 0.54 |  |  |  |  | 5S | -- | [8 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5e-05 | [21 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.25 |  | 0.54 |  |  |  |  | 10S | 0.065 | [8 empty] | 0.41 | 0.13203 | 0.034167 | 0.00091684 | 0.0014634 | 5e-05 | [5 empty] | 0.33 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.25 |  | 0.54 |  |  |  |  | 40S | 0.088 | [8 empty] | 0.364 | 0.10406 | 0.030333 | 0.00072265 | 0.0016484 | 5e-05 | [5 empty] | 0.43 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.25 |  | 0.54 |  |  |  |  | 80S | 0.119 | [8 empty] | 0.302 | 0.071631 | 0.025167 | 0.00049744 | 0.0019868 | 5e-05 | [5 empty] | 0.54 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.375 |  | 0.675 |  |  |  |  | 5S | -- | [8 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5e-05 | [21 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.375 |  | 0.675 |  |  |  |  | 10S | 0.065 | [8 empty] | 0.545 | 0.23328 | 0.045417 | 0.00162 | 0.0011009 | 5e-05 | [5 empty] | 0.42 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.375 |  | 0.675 |  |  |  |  | 40S | 0.091 | [8 empty] | 0.493 | 0.19089 | 0.041083 | 0.0013256 | 0.001217 | 5e-05 | [5 empty] | 0.57 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.375 |  | 0.675 |  |  |  |  | 80S | 0.126 | [8 empty] | 0.423 | 0.14053 | 0.03525 | 0.00097591 | 0.0014184 | 5e-05 | [5 empty] | 0.74 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.5 |  | 0.84 |  |  |  |  | 5S | 0.065 | [8 empty] | 0.71 | 0.39592 | 0.059167 | 0.0027494 | 0.00084507 | 5e-05 | [5 empty] | 0.54 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.5 |  | 0.84 |  |  |  |  | 10S | 0.083 | [8 empty] | 0.674 | 0.35679 | 0.056167 | 0.0024777 | 0.00089021 | 5e-05 | [5 empty] | 0.67 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.5 |  | 0.84 |  |  |  |  | 40S | 0.109 | [8 empty] | 0.622 | 0.30386 | 0.051833 | 0.0021101 | 0.00096463 | 5e-05 | [5 empty] | 0.85 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.5 |  | 0.84 |  |  |  |  | 80S | 0.147 | [8 empty] | 0.546 | 0.23414 | 0.0455 | 0.001626 | 0.0010989 | 5e-05 | [5 empty] | 1.09 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.75 |  | 1.05 |  |  |  |  | 5S | 0.065 | [8 empty] | 0.92 | 0.66476 | 0.076667 | 0.0046164 | 0.00065217 | 5e-05 | [5 empty] | 0.68 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.75 |  | 1.05 |  |  |  |  | 10S | 0.083 | [8 empty] | 0.884 | 0.61375 | 0.073667 | 0.0042622 | 0.00067873 | 5e-05 | [5 empty] | 0.86 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.75 |  | 1.05 |  |  |  |  | 40S | 0.113 | [8 empty] | 0.824 | 0.53327 | 0.068667 | 0.0037032 | 0.00072816 | 5e-05 | [5 empty] | 1.13 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 0.75 |  | 1.05 |  |  |  |  | 80S | 0.154 | [8 empty] | 0.742 | 0.43241 | 0.061833 | 0.0030029 | 0.00080863 | 5e-05 | [5 empty] | 1.48 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 1 |  | 1.315 |  |  |  |  | 5S | 0.065 | [8 empty] | 1.185 | 1.1029 | 0.09875 | 0.0076589 | 0.00050633 | 5e-05 | [5 empty] | 0.87 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 1 |  | 1.315 |  |  |  |  | 10S | 0.109 | [8 empty] | 1.097 | 0.94516 | 0.091417 | 0.0065636 | 0.00054695 | 5e-05 | [5 empty] | 1.41 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 1 |  | 1.315 |  |  |  |  | 40S | 0.133 | [8 empty] | 1.049 | 0.86425 | 0.087417 | 0.0060018 | 0.00057197 | 5e-05 | [5 empty] | 1.68 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 1 |  | 1.315 |  |  |  |  | 80S | 0.179 | [8 empty] | 0.957 | 0.71931 | 0.07975 | 0.0049952 | 0.00062696 | 5e-05 | [5 empty] | 2.17 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 1.25 |  | 1.66 |  |  |  |  | 5S | 0.065 | [8 empty] | 1.53 | 1.8385 | 0.1275 | 0.012768 | 0.00039216 | 5e-05 | [5 empty] | 1.11 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 1.25 |  | 1.66 |  |  |  |  | 10S | 0.109 | [8 empty] | 1.442 | 1.6331 | 0.12017 | 0.011341 | 0.00041609 | 5e-05 | [5 empty] | 1.81 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 1.25 |  | 1.66 |  |  |  |  | 40S | 0.14 | [8 empty] | 1.38 | 1.4957 | 0.115 | 0.010387 | 0.00043478 | 5e-05 | [5 empty] | 2.27 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 1.25 |  | 1.66 |  |  |  |  | 80S | 0.191 | [8 empty] | 1.278 | 1.2828 | 0.1065 | 0.0089082 | 0.00046948 | 5e-05 | [5 empty] | 3 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 1.5 |  | 1.9 |  |  |  |  | 5S | 0.065 | [8 empty] | 1.77 | 2.4606 | 0.1475 | 0.017087 | 0.00033898 | 5e-05 | [5 empty] | 1.28 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 1.5 |  | 1.9 |  |  |  |  | 10S | 0.109 | [8 empty] | 1.682 | 2.222 | 0.14017 | 0.01543 | 0.00035672 | 5e-05 | [5 empty] | 2.09 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 1.5 |  | 1.9 |  |  |  |  | 40S | 0.145 | [8 empty] | 1.61 | 2.0358 | 0.13417 | 0.014138 | 0.00037267 | 5e-05 | [5 empty] | 2.72 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 1.5 |  | 1.9 |  |  |  |  | 80S | 0.2 | [8 empty] | 1.5 | 1.7671 | 0.125 | 0.012272 | 0.0004 | 5e-05 | [5 empty] | 3.63 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 2 |  | 2.375 |  |  |  |  | 5S | 0.065 | [8 empty] | 2.245 | 3.9584 | 0.18708 | 0.027489 | 0.00026726 | 5e-05 | [5 empty] | 1.61 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 2 |  | 2.375 |  |  |  |  | 10S | 0.109 | [8 empty] | 2.157 | 3.6542 | 0.17975 | 0.025376 | 0.00027816 | 5e-05 | [5 empty] | 2.64 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 2 |  | 2.375 |  |  |  |  | 40S | 0.154 | [8 empty] | 2.067 | 3.3556 | 0.17225 | 0.023303 | 0.00029028 | 5e-05 | [5 empty] | 3.66 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 2 |  | 2.375 |  |  |  |  | 80S | 0.218 | [8 empty] | 1.939 | 2.9529 | 0.16158 | 0.020506 | 0.00030944 | 5e-05 | [5 empty] | 5.03 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 2.5 |  | 2.875 |  |  |  |  | 5S | 0.083 | [8 empty] | 2.709 | 5.7638 | 0.22575 | 0.040026 | 0.00022148 | 5e-05 | [5 empty] | 2.48 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 2.5 |  | 2.875 |  |  |  |  | 10S | 0.12 | [8 empty] | 2.635 | 5.4532 | 0.21958 | 0.037869 | 0.0002277 | 5e-05 | [5 empty] | 3.53 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 2.5 |  | 2.875 |  |  |  |  | 40S | 0.203 | [8 empty] | 2.469 | 4.7878 | 0.20575 | 0.033248 | 0.00024301 | 5e-05 | [5 empty] | 5.8 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 2.5 |  | 2.875 |  |  |  |  | 80S | 0.276 | [8 empty] | 2.323 | 4.2383 | 0.19358 | 0.029432 | 0.00025829 | 5e-05 | [5 empty] | 7.67 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 3 |  | 3.5 |  |  |  |  | 5S | 0.083 | [8 empty] | 3.334 | 8.7301 | 0.27783 | 0.060626 | 0.00017996 | 5e-05 | [5 empty] | 3.03 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 3 |  | 3.5 |  |  |  |  | 10S | 0.12 | [8 empty] | 3.26 | 8.3469 | 0.27167 | 0.057965 | 0.00018405 | 5e-05 | [5 empty] | 4.34 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 3 |  | 3.5 |  |  |  |  | 40S | 0.216 | [8 empty] | 3.068 | 7.3927 | 0.25567 | 0.051338 | 0.00019557 | 5e-05 | [5 empty] | 7.58 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 3 |  | 3.5 |  |  |  |  | 80S | 0.3 | [8 empty] | 2.9 | 6.6052 | 0.24167 | 0.045869 | 0.0002069 | 5e-05 | [5 empty] | 10.26 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 3.5 |  | 4 |  |  |  |  | 5S | 0.083 | [8 empty] | 3.834 | 11.545 | 0.3195 | 0.080174 | 0.00015649 | 5e-05 | [5 empty] | 3.48 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 3.5 |  | 4 |  |  |  |  | 10S | 0.12 | [8 empty] | 3.76 | 11.1036 | 0.31333 | 0.077109 | 0.00015957 | 5e-05 | [5 empty] | 4.98 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 3.5 |  | 4 |  |  |  |  | 40S | 0.226 | [8 empty] | 3.548 | 9.8868 | 0.29567 | 0.068659 | 0.00016911 | 5e-05 | [5 empty] | 9.12 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 3.5 |  | 4 |  |  |  |  | 80S | 0.318 | [8 empty] | 3.364 | 8.888 | 0.28033 | 0.061722 | 0.00017836 | 5e-05 | [5 empty] | 12.52 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 4 |  | 4.5 |  |  |  |  | 5S | 0.083 | [8 empty] | 4.334 | 14.7526 | 0.36117 | 0.10245 | 0.00013844 | 5e-05 | [5 empty] | 3.92 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 4 |  | 4.5 |  |  |  |  | 10S | 0.12 | [8 empty] | 4.26 | 14.2531 | 0.355 | 0.09898 | 0.00014085 | 5e-05 | [5 empty] | 5.62 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 4 |  | 4.5 |  |  |  |  | 40S | 0.237 | [8 empty] | 4.026 | 12.7303 | 0.3355 | 0.088405 | 0.00014903 | 5e-05 | [5 empty] | 10.8 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 4 |  | 4.5 |  |  |  |  | 80S | 0.337 | [8 empty] | 3.826 | 11.4969 | 0.31883 | 0.079839 | 0.00015682 | 5e-05 | [5 empty] | 15 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 5 |  | 5.563 |  |  |  |  | 5S | 0.109 | [8 empty] | 5.345 | 22.4381 | 0.44542 | 0.15582 | 0.00011225 | 5e-05 | [5 empty] | 6.36 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 5 |  | 5.563 |  |  |  |  | 10S | 0.134 | [8 empty] | 5.295 | 22.0202 | 0.44125 | 0.15292 | 0.00011331 | 5e-05 | [5 empty] | 7.78 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 5 |  | 5.563 |  |  |  |  | 40S | 0.258 | [8 empty] | 5.047 | 20.0058 | 0.42058 | 0.13893 | 0.00011888 | 5e-05 | [5 empty] | 14.63 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 5 |  | 5.563 |  |  |  |  | 80S | 0.375 | [8 empty] | 4.813 | 18.1937 | 0.40108 | 0.12635 | 0.00012466 | 5e-05 | [5 empty] | 20.8 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 6 |  | 6.625 |  |  |  |  | 5S | 0.109 | [8 empty] | 6.407 | 32.2403 | 0.53392 | 0.22389 | 9.3648e-05 | 5e-05 | [5 empty] | 7.59 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 6 |  | 6.625 |  |  |  |  | 10S | 0.134 | [8 empty] | 6.357 | 31.7391 | 0.52975 | 0.22041 | 9.4384e-05 | 5e-05 | [5 empty] | 9.3 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 6 |  | 6.625 |  |  |  |  | 40S | 0.28 | [8 empty] | 6.065 | 28.8903 | 0.50542 | 0.20063 | 9.8928e-05 | 5e-05 | [5 empty] | 18.99 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 6 |  | 6.625 |  |  |  |  | 80S | 0.432 | [8 empty] | 5.761 | 26.0667 | 0.48008 | 0.18102 | 0.00010415 | 5e-05 | [5 empty] | 28.6 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 8 |  | 8.625 |  |  |  |  | 5S | 0.109 | [8 empty] | 8.407 | 55.5101 | 0.70058 | 0.38549 | 7.1369e-05 | 5e-05 | [5 empty] | 9.92 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 8 |  | 8.625 |  |  |  |  | 10S | 0.148 | [8 empty] | 8.329 | 54.4848 | 0.69408 | 0.37837 | 7.2037e-05 | 5e-05 | [5 empty] | 13.41 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 8 |  | 8.625 |  |  |  |  | 40S | 0.322 | [8 empty] | 7.981 | 50.027 | 0.66508 | 0.34741 | 7.5179e-05 | 5e-05 | [5 empty] | 28.58 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 8 |  | 8.625 |  |  |  |  | 80S | 0.5 | [8 empty] | 7.625 | 45.6635 | 0.63542 | 0.31711 | 7.8689e-05 | 5e-05 | [5 empty] | 43.34 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 10 |  | 10.75 |  |  |  |  | 5S | 0.134 | [8 empty] | 10.482 | 86.2935 | 0.8735 | 0.59926 | 5.7241e-05 | 5e-05 | [5 empty] | 15.21 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 10 |  | 10.75 |  |  |  |  | 10S | 0.165 | [8 empty] | 10.42 | 85.2757 | 0.86833 | 0.59219 | 5.7582e-05 | 5e-05 | [5 empty] | 18.67 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 10 |  | 10.75 |  |  |  |  | 40S | 0.365 | [8 empty] | 10.02 | 78.8543 | 0.835 | 0.5476 | 5.988e-05 | 5e-05 | [5 empty] | 40.52 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 10 |  | 10.75 |  |  |  |  | 80S | 0.5 | [8 empty] | 9.75 | 74.6619 | 0.8125 | 0.51849 | 6.1538e-05 | 5e-05 | [5 empty] | 54.79 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 12 |  | 12.75 |  |  |  |  | 5S | 0.156 | [8 empty] | 12.438 | 121.5041 | 1.0365 | 0.84378 | 4.8239e-05 | 5e-05 | [5 empty] | 21 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 12 |  | 12.75 |  |  |  |  | 10S | 0.18 | [8 empty] | 12.39 | 120.5681 | 1.0325 | 0.83728 | 4.8426e-05 | 5e-05 | [5 empty] | 24.19 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 12 |  | 12.75 |  |  |  |  | 40S | 0.375 | [8 empty] | 12 | 113.0973 | 1 | 0.7854 | 5e-05 | 5e-05 | [5 empty] | 49.61 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 12 |  | 12.75 |  |  |  |  | 80S | 0.5 | [8 empty] | 11.75 | 108.434 | 0.97917 | 0.75301 | 5.1064e-05 | 5e-05 | [5 empty] | 65.48 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 14 |  | 14 |  |  |  |  | 5S | 0.156 | [8 empty] | 13.688 | 147.1533 | 1.1407 | 1.0219 | 4.3834e-05 | 5e-05 | [5 empty] | 23.09 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 14 |  | 14 |  |  |  |  | 10S | 0.188 | [8 empty] | 13.624 | 145.7804 | 1.1353 | 1.0124 | 4.404e-05 | 5e-05 | [5 empty] | 27.76 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 14 |  | 14 |  |  |  |  | 40S | 0.375 | [8 empty] | 13.25 | 137.8865 | 1.1042 | 0.95754 | 4.5283e-05 | 5e-05 | [5 empty] | 54.62 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 14 |  | 14 |  |  |  |  | 80S | 0.5 | [8 empty] | 13 | 132.7323 | 1.0833 | 0.92175 | 4.6154e-05 | 5e-05 | [5 empty] | 72.16 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 16 |  | 16 |  |  |  |  | 5S | 0.165 | [8 empty] | 15.67 | 192.8537 | 1.3058 | 1.3393 | 3.829e-05 | 5e-05 | [5 empty] | 27.93 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 16 |  | 16 |  |  |  |  | 10S | 0.188 | [8 empty] | 15.624 | 191.7231 | 1.302 | 1.3314 | 3.8402e-05 | 5e-05 | [5 empty] | 31.78 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 16 |  | 16 |  |  |  |  | 40S | 0.375 | [8 empty] | 15.25 | 182.6542 | 1.2708 | 1.2684 | 3.9344e-05 | 5e-05 | [5 empty] | 62.64 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 16 |  | 16 |  |  |  |  | 80S | 0.5 | [8 empty] | 15 | 176.7146 | 1.25 | 1.2272 | 4e-05 | 5e-05 | [5 empty] | 82.85 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 18 |  | 18 |  |  |  |  | 5S | 0.165 | [8 empty] | 17.67 | 245.224 | 1.4725 | 1.7029 | 3.3956e-05 | 5e-05 | [5 empty] | 31.46 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 18 |  | 18 |  |  |  |  | 10S | 0.188 | [8 empty] | 17.624 | 243.9489 | 1.4687 | 1.6941 | 3.4044e-05 | 5e-05 | [5 empty] | 35.8 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 18 |  | 18 |  |  |  |  | 40S | 0.375 | [8 empty] | 17.25 | 233.705 | 1.4375 | 1.623 | 3.4783e-05 | 5e-05 | [5 empty] | 70.65 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 18 |  | 18 |  |  |  |  | 80S | 0.5 | [8 empty] | 17 | 226.9801 | 1.4167 | 1.5763 | 3.5294e-05 | 5e-05 | [5 empty] | 93.54 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 20 |  | 20 |  |  |  |  | 5S | 0.188 | [8 empty] | 19.624 | 302.4579 | 1.6353 | 2.1004 | 3.0575e-05 | 5e-05 | [5 empty] | 39.82 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 20 |  | 20 |  |  |  |  | 10S | 0.218 | [8 empty] | 19.564 | 300.6112 | 1.6303 | 2.0876 | 3.0669e-05 | 5e-05 | [5 empty] | 46.1 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 20 |  | 20 |  |  |  |  | 40S | 0.375 | [8 empty] | 19.25 | 291.0391 | 1.6042 | 2.0211 | 3.1169e-05 | 5e-05 | [5 empty] | 78.67 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 20 |  | 20 |  |  |  |  | 80S | 0.5 | [8 empty] | 19 | 283.5287 | 1.5833 | 1.9689 | 3.1579e-05 | 5e-05 | [5 empty] | 104.23 | [15 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 22 |  | 22 |  |  |  |  | 5S | 0.188 | [8 empty] | 21.624 | 367.2501 | 1.802 | 2.5503 | 2.7747e-05 | 5e-05 | [21 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 22 |  | 22 |  |  |  |  | 10S | 0.218 | [8 empty] | 21.564 | 365.2149 | 1.797 | 2.5362 | 2.7824e-05 | 5e-05 | [21 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 22 |  | 22 |  |  |  |  | 40S | -- | [8 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5e-05 | [21 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 22 |  | 22 |  |  |  |  | 80S | -- | [8 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5e-05 | [21 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 24 |  | 24 |  |  |  |  | 5S | 0.218 | [8 empty] | 23.564 | 436.1018 | 1.9637 | 3.0285 | 2.5463e-05 | 5e-05 | [21 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 24 |  | 24 |  |  |  |  | 10S | 0.25 | [8 empty] | 23.5 | 433.7361 | 1.9583 | 3.0121 | 2.5532e-05 | 5e-05 | [21 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 24 |  | 24 |  |  |  |  | 40S | 0.375 | [8 empty] | 23.25 | 424.5568 | 1.9375 | 2.9483 | 2.5806e-05 | 5e-05 | [21 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 24 |  | 24 |  |  |  |  | 80S | 0.5 | [8 empty] | 23 | 415.4756 | 1.9167 | 2.8852 | 2.6087e-05 | 5e-05 | [21 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 30 |  | 30 |  |  |  |  | 5S | 0.25 | [8 empty] | 29.5 | 683.4928 | 2.4583 | 4.7465 | 2.0339e-05 | 5e-05 | [21 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 30 |  | 30 |  |  |  |  | 10S | 0.312 | [8 empty] | 29.376 | 677.7589 | 2.448 | 4.7067 | 2.0425e-05 | 5e-05 | [21 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 30 |  | 30 |  |  |  |  | 40S | -- | [8 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5e-05 | [21 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Stainless Steel Pipe | 1A | Stainless steel pipe - welded and seamless | 30 |  | 30 |  |  |  |  | 80S | -- | [8 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5e-05 | [21 empty] | Pages 3 - 5 | Table 2-1 | ANSI/ASME B36.19M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.125 | 6 | 0.405 |  |  |  |  | 10 | 0.049 | [8 empty] | 0.307 | 0.074023 | 0.025583 | 0.00051405 | 0.0058632 | 0.00015 | [5 empty] | 0.19 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.125 | 6 | 0.405 |  |  |  |  | 30 | 0.057 | [8 empty] | 0.291 | 0.066508 | 0.02425 | 0.00046186 | 0.0061856 | 0.00015 | [5 empty] | 0.21 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.125 | 6 | 0.405 |  |  |  | STD | 40 | 0.068 | [8 empty] | 0.269 | 0.056832 | 0.022417 | 0.00039467 | 0.0066914 | 0.00015 | [5 empty] | 0.24 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.125 | 6 | 0.405 |  |  |  | XS | 80 | 0.095 | [8 empty] | 0.215 | 0.036305 | 0.017917 | 0.00025212 | 0.0083721 | 0.00015 | [5 empty] | 0.31 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.125 | 6 | 0.405 |  |  |  |  | 160 | 0.124 | [8 empty] | 0.157 | 0.019359 | 0.013083 | 0.00013444 | 0.011465 | 0.00015 | [5 empty] | 0.37 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.125 | 6 | 0.405 |  |  |  | XXS |  | 0.19 | [8 empty] | 0.025 | 0.00049087 | 0.0020833 | 3.4088e-06 | 0.072 | 0.00015 | [5 empty] | 0.44 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.25 | 8 | 0.54 |  |  |  |  | 10 | 0.065 | [8 empty] | 0.41 | 0.13203 | 0.034167 | 0.00091684 | 0.0043902 | 0.00015 | [5 empty] | 0.33 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.25 | 8 | 0.54 |  |  |  |  | 30 | 0.073 | [8 empty] | 0.394 | 0.12192 | 0.032833 | 0.00084668 | 0.0045685 | 0.00015 | [5 empty] | 0.36 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.25 | 8 | 0.54 |  |  |  | STD | 40 | 0.088 | [8 empty] | 0.364 | 0.10406 | 0.030333 | 0.00072265 | 0.0049451 | 0.00015 | [5 empty] | 0.43 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.25 | 8 | 0.54 |  |  |  | XS | 80 | 0.119 | [8 empty] | 0.302 | 0.071631 | 0.025167 | 0.00049744 | 0.0059603 | 0.00015 | [5 empty] | 0.54 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 2 | Steel pipe - welded and seamless wrought | 0.25 | 8 | 0.54 |  |  |  |  | 160 | 0.145 | [8 empty] | 0.25 | 0.049087 | 0.020833 | 0.00034088 | 0.0072 | 0.00015 | [5 empty] | 0.61 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 3 | Steel pipe - welded and seamless wrought | 0.25 | 8 | 0.54 |  |  |  | XXS |  | 0.238 | [8 empty] | 0.064 | 0.003217 | 0.0053333 | 2.234e-05 | 0.028125 | 0.00015 | [5 empty] | 0.77 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.375 | 10 | 0.675 |  |  |  |  | 10 | 0.065 | [8 empty] | 0.545 | 0.23328 | 0.045417 | 0.00162 | 0.0033028 | 0.00015 | [5 empty] | 0.42 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 0 | Steel pipe - welded and seamless wrought | 0.375 | 10 | 0.675 |  |  |  |  | 30 | 0.073 | [8 empty] | 0.529 | 0.21979 | 0.044083 | 0.0015263 | 0.0034026 | 0.00015 | [5 empty] | 0.47 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.375 | 10 | 0.675 |  |  |  | STD | 40 | 0.091 | [8 empty] | 0.493 | 0.19089 | 0.041083 | 0.0013256 | 0.0036511 | 0.00015 | [5 empty] | 0.57 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.375 | 10 | 0.675 |  |  |  | XS | 80 | 0.126 | [8 empty] | 0.423 | 0.14053 | 0.03525 | 0.00097591 | 0.0042553 | 0.00015 | [5 empty] | 0.74 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 2 | Steel pipe - welded and seamless wrought | 0.375 | 10 | 0.675 |  |  |  |  | 160 | 0.158 | [8 empty] | 0.359 | 0.10122 | 0.029917 | 0.00070294 | 0.0050139 | 0.00015 | [5 empty] | 0.87 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 3 | Steel pipe - welded and seamless wrought | 0.375 | 10 | 0.675 |  |  |  | XXS |  | 0.252 | [8 empty] | 0.171 | 0.022966 | 0.01425 | 0.00015948 | 0.010526 | 0.00015 | [5 empty] | 1.14 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.5 | 15 | 0.84 |  |  |  |  | 5 | 0.065 | [8 empty] | 0.71 | 0.39592 | 0.059167 | 0.0027494 | 0.0025352 | 0.00015 | [5 empty] | 0.54 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.5 | 15 | 0.84 |  |  |  |  | 10 | 0.083 | [8 empty] | 0.674 | 0.35679 | 0.056167 | 0.0024777 | 0.0026706 | 0.00015 | [5 empty] | 0.67 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.5 | 15 | 0.84 |  |  |  |  | 30 | 0.095 | [8 empty] | 0.65 | 0.33183 | 0.054167 | 0.0023044 | 0.0027692 | 0.00015 | [5 empty] | 0.76 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.5 | 15 | 0.84 |  |  |  | STD | 40 | 0.109 | [8 empty] | 0.622 | 0.30386 | 0.051833 | 0.0021101 | 0.0028939 | 0.00015 | [5 empty] | 0.85 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.5 | 15 | 0.84 |  |  |  | XS | 80 | 0.147 | [8 empty] | 0.546 | 0.23414 | 0.0455 | 0.001626 | 0.0032967 | 0.00015 | [5 empty] | 1.09 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.5 | 15 | 0.84 |  |  |  |  | 160 | 0.188 | [8 empty] | 0.464 | 0.16909 | 0.038667 | 0.0011743 | 0.0038793 | 0.00015 | [5 empty] | 1.31 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.5 | 15 | 0.84 |  |  |  | XXS |  | 0.294 | [8 empty] | 0.252 | 0.049876 | 0.021 | 0.00034636 | 0.0071429 | 0.00015 | [5 empty] | 1.72 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.75 | 20 | 1.05 |  |  |  |  | 5 | 0.065 | [8 empty] | 0.92 | 0.66476 | 0.076667 | 0.0046164 | 0.0019565 | 0.00015 | [5 empty] | 0.68 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.75 | 20 | 1.05 |  |  |  |  | 10 | 0.083 | [8 empty] | 0.884 | 0.61375 | 0.073667 | 0.0042622 | 0.0020362 | 0.00015 | [5 empty] | 0.86 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.75 | 20 | 1.05 |  |  |  |  | 30 | 0.095 | [8 empty] | 0.86 | 0.58088 | 0.071667 | 0.0040339 | 0.002093 | 0.00015 | [5 empty] | 0.97 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.75 | 20 | 1.05 |  |  |  | STD | 40 | 0.113 | [8 empty] | 0.824 | 0.53327 | 0.068667 | 0.0037032 | 0.0021845 | 0.00015 | [5 empty] | 1.13 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.75 | 20 | 1.05 |  |  |  | XS | 80 | 0.154 | [8 empty] | 0.742 | 0.43241 | 0.061833 | 0.0030029 | 0.0024259 | 0.00015 | [5 empty] | 1.48 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.75 | 20 | 1.05 |  |  |  |  | 160 | 0.219 | [8 empty] | 0.612 | 0.29417 | 0.051 | 0.0020428 | 0.0029412 | 0.00015 | [5 empty] | 1.95 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 0.75 | 20 | 1.05 |  |  |  | XXS |  | 0.308 | [8 empty] | 0.434 | 0.14793 | 0.036167 | 0.0010273 | 0.0041475 | 0.00015 | [5 empty] | 2.44 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1 | 25 | 1.315 |  |  |  |  | 5 | 0.065 | [8 empty] | 1.185 | 1.1029 | 0.09875 | 0.0076589 | 0.001519 | 0.00015 | [5 empty] | 0.87 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1 | 25 | 1.315 |  |  |  |  | 10 | 0.109 | [8 empty] | 1.097 | 0.94516 | 0.091417 | 0.0065636 | 0.0016408 | 0.00015 | [5 empty] | 1.41 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1 | 25 | 1.315 |  |  |  |  | 30 | 0.114 | [8 empty] | 1.087 | 0.928 | 0.090583 | 0.0064445 | 0.0016559 | 0.00015 | [5 empty] | 1.46 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1 | 25 | 1.315 |  |  |  | STD | 40 | 0.133 | [8 empty] | 1.049 | 0.86425 | 0.087417 | 0.0060018 | 0.0017159 | 0.00015 | [5 empty] | 1.68 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1 | 25 | 1.315 |  |  |  | XS | 80 | 0.179 | [8 empty] | 0.957 | 0.71931 | 0.07975 | 0.0049952 | 0.0018809 | 0.00015 | [5 empty] | 2.17 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1 | 25 | 1.315 |  |  |  |  | 160 | 0.25 | [8 empty] | 0.815 | 0.52168 | 0.067917 | 0.0036228 | 0.0022086 | 0.00015 | [5 empty] | 2.85 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1 | 25 | 1.315 |  |  |  | XXS |  | 0.358 | [8 empty] | 0.599 | 0.2818 | 0.049917 | 0.001957 | 0.003005 | 0.00015 | [5 empty] | 3.66 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1.25 | 32 | 1.66 |  |  |  |  | 5 | 0.065 | [8 empty] | 1.53 | 1.8385 | 0.1275 | 0.012768 | 0.0011765 | 0.00015 | [5 empty] | 1.11 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1.25 | 32 | 1.66 |  |  |  |  | 10 | 0.109 | [8 empty] | 1.442 | 1.6331 | 0.12017 | 0.011341 | 0.0012483 | 0.00015 | [5 empty] | 1.81 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1.25 | 32 | 1.66 |  |  |  |  | 30 | 0.117 | [8 empty] | 1.426 | 1.5971 | 0.11883 | 0.011091 | 0.0012623 | 0.00015 | [5 empty] | 1.93 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1.25 | 32 | 1.66 |  |  |  | STD | 40 | 0.14 | [8 empty] | 1.38 | 1.4957 | 0.115 | 0.010387 | 0.0013043 | 0.00015 | [5 empty] | 2.27 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1.25 | 32 | 1.66 |  |  |  | XS | 80 | 0.191 | [8 empty] | 1.278 | 1.2828 | 0.1065 | 0.0089082 | 0.0014085 | 0.00015 | [5 empty] | 3 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1.25 | 32 | 1.66 |  |  |  |  | 160 | 0.25 | [8 empty] | 1.16 | 1.0568 | 0.096667 | 0.0073391 | 0.0015517 | 0.00015 | [5 empty] | 3.77 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1.25 | 32 | 1.66 |  |  |  | XXS |  | 0.382 | [8 empty] | 0.896 | 0.63053 | 0.074667 | 0.0043787 | 0.0020089 | 0.00015 | [5 empty] | 5.22 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1.5 | 40 | 1.9 |  |  |  |  | 5 | 0.065 | [8 empty] | 1.77 | 2.4606 | 0.1475 | 0.017087 | 0.0010169 | 0.00015 | [5 empty] | 1.28 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1.5 | 40 | 1.9 |  |  |  |  | 10 | 0.109 | [8 empty] | 1.682 | 2.222 | 0.14017 | 0.01543 | 0.0010702 | 0.00015 | [5 empty] | 2.09 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1.5 | 40 | 1.9 |  |  |  |  | 30 | 0.125 | [8 empty] | 1.65 | 2.1382 | 0.1375 | 0.014849 | 0.0010909 | 0.00015 | [5 empty] | 2.37 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1.5 | 40 | 1.9 |  |  |  | STD | 40 | 0.145 | [8 empty] | 1.61 | 2.0358 | 0.13417 | 0.014138 | 0.001118 | 0.00015 | [5 empty] | 2.72 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1.5 | 40 | 1.9 |  |  |  | XS | 80 | 0.2 | [8 empty] | 1.5 | 1.7671 | 0.125 | 0.012272 | 0.0012 | 0.00015 | [5 empty] | 3.63 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1.5 | 40 | 1.9 |  |  |  |  | 160 | 0.281 | [8 empty] | 1.338 | 1.4061 | 0.1115 | 0.0097643 | 0.0013453 | 0.00015 | [5 empty] | 4.86 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 1.5 | 40 | 1.9 |  |  |  | XXS |  | 0.4 | [8 empty] | 1.1 | 0.95033 | 0.091667 | 0.0065995 | 0.0016364 | 0.00015 | [5 empty] | 6.41 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2 | 50 | 2.375 |  |  |  |  | 5 | 0.065 | [8 empty] | 2.245 | 3.9584 | 0.18708 | 0.027489 | 0.00080178 | 0.00015 | [5 empty] | 1.61 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2 | 50 | 2.375 | [5 empty] | 0.083 | [8 empty] | 2.209 | 3.8325 | 0.18408 | 0.026615 | 0.00081485 | 0.00015 | [5 empty] | 2.03 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2 | 50 | 2.375 |  |  |  |  | 10 | 0.109 | [8 empty] | 2.157 | 3.6542 | 0.17975 | 0.025376 | 0.00083449 | 0.00015 | [5 empty] | 2.64 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2 | 50 | 2.375 |  |  |  |  | 30 | 0.125 | [8 empty] | 2.125 | 3.5466 | 0.17708 | 0.024629 | 0.00084706 | 0.00015 | [5 empty] | 3.01 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2 | 50 | 2.375 | [5 empty] | 0.141 | [8 empty] | 2.093 | 3.4406 | 0.17442 | 0.023893 | 0.00086001 | 0.00015 | [5 empty] | 3.37 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2 | 50 | 2.375 |  |  |  | STD | 40 | 0.154 | [8 empty] | 2.067 | 3.3556 | 0.17225 | 0.023303 | 0.00087083 | 0.00015 | [5 empty] | 3.66 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2 | 50 | 2.375 | [5 empty] | 0.172 | [8 empty] | 2.031 | 3.2397 | 0.16925 | 0.022498 | 0.00088626 | 0.00015 | [5 empty] | 4.05 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2 | 50 | 2.375 | [5 empty] | 0.188 | [8 empty] | 1.999 | 3.1385 | 0.16658 | 0.021795 | 0.00090045 | 0.00015 | [5 empty] | 4.4 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2 | 50 | 2.375 |  |  |  | XS | 80 | 0.218 | [8 empty] | 1.939 | 2.9529 | 0.16158 | 0.020506 | 0.00092831 | 0.00015 | [5 empty] | 5.03 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2 | 50 | 2.375 | [5 empty] | 0.25 | [8 empty] | 1.875 | 2.7612 | 0.15625 | 0.019175 | 0.00096 | 0.00015 | [5 empty] | 5.68 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2 | 50 | 2.375 | [5 empty] | 0.281 | [8 empty] | 1.813 | 2.5816 | 0.15108 | 0.017928 | 0.00099283 | 0.00015 | [5 empty] | 6.29 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2 | 50 | 2.375 |  |  |  |  | 160 | 0.344 | [8 empty] | 1.687 | 2.2352 | 0.14058 | 0.015522 | 0.001067 | 0.00015 | [5 empty] | 7.47 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2 | 50 | 2.375 |  |  |  | XXS |  | 0.436 | [8 empty] | 1.503 | 1.7742 | 0.12525 | 0.012321 | 0.0011976 | 0.00015 | [5 empty] | 9.04 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2.5 | 65 | 2.875 |  |  |  |  | 5 | 0.083 | [8 empty] | 2.709 | 5.7638 | 0.22575 | 0.040026 | 0.00066445 | 0.00015 | [5 empty] | 2.48 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2.5 | 65 | 2.875 | [5 empty] | 0.109 | [8 empty] | 2.657 | 5.5446 | 0.22142 | 0.038504 | 0.00067746 | 0.00015 | [5 empty] | 3.22 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2.5 | 65 | 2.875 |  |  |  |  | 10 | 0.12 | [8 empty] | 2.635 | 5.4532 | 0.21958 | 0.037869 | 0.00068311 | 0.00015 | [5 empty] | 3.53 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2.5 | 65 | 2.875 | [5 empty] | 0.125 | [8 empty] | 2.625 | 5.4119 | 0.21875 | 0.037583 | 0.00068571 | 0.00015 | [5 empty] | 3.67 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2.5 | 65 | 2.875 | [5 empty] | 0.141 | [8 empty] | 2.593 | 5.2807 | 0.21608 | 0.036672 | 0.00069418 | 0.00015 | [5 empty] | 4.12 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2.5 | 65 | 2.875 | [5 empty] | 0.156 | [8 empty] | 2.563 | 5.1593 | 0.21358 | 0.035828 | 0.0007023 | 0.00015 | [5 empty] | 4.53 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2.5 | 65 | 2.875 | [5 empty] | 0.172 | [8 empty] | 2.531 | 5.0312 | 0.21092 | 0.034939 | 0.00071118 | 0.00015 | [5 empty] | 4.97 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2.5 | 65 | 2.875 |  |  |  |  | 30 | 0.188 | [8 empty] | 2.499 | 4.9048 | 0.20825 | 0.034061 | 0.00072029 | 0.00015 | [5 empty] | 5.4 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2.5 | 65 | 2.875 |  |  |  | STD | 40 | 0.203 | [8 empty] | 2.469 | 4.7878 | 0.20575 | 0.033248 | 0.00072904 | 0.00015 | [5 empty] | 5.8 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2.5 | 65 | 2.875 | [5 empty] | 0.216 | [8 empty] | 2.443 | 4.6875 | 0.20358 | 0.032552 | 0.0007368 | 0.00015 | [5 empty] | 6.14 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2.5 | 65 | 2.875 | [5 empty] | 0.25 | [8 empty] | 2.375 | 4.4301 | 0.19792 | 0.030765 | 0.00075789 | 0.00015 | [5 empty] | 7.02 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2.5 | 65 | 2.875 |  |  |  | XS | 80 | 0.276 | [8 empty] | 2.323 | 4.2383 | 0.19358 | 0.029432 | 0.00077486 | 0.00015 | [5 empty] | 7.67 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2.5 | 65 | 2.875 |  |  |  |  | 160 | 0.375 | [8 empty] | 2.125 | 3.5466 | 0.17708 | 0.024629 | 0.00084706 | 0.00015 | [5 empty] | 10.02 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 2.5 | 65 | 2.875 |  |  |  | XXS |  | 0.552 | [8 empty] | 1.771 | 2.4634 | 0.14758 | 0.017107 | 0.0010164 | 0.00015 | [5 empty] | 13.71 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3 | 80 | 3.5 |  |  |  |  | 5 | 0.083 | [8 empty] | 3.334 | 8.7301 | 0.27783 | 0.060626 | 0.00053989 | 0.00015 | [5 empty] | 3.03 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3 | 80 | 3.5 | [5 empty] | 0.109 | [8 empty] | 3.282 | 8.4599 | 0.2735 | 0.05875 | 0.00054845 | 0.00015 | [5 empty] | 3.95 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3 | 80 | 3.5 |  |  |  |  | 10 | 0.12 | [8 empty] | 3.26 | 8.3469 | 0.27167 | 0.057965 | 0.00055215 | 0.00015 | [5 empty] | 4.34 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3 | 80 | 3.5 | [5 empty] | 0.125 | [8 empty] | 3.25 | 8.2958 | 0.27083 | 0.05761 | 0.00055385 | 0.00015 | [5 empty] | 4.51 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3 | 80 | 3.5 | [5 empty] | 0.141 | [8 empty] | 3.218 | 8.1332 | 0.26817 | 0.056481 | 0.00055935 | 0.00015 | [5 empty] | 5.06 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3 | 80 | 3.5 | [5 empty] | 0.156 | [8 empty] | 3.188 | 7.9823 | 0.26567 | 0.055432 | 0.00056462 | 0.00015 | [5 empty] | 5.58 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3 | 80 | 3.5 | [5 empty] | 0.172 | [8 empty] | 3.156 | 7.8228 | 0.263 | 0.054325 | 0.00057034 | 0.00015 | [5 empty] | 6.12 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3 | 80 | 3.5 |  |  |  |  | 30 | 0.188 | [8 empty] | 3.124 | 7.665 | 0.26033 | 0.053229 | 0.00057618 | 0.00015 | [5 empty] | 6.66 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3 | 80 | 3.5 |  |  |  | STD | 40 | 0.216 | [8 empty] | 3.068 | 7.3927 | 0.25567 | 0.051338 | 0.0005867 | 0.00015 | [5 empty] | 7.58 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3 | 80 | 3.5 | [5 empty] | 0.25 | [8 empty] | 3 | 7.0686 | 0.25 | 0.049087 | 0.0006 | 0.00015 | [5 empty] | 8.69 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3 | 80 | 3.5 | [5 empty] | 0.281 | [8 empty] | 2.938 | 6.7794 | 0.24483 | 0.047079 | 0.00061266 | 0.00015 | [5 empty] | 9.67 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3 | 80 | 3.5 |  |  |  | XS | 80 | 0.3 | [8 empty] | 2.9 | 6.6052 | 0.24167 | 0.045869 | 0.00062069 | 0.00015 | [5 empty] | 10.26 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3 | 80 | 3.5 |  |  |  |  | 160 | 0.438 | [8 empty] | 2.624 | 5.4078 | 0.21867 | 0.037554 | 0.00068598 | 0.00015 | [5 empty] | 14.34 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3 | 80 | 3.5 |  |  |  | XXS |  | 0.6 | [8 empty] | 2.3 | 4.1548 | 0.19167 | 0.028852 | 0.00078261 | 0.00015 | [5 empty] | 18.6 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3.5 | 90 | 4 |  |  |  |  | 5 | 0.083 | [8 empty] | 3.834 | 11.545 | 0.3195 | 0.080174 | 0.00046948 | 0.00015 | [5 empty] | 3.48 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3.5 | 90 | 4 | [5 empty] | 0.109 | [8 empty] | 3.782 | 11.234 | 0.31517 | 0.078014 | 0.00047594 | 0.00015 | [5 empty] | 4.53 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3.5 | 90 | 4 |  |  |  |  | 10 | 0.12 | [8 empty] | 3.76 | 11.1036 | 0.31333 | 0.077109 | 0.00047872 | 0.00015 | [5 empty] | 4.98 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3.5 | 90 | 4 | [5 empty] | 0.125 | [8 empty] | 3.75 | 11.0447 | 0.3125 | 0.076699 | 0.00048 | 0.00015 | [5 empty] | 5.18 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3.5 | 90 | 4 | [5 empty] | 0.141 | [8 empty] | 3.718 | 10.857 | 0.30983 | 0.075396 | 0.00048413 | 0.00015 | [5 empty] | 5.82 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3.5 | 90 | 4 | [5 empty] | 0.156 | [8 empty] | 3.688 | 10.6825 | 0.30733 | 0.074184 | 0.00048807 | 0.00015 | [5 empty] | 6.41 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3.5 | 90 | 4 | [5 empty] | 0.172 | [8 empty] | 3.656 | 10.4979 | 0.30467 | 0.072902 | 0.00049234 | 0.00015 | [5 empty] | 7.04 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3.5 | 90 | 4 |  |  |  |  | 30 | 0.188 | [8 empty] | 3.624 | 10.3149 | 0.302 | 0.071631 | 0.00049669 | 0.00015 | [5 empty] | 7.66 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3.5 | 90 | 4 |  |  |  | STD | 40 | 0.226 | [8 empty] | 3.548 | 9.8868 | 0.29567 | 0.068659 | 0.00050733 | 0.00015 | [5 empty] | 9.12 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3.5 | 90 | 4 | [5 empty] | 0.25 | [8 empty] | 3.5 | 9.6211 | 0.29167 | 0.066813 | 0.00051429 | 0.00015 | [5 empty] | 10.02 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3.5 | 90 | 4 | [5 empty] | 0.281 | [8 empty] | 3.438 | 9.2833 | 0.2865 | 0.064467 | 0.00052356 | 0.00015 | [5 empty] | 11.17 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3.5 | 90 | 4 |  |  |  | XS | 80 | 0.318 | [8 empty] | 3.364 | 8.888 | 0.28033 | 0.061722 | 0.00053508 | 0.00015 | [5 empty] | 12.52 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 3.5 | 90 | 4 |  |  |  |  | 80S | 0.318 | [8 empty] | 3.364 | 8.888 | 0.28033 | 0.061722 | 0.00053508 | 0.00015 | [5 empty] | 12.52 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 4 | 100 | 4.5 |  |  |  |  | 5 | 0.083 | [8 empty] | 4.334 | 14.7526 | 0.36117 | 0.10245 | 0.00041532 | 0.00015 | [5 empty] | 3.92 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 4 | 100 | 4.5 | [5 empty] | 0.109 | [8 empty] | 4.282 | 14.4007 | 0.35683 | 0.1 | 0.00042036 | 0.00015 | [5 empty] | 5.12 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 4 | 100 | 4.5 |  |  |  |  | 10 | 0.12 | [8 empty] | 4.26 | 14.2531 | 0.355 | 0.09898 | 0.00042254 | 0.00015 | [5 empty] | 5.62 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 4 | 100 | 4.5 | [5 empty] | 0.125 | [8 empty] | 4.25 | 14.1863 | 0.35417 | 0.098516 | 0.00042353 | 0.00015 | [5 empty] | 5.85 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 4 | 100 | 4.5 | [5 empty] | 0.141 | [8 empty] | 4.218 | 13.9734 | 0.3515 | 0.097038 | 0.00042674 | 0.00015 | [5 empty] | 6.57 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 4 | 100 | 4.5 | [5 empty] | 0.156 | [8 empty] | 4.188 | 13.7754 | 0.349 | 0.095662 | 0.0004298 | 0.00015 | [5 empty] | 7.24 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 4 | 100 | 4.5 | [5 empty] | 0.172 | [8 empty] | 4.156 | 13.5657 | 0.34633 | 0.094206 | 0.00043311 | 0.00015 | [5 empty] | 7.96 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 4 | 100 | 4.5 |  |  |  |  | 30 | 0.188 | [8 empty] | 4.124 | 13.3576 | 0.34367 | 0.092761 | 0.00043647 | 0.00015 | [5 empty] | 8.67 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 4 | 100 | 4.5 | [5 empty] | 0.203 | [8 empty] | 4.094 | 13.1639 | 0.34117 | 0.091416 | 0.00043967 | 0.00015 | [5 empty] | 9.32 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 4 | 100 | 4.5 | [5 empty] | 0.219 | [8 empty] | 4.062 | 12.9589 | 0.3385 | 0.089993 | 0.00044313 | 0.00015 | [5 empty] | 10.02 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 4 | 100 | 4.5 |  |  |  |  | 40 | 0.237 | [8 empty] | 4.026 | 12.7303 | 0.3355 | 0.088405 | 0.00044709 | 0.00015 | [5 empty] | 10.8 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 4 | 100 | 4.5 | [5 empty] | 0.25 | [8 empty] | 4 | 12.5664 | 0.33333 | 0.087266 | 0.00045 | 0.00015 | [5 empty] | 11.36 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 4 | 100 | 4.5 | [5 empty] | 0.281 | [8 empty] | 3.938 | 12.1798 | 0.32817 | 0.084582 | 0.00045708 | 0.00015 | [5 empty] | 12.67 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 4 | 100 | 4.5 | [5 empty] | 0.312 | [8 empty] | 3.876 | 11.7993 | 0.323 | 0.08194 | 0.0004644 | 0.00015 | [5 empty] | 13.97 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 4 | 100 | 4.5 |  |  |  | XS | 80 | 0.337 | [8 empty] | 3.826 | 11.4969 | 0.31883 | 0.079839 | 0.00047047 | 0.00015 | [5 empty] | 15 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 4 | 100 | 4.5 |  |  |  |  | 120 | 0.438 | [8 empty] | 3.624 | 10.3149 | 0.302 | 0.071631 | 0.00049669 | 0.00015 | [5 empty] | 19.02 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 4 | 100 | 4.5 |  |  |  |  | 160 | 0.531 | [8 empty] | 3.438 | 9.2833 | 0.2865 | 0.064467 | 0.00052356 | 0.00015 | [5 empty] | 22.53 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 4 | 100 | 4.5 |  |  |  | XXS |  | 0.674 | [8 empty] | 3.152 | 7.803 | 0.26267 | 0.054188 | 0.00057107 | 0.00015 | [5 empty] | 27.57 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 5 | 125 | 5.563 | [5 empty] | 0.083 | [8 empty] | 5.397 | 22.8768 | 0.44975 | 0.15887 | 0.00033352 | 0.00015 | [5 empty] | 4.86 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 5 | 125 | 5.563 |  |  |  |  | 5 | 0.109 | [8 empty] | 5.345 | 22.4381 | 0.44542 | 0.15582 | 0.00033676 | 0.00015 | [5 empty] | 6.36 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 5 | 125 | 5.563 | [5 empty] | 0.125 | [8 empty] | 5.313 | 22.1702 | 0.44275 | 0.15396 | 0.00033879 | 0.00015 | [5 empty] | 7.27 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 5 | 125 | 5.563 |  |  |  |  | 10 | 0.134 | [8 empty] | 5.295 | 22.0202 | 0.44125 | 0.15292 | 0.00033994 | 0.00015 | [5 empty] | 7.78 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 5 | 125 | 5.563 | [5 empty] | 0.156 | [8 empty] | 5.251 | 21.6558 | 0.43758 | 0.15039 | 0.00034279 | 0.00015 | [5 empty] | 9.02 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 5 | 125 | 5.563 | [5 empty] | 0.188 | [8 empty] | 5.187 | 21.1311 | 0.43225 | 0.14674 | 0.00034702 | 0.00015 | [5 empty] | 10.8 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 5 | 125 | 5.563 | [5 empty] | 0.219 | [8 empty] | 5.125 | 20.629 | 0.42708 | 0.14326 | 0.00035122 | 0.00015 | [5 empty] | 12.51 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 5 | 125 | 5.563 |  |  |  | STD | 40 | 0.258 | [8 empty] | 5.047 | 20.0058 | 0.42058 | 0.13893 | 0.00035665 | 0.00015 | [5 empty] | 14.63 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 5 | 125 | 5.563 | [5 empty] | 0.281 | [8 empty] | 5.001 | 19.6428 | 0.41675 | 0.13641 | 0.00035993 | 0.00015 | [5 empty] | 15.87 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 5 | 125 | 5.563 | [5 empty] | 0.312 | [8 empty] | 4.939 | 19.1588 | 0.41158 | 0.13305 | 0.00036445 | 0.00015 | [5 empty] | 17.51 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 5 | 125 | 5.563 | [5 empty] | 0.344 | [8 empty] | 4.875 | 18.6655 | 0.40625 | 0.12962 | 0.00036923 | 0.00015 | [5 empty] | 19.19 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 5 | 125 | 5.563 |  |  |  | XS | 80 | 0.375 | [8 empty] | 4.813 | 18.1937 | 0.40108 | 0.12635 | 0.00037399 | 0.00015 | [5 empty] | 20.8 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 5 | 125 | 5.563 |  |  |  |  | 120 | 0.5 | [8 empty] | 4.563 | 16.3528 | 0.38025 | 0.11356 | 0.00039448 | 0.00015 | [5 empty] | 27.06 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 5 | 125 | 5.563 |  |  |  |  | 160 | 0.625 | [8 empty] | 4.313 | 14.61 | 0.35942 | 0.10146 | 0.00041734 | 0.00015 | [5 empty] | 32.99 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 5 | 125 | 5.563 |  |  |  | XXS |  | 0.75 | [8 empty] | 4.063 | 12.9653 | 0.33858 | 0.090037 | 0.00044302 | 0.00015 | [5 empty] | 38.59 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 | [5 empty] | 0.083 | [8 empty] | 6.459 | 32.7658 | 0.53825 | 0.22754 | 0.00027868 | 0.00015 | [5 empty] | 5.8 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 |  |  |  |  | 5 | 0.109 | [8 empty] | 6.407 | 32.2403 | 0.53392 | 0.22389 | 0.00028094 | 0.00015 | [5 empty] | 7.59 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 | [5 empty] | 0.125 | [8 empty] | 6.375 | 31.9191 | 0.53125 | 0.22166 | 0.00028235 | 0.00015 | [5 empty] | 8.69 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 |  |  |  |  | 10 | 0.134 | [8 empty] | 6.357 | 31.7391 | 0.52975 | 0.22041 | 0.00028315 | 0.00015 | [5 empty] | 9.3 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 | [5 empty] | 0.141 | [8 empty] | 6.343 | 31.5994 | 0.52858 | 0.21944 | 0.00028378 | 0.00015 | [5 empty] | 9.77 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 | [5 empty] | 0.156 | [8 empty] | 6.313 | 31.3012 | 0.52608 | 0.21737 | 0.00028513 | 0.00015 | [5 empty] | 10.79 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 | [5 empty] | 0.172 | [8 empty] | 6.281 | 30.9847 | 0.52342 | 0.21517 | 0.00028658 | 0.00015 | [5 empty] | 11.87 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 | [5 empty] | 0.188 | [8 empty] | 6.249 | 30.6698 | 0.52075 | 0.21298 | 0.00028805 | 0.00015 | [5 empty] | 12.94 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 | [5 empty] | 0.203 | [8 empty] | 6.219 | 30.376 | 0.51825 | 0.21094 | 0.00028944 | 0.00015 | [5 empty] | 13.94 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 | [5 empty] | 0.219 | [8 empty] | 6.187 | 30.0642 | 0.51558 | 0.20878 | 0.00029093 | 0.00015 | [5 empty] | 15 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 | [5 empty] | 0.25 | [8 empty] | 6.125 | 29.4647 | 0.51042 | 0.20462 | 0.00029388 | 0.00015 | [5 empty] | 17.04 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 |  |  |  | STD | 40 | 0.28 | [8 empty] | 6.065 | 28.8903 | 0.50542 | 0.20063 | 0.00029678 | 0.00015 | [5 empty] | 18.99 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 | [5 empty] | 0.312 | [8 empty] | 6.001 | 28.2838 | 0.50008 | 0.19641 | 0.00029995 | 0.00015 | [5 empty] | 21.06 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 | [5 empty] | 0.344 | [8 empty] | 5.937 | 27.6837 | 0.49475 | 0.19225 | 0.00030318 | 0.00015 | [5 empty] | 23.1 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 | [5 empty] | 0.375 | [8 empty] | 5.875 | 27.1085 | 0.48958 | 0.18825 | 0.00030638 | 0.00015 | [5 empty] | 25.05 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 |  |  |  | XS | 80 | 0.432 | [8 empty] | 5.761 | 26.0667 | 0.48008 | 0.18102 | 0.00031245 | 0.00015 | [5 empty] | 28.6 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 | [5 empty] | 0.5 | [8 empty] | 5.625 | 24.8505 | 0.46875 | 0.17257 | 0.00032 | 0.00015 | [5 empty] | 32.74 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 |  |  |  |  | 120 | 0.562 | [8 empty] | 5.501 | 23.7669 | 0.45842 | 0.16505 | 0.00032721 | 0.00015 | [5 empty] | 36.43 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 | [5 empty] | 0.625 | [8 empty] | 5.375 | 22.6906 | 0.44792 | 0.15757 | 0.00033488 | 0.00015 | [5 empty] | 40.09 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 |  |  |  |  | 160 | 0.719 | [8 empty] | 5.187 | 21.1311 | 0.43225 | 0.14674 | 0.00034702 | 0.00015 | [5 empty] | 45.39 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 | [5 empty] | 0.75 | [8 empty] | 5.125 | 20.629 | 0.42708 | 0.14326 | 0.00035122 | 0.00015 | [5 empty] | 47.1 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 |  |  |  | XXS |  | 0.864 | [8 empty] | 4.897 | 18.8343 | 0.40808 | 0.13079 | 0.00036757 | 0.00015 | [5 empty] | 53.21 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 6 | 150 | 6.625 | [5 empty] | 0.875 | [8 empty] | 4.875 | 18.6655 | 0.40625 | 0.12962 | 0.00036923 | 0.00015 | [5 empty] | 53.78 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 |  |  |  |  | 5 | 0.109 | [8 empty] | 8.407 | 55.5101 | 0.70058 | 0.38549 | 0.00021411 | 0.00015 | [5 empty] | 9.92 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 | [5 empty] | 0.125 | [8 empty] | 8.375 | 55.0883 | 0.69792 | 0.38256 | 0.00021493 | 0.00015 | [5 empty] | 11.36 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 |  |  |  |  | 10 | 0.148 | [8 empty] | 8.329 | 54.4848 | 0.69408 | 0.37837 | 0.00021611 | 0.00015 | [5 empty] | 13.41 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 | [5 empty] | 0.156 | [8 empty] | 8.313 | 54.2757 | 0.69275 | 0.37691 | 0.00021653 | 0.00015 | [5 empty] | 14.12 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 | [5 empty] | 0.188 | [8 empty] | 8.249 | 53.4432 | 0.68742 | 0.37113 | 0.00021821 | 0.00015 | [5 empty] | 16.96 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 | [5 empty] | 0.203 | [8 empty] | 8.219 | 53.0552 | 0.68492 | 0.36844 | 0.000219 | 0.00015 | [5 empty] | 18.28 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 | [5 empty] | 0.219 | [8 empty] | 8.187 | 52.6429 | 0.68225 | 0.36558 | 0.00021986 | 0.00015 | [5 empty] | 19.68 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 |  |  |  |  | 20 | 0.25 | [8 empty] | 8.125 | 51.8486 | 0.67708 | 0.36006 | 0.00022154 | 0.00015 | [5 empty] | 22.38 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 | [5 empty] | 0.277 | [8 empty] | 8.071 | 51.1617 | 0.67258 | 0.35529 | 0.00022302 | 0.00015 | [5 empty] | 24.72 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 | [5 empty] | 0.312 | [8 empty] | 8.001 | 50.278 | 0.66675 | 0.34915 | 0.00022497 | 0.00015 | [5 empty] | 27.73 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 |  |  |  | STD | 40 | 0.322 | [8 empty] | 7.981 | 50.027 | 0.66508 | 0.34741 | 0.00022554 | 0.00015 | [5 empty] | 28.58 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 | [5 empty] | 0.344 | [8 empty] | 7.937 | 49.4769 | 0.66142 | 0.34359 | 0.00022679 | 0.00015 | [5 empty] | 30.45 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 | [5 empty] | 0.375 | [8 empty] | 7.875 | 48.707 | 0.65625 | 0.33824 | 0.00022857 | 0.00015 | [5 empty] | 33.07 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 |  |  |  |  | 60 | 0.406 | [8 empty] | 7.813 | 47.943 | 0.65108 | 0.33294 | 0.00023039 | 0.00015 | [5 empty] | 35.67 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 | [5 empty] | 0.438 | [8 empty] | 7.749 | 47.1608 | 0.64575 | 0.32751 | 0.00023229 | 0.00015 | [5 empty] | 38.33 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 |  |  |  | XS | 80 | 0.5 | [8 empty] | 7.625 | 45.6635 | 0.63542 | 0.31711 | 0.00023607 | 0.00015 | [5 empty] | 43.43 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 | [5 empty] | 0.562 | [8 empty] | 7.501 | 44.1904 | 0.62508 | 0.30688 | 0.00023997 | 0.00015 | [5 empty] | 48.44 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 |  |  |  |  | 100 | 0.594 | [8 empty] | 7.437 | 43.4396 | 0.61975 | 0.30166 | 0.00024203 | 0.00015 | [5 empty] | 51 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 | [5 empty] | 0.625 | [8 empty] | 7.375 | 42.7183 | 0.61458 | 0.29665 | 0.00024407 | 0.00015 | [5 empty] | 53.45 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 |  |  |  |  | 120 | 0.719 | [8 empty] | 7.187 | 40.5681 | 0.59892 | 0.28172 | 0.00025045 | 0.00015 | [5 empty] | 60.77 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 | [5 empty] | 0.75 | [8 empty] | 7.125 | 39.8712 | 0.59375 | 0.27688 | 0.00025263 | 0.00015 | [5 empty] | 63.14 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 |  |  |  |  | 140 | 0.812 | [8 empty] | 7.001 | 38.4955 | 0.58342 | 0.26733 | 0.00025711 | 0.00015 | [5 empty] | 67.82 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 |  |  |  | XXS |  | 0.875 | [8 empty] | 6.875 | 37.1223 | 0.57292 | 0.25779 | 0.00026182 | 0.00015 | [5 empty] | 72.49 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 |  |  |  |  | 160 | 0.906 | [8 empty] | 6.813 | 36.4558 | 0.56775 | 0.25317 | 0.0002642 | 0.00015 | [5 empty] | 74.76 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 8 | 200 | 8.625 | [5 empty] | 1 | [8 empty] | 6.625 | 34.4716 | 0.55208 | 0.23939 | 0.0002717 | 0.00015 | [5 empty] | 81.51 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 |  |  |  |  | 5 | 0.134 | [8 empty] | 10.482 | 86.2935 | 0.8735 | 0.59926 | 0.00017172 | 0.00015 | [5 empty] | 15.21 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 | [5 empty] | 0.156 | [8 empty] | 10.438 | 85.5706 | 0.86983 | 0.59424 | 0.00017245 | 0.00015 | [5 empty] | 17.67 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 |  |  |  |  | 10 | 0.165 | [8 empty] | 10.42 | 85.2757 | 0.86833 | 0.59219 | 0.00017274 | 0.00015 | [5 empty] | 18.67 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 | [5 empty] | 0.188 | [8 empty] | 10.374 | 84.5245 | 0.8645 | 0.58698 | 0.00017351 | 0.00015 | [5 empty] | 21.23 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 | [5 empty] | 0.203 | [8 empty] | 10.344 | 84.0363 | 0.862 | 0.58359 | 0.00017401 | 0.00015 | [5 empty] | 22.89 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 | [5 empty] | 0.219 | [8 empty] | 10.312 | 83.5172 | 0.85933 | 0.57998 | 0.00017455 | 0.00015 | [5 empty] | 24.65 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 |  |  |  |  | 20 | 0.25 | [8 empty] | 10.25 | 82.5159 | 0.85417 | 0.57303 | 0.00017561 | 0.00015 | [5 empty] | 28.06 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 | [5 empty] | 0.279 | [8 empty] | 10.192 | 81.5847 | 0.84933 | 0.56656 | 0.00017661 | 0.00015 | [5 empty] | 31.32 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 |  |  |  |  | 30 | 0.307 | [8 empty] | 10.136 | 80.6906 | 0.84467 | 0.56035 | 0.00017758 | 0.00015 | [5 empty] | 34.27 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 | [5 empty] | 0.344 | [8 empty] | 10.062 | 79.5167 | 0.8385 | 0.5522 | 0.00017889 | 0.00015 | [5 empty] | 38.27 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 |  |  |  | STD | 40 | 0.365 | [8 empty] | 10.02 | 78.8543 | 0.835 | 0.5476 | 0.00017964 | 0.00015 | [5 empty] | 40.52 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 | [5 empty] | 0.438 | [8 empty] | 9.874 | 76.5731 | 0.82283 | 0.53176 | 0.0001823 | 0.00015 | [5 empty] | 48.28 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 |  |  |  | XS | 60 | 0.5 | [8 empty] | 9.75 | 74.6619 | 0.8125 | 0.51849 | 0.00018462 | 0.00015 | [5 empty] | 54.79 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 | [5 empty] | 0.562 | [8 empty] | 9.626 | 72.7749 | 0.80217 | 0.50538 | 0.00018699 | 0.00015 | [5 empty] | 61.21 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 |  |  |  |  | 80 | 0.594 | [8 empty] | 9.562 | 71.8104 | 0.79683 | 0.49868 | 0.00018825 | 0.00015 | [5 empty] | 64.49 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 | [5 empty] | 0.625 | [8 empty] | 9.5 | 70.8822 | 0.79167 | 0.49224 | 0.00018947 | 0.00015 | [5 empty] | 67.65 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 |  |  |  |  | 100 | 0.719 | [8 empty] | 9.312 | 68.1045 | 0.776 | 0.47295 | 0.0001933 | 0.00015 | [5 empty] | 77.1 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 | [5 empty] | 0.812 | [8 empty] | 9.126 | 65.411 | 0.7605 | 0.45424 | 0.00019724 | 0.00015 | [5 empty] | 86.26 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 |  |  |  |  | 120 | 0.844 | [8 empty] | 9.062 | 64.4968 | 0.75517 | 0.44789 | 0.00019863 | 0.00015 | [5 empty] | 89.38 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 | [5 empty] | 0.875 | [8 empty] | 9 | 63.6173 | 0.75 | 0.44179 | 0.0002 | 0.00015 | [5 empty] | 92.37 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 | [5 empty] | 0.938 | [8 empty] | 8.874 | 61.8484 | 0.7395 | 0.4295 | 0.00020284 | 0.00015 | [5 empty] | 98.39 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 |  |  |  | XXS | 140 | 1 | [8 empty] | 8.75 | 60.132 | 0.72917 | 0.41758 | 0.00020571 | 0.00015 | [5 empty] | 104.23 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 |  |  |  |  | 160 | 1.125 | [8 empty] | 8.5 | 56.745 | 0.70833 | 0.39406 | 0.00021176 | 0.00015 | [5 empty] | 115.75 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 10 | 250 | 10.75 |  |  |  |  | 160 | 1.25 | [8 empty] | 8.25 | 53.4562 | 0.6875 | 0.37122 | 0.00021818 | 0.00015 | [5 empty] | 126.94 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 |  |  |  |  | 5 | 0.156 | [8 empty] | 12.438 | 121.5041 | 1.0365 | 0.84378 | 0.00014472 | 0.00015 | [5 empty] | 21 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 | [5 empty] | 0.172 | [8 empty] | 12.406 | 120.8797 | 1.0338 | 0.83944 | 0.00014509 | 0.00015 | [5 empty] | 23.13 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 |  |  |  |  | 10 | 0.18 | [8 empty] | 12.39 | 120.5681 | 1.0325 | 0.83728 | 0.00014528 | 0.00015 | [5 empty] | 24.19 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 | [5 empty] | 0.188 | [8 empty] | 12.374 | 120.2569 | 1.0312 | 0.83512 | 0.00014547 | 0.00015 | [5 empty] | 25.25 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 | [5 empty] | 0.203 | [8 empty] | 12.344 | 119.6745 | 1.0287 | 0.83107 | 0.00014582 | 0.00015 | [5 empty] | 27.23 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 | [5 empty] | 0.219 | [8 empty] | 12.312 | 119.0549 | 1.026 | 0.82677 | 0.0001462 | 0.00015 | [5 empty] | 29.34 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 |  |  |  |  | 20 | 0.25 | [8 empty] | 12.25 | 117.8588 | 1.0208 | 0.81846 | 0.00014694 | 0.00015 | [5 empty] | 33.41 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 | [5 empty] | 0.281 | [8 empty] | 12.188 | 116.6688 | 1.0157 | 0.8102 | 0.00014769 | 0.00015 | [5 empty] | 37.46 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 | [5 empty] | 0.312 | [8 empty] | 12.126 | 115.4848 | 1.0105 | 0.80198 | 0.00014844 | 0.00015 | [5 empty] | 41.48 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 |  |  |  |  | 30 | 0.33 | [8 empty] | 12.09 | 114.8002 | 1.0075 | 0.79722 | 0.00014888 | 0.00015 | [5 empty] | 43.81 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 | [5 empty] | 0.344 | [8 empty] | 12.062 | 114.269 | 1.0052 | 0.79353 | 0.00014923 | 0.00015 | [5 empty] | 45.62 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 |  |  |  | STD |  | 0.375 | [8 empty] | 12 | 113.0973 | 1 | 0.7854 | 0.00015 | 0.00015 | [5 empty] | 49.61 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 |  |  |  |  | 40 | 0.406 | [8 empty] | 11.938 | 111.9317 | 0.99483 | 0.7773 | 0.00015078 | 0.00015 | [5 empty] | 53.57 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 | [5 empty] | 0.438 | [8 empty] | 11.874 | 110.7348 | 0.9895 | 0.76899 | 0.00015159 | 0.00015 | [5 empty] | 57.65 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 |  |  |  | XS |  | 0.5 | [8 empty] | 11.75 | 108.434 | 0.97917 | 0.75301 | 0.00015319 | 0.00015 | [5 empty] | 65.48 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 |  |  |  |  | 60 | 0.562 | [8 empty] | 11.626 | 106.1575 | 0.96883 | 0.7372 | 0.00015483 | 0.00015 | [5 empty] | 73.22 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 | [5 empty] | 0.625 | [8 empty] | 11.5 | 103.8689 | 0.95833 | 0.72131 | 0.00015652 | 0.00015 | [5 empty] | 81.01 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 |  |  |  |  | 80 | 0.688 | [8 empty] | 11.374 | 101.6053 | 0.94783 | 0.70559 | 0.00015826 | 0.00015 | [5 empty] | 88.71 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 | [5 empty] | 0.75 | [8 empty] | 11.25 | 99.402 | 0.9375 | 0.69029 | 0.00016 | 0.00015 | [5 empty] | 96.21 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 | [5 empty] | 0.812 | [8 empty] | 11.126 | 97.2228 | 0.92717 | 0.67516 | 0.00016178 | 0.00015 | [5 empty] | 103.63 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 |  |  |  |  | 100 | 0.844 | [8 empty] | 11.062 | 96.1075 | 0.92183 | 0.66741 | 0.00016272 | 0.00015 | [5 empty] | 107.42 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 | [5 empty] | 0.875 | [8 empty] | 11 | 95.0332 | 0.91667 | 0.65995 | 0.00016364 | 0.00015 | [5 empty] | 111.08 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 | [5 empty] | 0.938 | [8 empty] | 10.874 | 92.8685 | 0.90617 | 0.64492 | 0.00016553 | 0.00015 | [5 empty] | 118.44 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 |  |  |  | XXS | 120 | 1 | [8 empty] | 10.75 | 90.7626 | 0.89583 | 0.6303 | 0.00016744 | 0.00015 | [5 empty] | 125.61 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 | [5 empty] | 1.062 | [8 empty] | 10.626 | 88.6808 | 0.8855 | 0.61584 | 0.0001694 | 0.00015 | [5 empty] | 132.69 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 |  |  |  |  | 140 | 1.125 | [8 empty] | 10.5 | 86.5901 | 0.875 | 0.60132 | 0.00017143 | 0.00015 | [5 empty] | 139.81 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 | [5 empty] | 1.25 | [8 empty] | 10.25 | 82.5159 | 0.85417 | 0.57303 | 0.00017561 | 0.00015 | [5 empty] | 153.67 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 12 | 300 | 12.75 |  |  |  |  | 160 | 1.312 | [8 empty] | 10.126 | 80.5315 | 0.84383 | 0.55925 | 0.00017776 | 0.00015 | [5 empty] | 160.42 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 |  |  |  |  | 5 | 0.156 | [8 empty] | 13.688 | 147.1533 | 1.1407 | 1.0219 | 0.0001315 | 0.00015 | [5 empty] | 23.09 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 0.188 | [8 empty] | 13.624 | 145.7804 | 1.1353 | 1.0124 | 0.00013212 | 0.00015 | [5 empty] | 27.76 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 0.203 | [8 empty] | 13.594 | 145.1391 | 1.1328 | 1.0079 | 0.00013241 | 0.00015 | [5 empty] | 29.94 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 0.21 | [8 empty] | 13.58 | 144.8403 | 1.1317 | 1.0058 | 0.00013255 | 0.00015 | [5 empty] | 30.96 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 0.219 | [8 empty] | 13.562 | 144.4566 | 1.1302 | 1.0032 | 0.00013272 | 0.00015 | [5 empty] | 32.26 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 |  |  |  |  | 10 | 0.25 | [8 empty] | 13.5 | 143.1388 | 1.125 | 0.99402 | 0.00013333 | 0.00015 | [5 empty] | 36.75 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 0.281 | [8 empty] | 13.438 | 141.8271 | 1.1198 | 0.98491 | 0.00013395 | 0.00015 | [5 empty] | 41.21 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 |  |  |  |  | 20 | 0.312 | [8 empty] | 13.376 | 140.5214 | 1.1147 | 0.97584 | 0.00013457 | 0.00015 | [5 empty] | 45.65 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 0.344 | [8 empty] | 13.312 | 139.1799 | 1.1093 | 0.96653 | 0.00013522 | 0.00015 | [5 empty] | 50.22 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 |  |  |  | STD | 30 | 0.375 | [8 empty] | 13.25 | 137.8865 | 1.1042 | 0.95754 | 0.00013585 | 0.00015 | [5 empty] | 54.62 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 0.406 | [8 empty] | 13.188 | 136.5991 | 1.099 | 0.9486 | 0.00013649 | 0.00015 | [5 empty] | 59 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 |  |  |  |  | 40 | 0.438 | [8 empty] | 13.124 | 135.2765 | 1.0937 | 0.93942 | 0.00013715 | 0.00015 | [5 empty] | 63.5 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 0.469 | [8 empty] | 13.062 | 134.0014 | 1.0885 | 0.93057 | 0.0001378 | 0.00015 | [5 empty] | 67.84 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 |  |  |  | XS |  | 0.5 | [8 empty] | 13 | 132.7323 | 1.0833 | 0.92175 | 0.00013846 | 0.00015 | [5 empty] | 72.16 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 0.562 | [8 empty] | 12.876 | 130.2122 | 1.073 | 0.90425 | 0.00013979 | 0.00015 | [5 empty] | 80.73 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 |  |  |  |  | 60 | 0.594 | [8 empty] | 12.812 | 128.921 | 1.0677 | 0.89528 | 0.00014049 | 0.00015 | [5 empty] | 85.13 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 0.625 | [8 empty] | 12.75 | 127.6763 | 1.0625 | 0.88664 | 0.00014118 | 0.00015 | [5 empty] | 89.36 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 0.688 | [8 empty] | 12.624 | 125.1653 | 1.052 | 0.8692 | 0.00014259 | 0.00015 | [5 empty] | 97.91 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 |  |  |  |  | 80 | 0.75 | [8 empty] | 12.5 | 122.7185 | 1.0417 | 0.85221 | 0.000144 | 0.00015 | [5 empty] | 106.23 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 0.812 | [8 empty] | 12.376 | 120.2958 | 1.0313 | 0.83539 | 0.00014544 | 0.00015 | [5 empty] | 114.48 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 0.875 | [8 empty] | 12.25 | 117.8588 | 1.0208 | 0.81846 | 0.00014694 | 0.00015 | [5 empty] | 122.77 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 |  |  |  |  | 100 | 0.938 | [8 empty] | 12.124 | 115.4468 | 1.0103 | 0.80171 | 0.00014847 | 0.00015 | [5 empty] | 130.98 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 1 | [8 empty] | 12 | 113.0973 | 1 | 0.7854 | 0.00015 | 0.00015 | [5 empty] | 138.97 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 1.062 | [8 empty] | 11.876 | 110.7721 | 0.98967 | 0.76925 | 0.00015157 | 0.00015 | [5 empty] | 146.88 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 |  |  |  |  | 120 | 1.094 | [8 empty] | 11.812 | 109.5814 | 0.98433 | 0.76098 | 0.00015239 | 0.00015 | [5 empty] | 150.93 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 1.125 | [8 empty] | 11.75 | 108.434 | 0.97917 | 0.75301 | 0.00015319 | 0.00015 | [5 empty] | 154.84 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 |  |  |  |  | 140 | 1.25 | [8 empty] | 11.5 | 103.8689 | 0.95833 | 0.72131 | 0.00015652 | 0.00015 | [5 empty] | 170.37 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 |  |  |  |  | 160 | 1.406 | [8 empty] | 11.188 | 98.3093 | 0.93233 | 0.6827 | 0.00016089 | 0.00015 | [5 empty] | 189.29 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 2 | [8 empty] | 10 | 78.5398 | 0.83333 | 0.54542 | 0.00018 | 0.00015 | [5 empty] | 256.56 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 2.125 | [8 empty] | 9.75 | 74.6619 | 0.8125 | 0.51849 | 0.00018462 | 0.00015 | [5 empty] | 269.76 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 2.2 | [8 empty] | 9.6 | 72.3823 | 0.8 | 0.50265 | 0.0001875 | 0.00015 | [5 empty] | 277.51 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 14 | 350 | 14 | [5 empty] | 2.5 | [8 empty] | 9 | 63.6173 | 0.75 | 0.44179 | 0.0002 | 0.00015 | [5 empty] | 307.34 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 |  |  |  |  | 5 | 0.165 | [8 empty] | 15.67 | 192.8537 | 1.3058 | 1.3393 | 0.00011487 | 0.00015 | [5 empty] | 27.93 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 0.188 | [8 empty] | 15.624 | 191.7231 | 1.302 | 1.3314 | 0.00011521 | 0.00015 | [5 empty] | 31.78 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 0.203 | [8 empty] | 15.594 | 190.9875 | 1.2995 | 1.3263 | 0.00011543 | 0.00015 | [5 empty] | 34.28 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 0.219 | [8 empty] | 15.562 | 190.2045 | 1.2968 | 1.3209 | 0.00011567 | 0.00015 | [5 empty] | 36.95 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 |  |  |  |  | 10 | 0.25 | [8 empty] | 15.5 | 188.6919 | 1.2917 | 1.3104 | 0.00011613 | 0.00015 | [5 empty] | 42.09 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 0.281 | [8 empty] | 15.438 | 187.1854 | 1.2865 | 1.2999 | 0.0001166 | 0.00015 | [5 empty] | 47.22 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 |  |  |  |  | 20 | 0.312 | [8 empty] | 15.376 | 185.6849 | 1.2813 | 1.2895 | 0.00011707 | 0.00015 | [5 empty] | 52.32 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 0.344 | [8 empty] | 15.312 | 184.1424 | 1.276 | 1.2788 | 0.00011755 | 0.00015 | [5 empty] | 57.57 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 |  |  |  |  | 30 | 0.375 | [8 empty] | 15.25 | 182.6542 | 1.2708 | 1.2684 | 0.00011803 | 0.00015 | [5 empty] | 62.64 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 0.406 | [8 empty] | 15.188 | 181.172 | 1.2657 | 1.2581 | 0.00011851 | 0.00015 | [5 empty] | 67.68 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 0.438 | [8 empty] | 15.124 | 179.6483 | 1.2603 | 1.2476 | 0.00011902 | 0.00015 | [5 empty] | 72.86 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 0.469 | [8 empty] | 15.062 | 178.1784 | 1.2552 | 1.2374 | 0.00011951 | 0.00015 | [5 empty] | 77.87 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 |  |  |  |  | 40 | 0.5 | [8 empty] | 15 | 176.7146 | 1.25 | 1.2272 | 0.00012 | 0.00015 | [5 empty] | 82.85 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 0.562 | [8 empty] | 14.876 | 173.805 | 1.2397 | 1.207 | 0.000121 | 0.00015 | [5 empty] | 92.75 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 0.625 | [8 empty] | 14.75 | 170.8732 | 1.2292 | 1.1866 | 0.00012203 | 0.00015 | [5 empty] | 102.72 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 |  |  |  |  | 60 | 0.656 | [8 empty] | 14.688 | 169.4397 | 1.224 | 1.1767 | 0.00012255 | 0.00015 | [5 empty] | 107.6 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 0.688 | [8 empty] | 14.624 | 167.9663 | 1.2187 | 1.1664 | 0.00012309 | 0.00015 | [5 empty] | 112.62 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 0.75 | [8 empty] | 14.5 | 165.13 | 1.2083 | 1.1467 | 0.00012414 | 0.00015 | [5 empty] | 122.27 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 0.812 | [8 empty] | 14.376 | 162.3177 | 1.198 | 1.1272 | 0.00012521 | 0.00015 | [5 empty] | 131.84 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 |  |  |  |  | 80 | 0.844 | [8 empty] | 14.312 | 160.8757 | 1.1927 | 1.1172 | 0.00012577 | 0.00015 | [5 empty] | 136.74 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 0.875 | [8 empty] | 14.25 | 159.4849 | 1.1875 | 1.1075 | 0.00012632 | 0.00015 | [5 empty] | 141.48 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 0.938 | [8 empty] | 14.124 | 156.677 | 1.177 | 1.088 | 0.00012744 | 0.00015 | [5 empty] | 151.03 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 1 | [8 empty] | 14 | 153.938 | 1.1667 | 1.069 | 0.00012857 | 0.00015 | [5 empty] | 160.35 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 |  |  |  |  | 100 | 1.031 | [8 empty] | 13.938 | 152.5776 | 1.1615 | 1.0596 | 0.00012914 | 0.00015 | [5 empty] | 164.98 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 1.062 | [8 empty] | 13.876 | 151.2232 | 1.1563 | 1.0502 | 0.00012972 | 0.00015 | [5 empty] | 169.59 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 1.125 | [8 empty] | 13.75 | 148.4893 | 1.1458 | 1.0312 | 0.00013091 | 0.00015 | [5 empty] | 178.89 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 1.188 | [8 empty] | 13.624 | 145.7804 | 1.1353 | 1.0124 | 0.00013212 | 0.00015 | [5 empty] | 188.11 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 |  |  |  |  | 120 | 1.219 | [8 empty] | 13.562 | 144.4566 | 1.1302 | 1.0032 | 0.00013272 | 0.00015 | [5 empty] | 192.61 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 | [5 empty] | 1.25 | [8 empty] | 13.5 | 143.1388 | 1.125 | 0.99402 | 0.00013333 | 0.00015 | [5 empty] | 197.1 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 |  |  |  |  | 140 | 1.438 | [8 empty] | 13.124 | 135.2765 | 1.0937 | 0.93942 | 0.00013715 | 0.00015 | [5 empty] | 223.85 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 16 | 400 | 16 |  |  |  |  | 160 | 1.594 | [8 empty] | 12.812 | 128.921 | 1.0677 | 0.89528 | 0.00014049 | 0.00015 | [5 empty] | 245.48 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 |  |  |  |  | 5 | 0.165 | [8 empty] | 17.67 | 245.224 | 1.4725 | 1.7029 | 0.00010187 | 0.00015 | [5 empty] | 31.46 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 | [5 empty] | 0.188 | [8 empty] | 17.624 | 243.9489 | 1.4687 | 1.6941 | 0.00010213 | 0.00015 | [5 empty] | 35.8 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 | [5 empty] | 0.219 | [8 empty] | 17.562 | 242.2355 | 1.4635 | 1.6822 | 0.00010249 | 0.00015 | [5 empty] | 41.63 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 |  |  |  |  | 10 | 0.25 | [8 empty] | 17.5 | 240.5282 | 1.4583 | 1.6703 | 0.00010286 | 0.00015 | [5 empty] | 47.44 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 | [5 empty] | 0.281 | [8 empty] | 17.438 | 238.8269 | 1.4532 | 1.6585 | 0.00010322 | 0.00015 | [5 empty] | 53.23 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 |  |  |  |  | 20 | 0.312 | [8 empty] | 17.376 | 237.1316 | 1.448 | 1.6467 | 0.00010359 | 0.00015 | [5 empty] | 58.99 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 | [5 empty] | 0.344 | [8 empty] | 17.312 | 235.388 | 1.4427 | 1.6346 | 0.00010397 | 0.00015 | [5 empty] | 64.93 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 |  |  |  | STD |  | 0.375 | [8 empty] | 17.25 | 233.705 | 1.4375 | 1.623 | 0.00010435 | 0.00015 | [5 empty] | 70.65 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 | [5 empty] | 0.406 | [8 empty] | 17.188 | 232.0281 | 1.4323 | 1.6113 | 0.00010472 | 0.00015 | [5 empty] | 76.36 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 |  |  |  |  | 30 | 0.438 | [8 empty] | 17.124 | 230.3034 | 1.427 | 1.5993 | 0.00010512 | 0.00015 | [5 empty] | 82.23 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 | [5 empty] | 0.469 | [8 empty] | 17.062 | 228.6387 | 1.4218 | 1.5878 | 0.0001055 | 0.00015 | [5 empty] | 87.89 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 |  |  |  | XS |  | 0.5 | [8 empty] | 17 | 226.9801 | 1.4167 | 1.5763 | 0.00010588 | 0.00015 | [5 empty] | 93.54 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 |  |  |  |  | 40 | 0.562 | [8 empty] | 16.876 | 223.6809 | 1.4063 | 1.5533 | 0.00010666 | 0.00015 | [5 empty] | 104.76 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 | [5 empty] | 0.625 | [8 empty] | 16.75 | 220.3533 | 1.3958 | 1.5302 | 0.00010746 | 0.00015 | [5 empty] | 116.09 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 | [5 empty] | 0.688 | [8 empty] | 16.624 | 217.0506 | 1.3853 | 1.5073 | 0.00010828 | 0.00015 | [5 empty] | 127.32 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 |  |  |  |  | 60 | 0.75 | [8 empty] | 16.5 | 213.8246 | 1.375 | 1.4849 | 0.00010909 | 0.00015 | [5 empty] | 138.3 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 | [5 empty] | 0.812 | [8 empty] | 16.376 | 210.6229 | 1.3647 | 1.4627 | 0.00010992 | 0.00015 | [5 empty] | 149.2 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 | [5 empty] | 0.875 | [8 empty] | 16.25 | 207.3942 | 1.3542 | 1.4402 | 0.00011077 | 0.00015 | [5 empty] | 160.18 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 |  |  |  |  | 80 | 0.938 | [8 empty] | 16.124 | 204.1905 | 1.3437 | 1.418 | 0.00011163 | 0.00015 | [5 empty] | 171.08 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 | [5 empty] | 1 | [8 empty] | 16 | 201.0619 | 1.3333 | 1.3963 | 0.0001125 | 0.00015 | [5 empty] | 171.73 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 | [5 empty] | 1.062 | [8 empty] | 15.876 | 197.9575 | 1.323 | 1.3747 | 0.00011338 | 0.00015 | [5 empty] | 192.29 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 | [5 empty] | 1.125 | [8 empty] | 15.75 | 194.8278 | 1.3125 | 1.353 | 0.00011429 | 0.00015 | [5 empty] | 202.94 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 |  |  |  |  | 100 | 1.156 | [8 empty] | 15.688 | 193.297 | 1.3073 | 1.3423 | 0.00011474 | 0.00015 | [5 empty] | 208.15 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 | [5 empty] | 1.188 | [8 empty] | 15.624 | 191.7231 | 1.302 | 1.3314 | 0.00011521 | 0.00015 | [5 empty] | 213.51 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 | [5 empty] | 1.25 | [8 empty] | 15.5 | 188.6919 | 1.2917 | 1.3104 | 0.00011613 | 0.00015 | [5 empty] | 223.82 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 |  |  |  |  | 120 | 1.375 | [8 empty] | 15.25 | 182.6542 | 1.2708 | 1.2684 | 0.00011803 | 0.00015 | [5 empty] | 244.37 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 |  |  |  |  | 140 | 1.562 | [8 empty] | 14.876 | 173.805 | 1.2397 | 1.207 | 0.000121 | 0.00015 | [5 empty] | 274.48 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 18 | 450 | 18 |  |  |  |  | 160 | 1.781 | [8 empty] | 14.438 | 163.7208 | 1.2032 | 1.137 | 0.00012467 | 0.00015 | [5 empty] | 308.79 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 |  |  |  |  | 5 | 0.188 | [8 empty] | 19.624 | 302.4579 | 1.6353 | 2.1004 | 9.1724e-05 | 0.00015 | [5 empty] | 39.82 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 0.219 | [8 empty] | 19.562 | 300.5498 | 1.6302 | 2.0872 | 9.2015e-05 | 0.00015 | [5 empty] | 46.31 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 |  |  |  |  | 10 | 0.25 | [8 empty] | 19.5 | 298.6477 | 1.625 | 2.0739 | 9.2308e-05 | 0.00015 | [5 empty] | 52.78 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 0.281 | [8 empty] | 19.438 | 296.7516 | 1.6198 | 2.0608 | 9.2602e-05 | 0.00015 | [5 empty] | 59.23 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 0.312 | [8 empty] | 19.376 | 294.8615 | 1.6147 | 2.0476 | 9.2898e-05 | 0.00015 | [5 empty] | 65.66 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 0.344 | [8 empty] | 19.312 | 292.9169 | 1.6093 | 2.0341 | 9.3206e-05 | 0.00015 | [5 empty] | 72.28 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 |  |  |  | STD | 20 | 0.375 | [8 empty] | 19.25 | 291.0391 | 1.6042 | 2.0211 | 9.3506e-05 | 0.00015 | [5 empty] | 78.67 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 0.406 | [8 empty] | 19.188 | 289.1674 | 1.599 | 2.0081 | 9.3809e-05 | 0.00015 | [5 empty] | 85.04 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 0.438 | [8 empty] | 19.124 | 287.2416 | 1.5937 | 1.9947 | 9.4123e-05 | 0.00015 | [5 empty] | 91.59 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 0.469 | [8 empty] | 19.062 | 285.3822 | 1.5885 | 1.9818 | 9.4429e-05 | 0.00015 | [5 empty] | 97.92 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 |  |  |  | XS | 30 | 0.5 | [8 empty] | 19 | 283.5287 | 1.5833 | 1.9689 | 9.4737e-05 | 0.00015 | [5 empty] | 104.23 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 0.562 | [8 empty] | 18.876 | 279.84 | 1.573 | 1.9433 | 9.5359e-05 | 0.00015 | [5 empty] | 116.78 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 |  |  |  |  | 40 | 0.594 | [8 empty] | 18.812 | 277.9456 | 1.5677 | 1.9302 | 9.5684e-05 | 0.00015 | [5 empty] | 123.23 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 0.625 | [8 empty] | 18.75 | 276.1165 | 1.5625 | 1.9175 | 9.6e-05 | 0.00015 | [5 empty] | 129.45 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 0.688 | [8 empty] | 18.624 | 272.418 | 1.552 | 1.8918 | 9.6649e-05 | 0.00015 | [5 empty] | 142.03 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 0.75 | [8 empty] | 18.5 | 268.8025 | 1.5417 | 1.8667 | 9.7297e-05 | 0.00015 | [5 empty] | 154.34 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 |  |  |  |  | 60 | 0.812 | [8 empty] | 18.376 | 265.2112 | 1.5313 | 1.8417 | 9.7954e-05 | 0.00015 | [5 empty] | 166.56 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 0.875 | [8 empty] | 18.25 | 261.5867 | 1.5208 | 1.8166 | 9.863e-05 | 0.00015 | [5 empty] | 178.89 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 0.938 | [8 empty] | 18.124 | 257.9871 | 1.5103 | 1.7916 | 9.9316e-05 | 0.00015 | [5 empty] | 191.14 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 1 | [8 empty] | 18 | 254.469 | 1.5 | 1.7671 | 0.0001 | 0.00015 | [5 empty] | 203.11 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 |  |  |  |  | 80 | 1.031 | [8 empty] | 17.938 | 252.719 | 1.4948 | 1.755 | 0.00010035 | 0.00015 | [5 empty] | 209.06 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 1.062 | [8 empty] | 17.876 | 250.9751 | 1.4897 | 1.7429 | 0.00010069 | 0.00015 | [5 empty] | 215 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 1.125 | [8 empty] | 17.75 | 247.4495 | 1.4792 | 1.7184 | 0.00010141 | 0.00015 | [5 empty] | 227 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 1.188 | [8 empty] | 17.624 | 243.9489 | 1.4687 | 1.6941 | 0.00010213 | 0.00015 | [5 empty] | 238.91 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 1.25 | [8 empty] | 17.5 | 240.5282 | 1.4583 | 1.6703 | 0.00010286 | 0.00015 | [5 empty] | 250.55 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 |  |  |  |  | 100 | 1.281 | [8 empty] | 17.438 | 238.8269 | 1.4532 | 1.6585 | 0.00010322 | 0.00015 | [5 empty] | 256.34 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 1.312 | [8 empty] | 17.376 | 237.1316 | 1.448 | 1.6467 | 0.00010359 | 0.00015 | [5 empty] | 262.1 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 | [5 empty] | 1.375 | [8 empty] | 17.25 | 233.705 | 1.4375 | 1.623 | 0.00010435 | 0.00015 | [5 empty] | 273.76 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 |  |  |  |  | 120 | 1.5 | [8 empty] | 17 | 226.9801 | 1.4167 | 1.5763 | 0.00010588 | 0.00015 | [5 empty] | 296.65 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 |  |  |  |  | 140 | 1.75 | [8 empty] | 16.5 | 213.8246 | 1.375 | 1.4849 | 0.00010909 | 0.00015 | [5 empty] | 341.41 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 20 | 500 | 20 |  |  |  |  | 160 | 1.969 | [8 empty] | 16.062 | 202.6232 | 1.3385 | 1.4071 | 0.00011207 | 0.00015 | [5 empty] | 379.53 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 |  |  |  |  | 5 | 0.188 | [8 empty] | 21.624 | 367.2501 | 1.802 | 2.5503 | 8.3241e-05 | 0.00015 | [5 empty] | 43.84 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 0.219 | [8 empty] | 21.562 | 365.1472 | 1.7968 | 2.5357 | 8.348e-05 | 0.00015 | [5 empty] | 50.99 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 |  |  |  |  | 10 | 0.25 | [8 empty] | 21.5 | 363.0503 | 1.7917 | 2.5212 | 8.3721e-05 | 0.00015 | [5 empty] | 58.13 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 0.281 | [8 empty] | 21.438 | 360.9594 | 1.7865 | 2.5067 | 8.3963e-05 | 0.00015 | [5 empty] | 65.24 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 0.312 | [8 empty] | 21.376 | 358.8746 | 1.7813 | 2.4922 | 8.4207e-05 | 0.00015 | [5 empty] | 72.34 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 0.344 | [8 empty] | 21.312 | 356.7289 | 1.776 | 2.4773 | 8.4459e-05 | 0.00015 | [5 empty] | 79.64 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 |  |  |  | STD | 20 | 0.375 | [8 empty] | 21.25 | 354.6564 | 1.7708 | 2.4629 | 8.4706e-05 | 0.00015 | [5 empty] | 86.69 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 0.406 | [8 empty] | 21.188 | 352.5899 | 1.7657 | 2.4485 | 8.4954e-05 | 0.00015 | [5 empty] | 93.72 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 0.438 | [8 empty] | 21.124 | 350.463 | 1.7603 | 2.4338 | 8.5211e-05 | 0.00015 | [5 empty] | 100.96 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 0.469 | [8 empty] | 21.062 | 348.4088 | 1.7552 | 2.4195 | 8.5462e-05 | 0.00015 | [5 empty] | 107.95 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 |  |  |  | XS | 30 | 0.5 | [8 empty] | 21 | 346.3606 | 1.75 | 2.4053 | 8.5714e-05 | 0.00015 | [5 empty] | 114.92 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 0.562 | [8 empty] | 20.876 | 342.2823 | 1.7397 | 2.377 | 8.6223e-05 | 0.00015 | [5 empty] | 128.79 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 0.625 | [8 empty] | 20.75 | 338.163 | 1.7292 | 2.3484 | 8.6747e-05 | 0.00015 | [5 empty] | 142.81 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 0.688 | [8 empty] | 20.624 | 334.0686 | 1.7187 | 2.3199 | 8.7277e-05 | 0.00015 | [5 empty] | 156.74 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 0.75 | [8 empty] | 20.5 | 330.0636 | 1.7083 | 2.2921 | 8.7805e-05 | 0.00015 | [5 empty] | 170.37 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 0.812 | [8 empty] | 20.376 | 326.0827 | 1.698 | 2.2645 | 8.8339e-05 | 0.00015 | [5 empty] | 183.92 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 |  |  |  |  | 60 | 0.875 | [8 empty] | 20.25 | 322.0623 | 1.6875 | 2.2365 | 8.8889e-05 | 0.00015 | [5 empty] | 197.6 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 0.938 | [8 empty] | 20.124 | 318.0669 | 1.677 | 2.2088 | 8.9445e-05 | 0.00015 | [5 empty] | 211.19 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 1 | [8 empty] | 20 | 314.1593 | 1.6667 | 2.1817 | 9e-05 | 0.00015 | [5 empty] | 224.49 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 1.062 | [8 empty] | 19.876 | 310.2758 | 1.6563 | 2.1547 | 9.0561e-05 | 0.00015 | [5 empty] | 237.7 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 |  |  |  |  | 80 | 1.125 | [8 empty] | 19.75 | 306.3544 | 1.6458 | 2.1275 | 9.1139e-05 | 0.00015 | [5 empty] | 251.05 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 1.188 | [8 empty] | 19.624 | 302.4579 | 1.6353 | 2.1004 | 9.1724e-05 | 0.00015 | [5 empty] | 264.31 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 1.25 | [8 empty] | 19.5 | 298.6477 | 1.625 | 2.0739 | 9.2308e-05 | 0.00015 | [5 empty] | 277.27 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 1.312 | [8 empty] | 19.376 | 294.8615 | 1.6147 | 2.0476 | 9.2898e-05 | 0.00015 | [5 empty] | 290.15 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 |  |  |  |  | 100 | 1.375 | [8 empty] | 19.25 | 291.0391 | 1.6042 | 2.0211 | 9.3506e-05 | 0.00015 | [5 empty] | 303.16 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 1.438 | [8 empty] | 19.124 | 287.2416 | 1.5937 | 1.9947 | 9.4123e-05 | 0.00015 | [5 empty] | 316.08 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 | [5 empty] | 1.5 | [8 empty] | 19 | 283.5287 | 1.5833 | 1.9689 | 9.4737e-05 | 0.00015 | [5 empty] | 328.72 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 |  |  |  |  | 120 | 1.625 | [8 empty] | 18.75 | 276.1165 | 1.5625 | 1.9175 | 9.6e-05 | 0.00015 | [5 empty] | 353.94 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 |  |  |  |  | 140 | 1.875 | [8 empty] | 18.25 | 261.5867 | 1.5208 | 1.8166 | 9.863e-05 | 0.00015 | [5 empty] | 403.38 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 22 | 550 | 22 |  |  |  |  | 160 | 2.125 | [8 empty] | 17.75 | 247.4495 | 1.4792 | 1.7184 | 0.00010141 | 0.00015 | [5 empty] | 451.49 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 |  |  |  |  | 5 | 0.218 | [8 empty] | 23.564 | 436.1018 | 1.9637 | 3.0285 | 7.6388e-05 | 0.00015 | [5 empty] | 55.42 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 |  |  |  |  | 10 | 0.25 | [8 empty] | 23.5 | 433.7361 | 1.9583 | 3.0121 | 7.6596e-05 | 0.00015 | [5 empty] | 63.47 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 0.281 | [8 empty] | 23.438 | 431.4505 | 1.9532 | 2.9962 | 7.6798e-05 | 0.00015 | [5 empty] | 71.25 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 0.312 | [8 empty] | 23.376 | 429.1709 | 1.948 | 2.9804 | 7.7002e-05 | 0.00015 | [5 empty] | 79.01 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 0.344 | [8 empty] | 23.312 | 426.8241 | 1.9427 | 2.9641 | 7.7213e-05 | 0.00015 | [5 empty] | 86.99 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 |  |  |  | STD | 20 | 0.375 | [8 empty] | 23.25 | 424.5568 | 1.9375 | 2.9483 | 7.7419e-05 | 0.00015 | [5 empty] | 94.71 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 0.406 | [8 empty] | 23.188 | 422.2955 | 1.9323 | 2.9326 | 7.7626e-05 | 0.00015 | [5 empty] | 102.4 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 0.438 | [8 empty] | 23.124 | 419.9676 | 1.927 | 2.9164 | 7.7841e-05 | 0.00015 | [5 empty] | 110.32 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 0.469 | [8 empty] | 23.062 | 417.7186 | 1.9218 | 2.9008 | 7.805e-05 | 0.00015 | [5 empty] | 117.98 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 |  |  |  | XS |  | 0.5 | [8 empty] | 23 | 415.4756 | 1.9167 | 2.8852 | 7.8261e-05 | 0.00015 | [5 empty] | 125.61 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 |  |  |  |  | 30 | 0.562 | [8 empty] | 22.876 | 411.0078 | 1.9063 | 2.8542 | 7.8685e-05 | 0.00015 | [5 empty] | 140.81 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 0.625 | [8 empty] | 22.75 | 406.4926 | 1.8958 | 2.8229 | 7.9121e-05 | 0.00015 | [5 empty] | 156.17 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 |  |  |  |  | 40 | 0.688 | [8 empty] | 22.624 | 402.0024 | 1.8853 | 2.7917 | 7.9562e-05 | 0.00015 | [5 empty] | 171.45 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 0.75 | [8 empty] | 22.5 | 397.6078 | 1.875 | 2.7612 | 8e-05 | 0.00015 | [5 empty] | 186.41 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 0.812 | [8 empty] | 22.376 | 393.2374 | 1.8647 | 2.7308 | 8.0443e-05 | 0.00015 | [5 empty] | 201.28 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 0.875 | [8 empty] | 22.25 | 388.8212 | 1.8542 | 2.7001 | 8.0899e-05 | 0.00015 | [5 empty] | 216.31 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 0.938 | [8 empty] | 22.124 | 384.4299 | 1.8437 | 2.6697 | 8.136e-05 | 0.00015 | [5 empty] | 231.25 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 |  |  |  |  | 60 | 0.969 | [8 empty] | 22.062 | 382.2783 | 1.8385 | 2.6547 | 8.1588e-05 | 0.00015 | [5 empty] | 238.57 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 1 | [8 empty] | 22 | 380.1327 | 1.8333 | 2.6398 | 8.1818e-05 | 0.00015 | [5 empty] | 245.87 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 1.062 | [8 empty] | 21.876 | 375.8597 | 1.823 | 2.6101 | 8.2282e-05 | 0.00015 | [5 empty] | 260.41 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 1.125 | [8 empty] | 21.75 | 371.5424 | 1.8125 | 2.5802 | 8.2759e-05 | 0.00015 | [5 empty] | 275.1 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 1.188 | [8 empty] | 21.624 | 367.2501 | 1.802 | 2.5503 | 8.3241e-05 | 0.00015 | [5 empty] | 289.71 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 |  |  |  |  | 80 | 1.219 | [8 empty] | 21.562 | 365.1472 | 1.7968 | 2.5357 | 8.348e-05 | 0.00015 | [5 empty] | 296.86 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 1.25 | [8 empty] | 21.5 | 363.0503 | 1.7917 | 2.5212 | 8.3721e-05 | 0.00015 | [5 empty] | 304 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 1.312 | [8 empty] | 21.376 | 358.8746 | 1.7813 | 2.4922 | 8.4207e-05 | 0.00015 | [5 empty] | 318.21 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 1.375 | [8 empty] | 21.25 | 354.6564 | 1.7708 | 2.4629 | 8.4706e-05 | 0.00015 | [5 empty] | 332.56 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 1.438 | [8 empty] | 21.124 | 350.463 | 1.7603 | 2.4338 | 8.5211e-05 | 0.00015 | [5 empty] | 346.83 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 1.5 | [8 empty] | 21 | 346.3606 | 1.75 | 2.4053 | 8.5714e-05 | 0.00015 | [5 empty] | 360.79 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 |  |  |  |  | 100 | 1.531 | [8 empty] | 20.938 | 344.3184 | 1.7448 | 2.3911 | 8.5968e-05 | 0.00015 | [5 empty] | 367.74 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 | [5 empty] | 1.562 | [8 empty] | 20.876 | 342.2823 | 1.7397 | 2.377 | 8.6223e-05 | 0.00015 | [5 empty] | 374.66 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 |  |  |  |  | 120 | 1.812 | [8 empty] | 20.376 | 326.0827 | 1.698 | 2.2645 | 8.8339e-05 | 0.00015 | [5 empty] | 429.79 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 |  |  |  |  | 140 | 2.062 | [8 empty] | 19.876 | 310.2758 | 1.6563 | 2.1547 | 9.0561e-05 | 0.00015 | [5 empty] | 483.57 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 24 | 600 | 24 |  |  |  |  | 160 | 2.344 | [8 empty] | 19.312 | 292.9169 | 1.6093 | 2.0341 | 9.3206e-05 | 0.00015 | [5 empty] | 542.64 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 26 | 650 | 26 | [5 empty] | 0.25 | [8 empty] | 25.5 | 510.7052 | 2.125 | 3.5466 | 7.0588e-05 | 0.00015 | [5 empty] | 68.82 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 26 | 650 | 26 | [5 empty] | 0.281 | [8 empty] | 25.438 | 508.2247 | 2.1198 | 3.5293 | 7.076e-05 | 0.00015 | [5 empty] | 77.26 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 26 | 650 | 26 |  |  |  |  | 10 | 0.312 | [8 empty] | 25.376 | 505.7504 | 2.1147 | 3.5122 | 7.0933e-05 | 0.00015 | [5 empty] | 85.68 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 26 | 650 | 26 | [5 empty] | 0.344 | [8 empty] | 25.312 | 503.2025 | 2.1093 | 3.4945 | 7.1113e-05 | 0.00015 | [5 empty] | 94.35 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 26 | 650 | 26 |  |  |  | STD |  | 0.375 | [8 empty] | 25.25 | 500.7404 | 2.1042 | 3.4774 | 7.1287e-05 | 0.00015 | [5 empty] | 102.72 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 26 | 650 | 26 | [5 empty] | 0.406 | [8 empty] | 25.188 | 498.2844 | 2.099 | 3.4603 | 7.1463e-05 | 0.00015 | [5 empty] | 111.08 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 26 | 650 | 26 | [5 empty] | 0.438 | [8 empty] | 25.124 | 495.7554 | 2.0937 | 3.4427 | 7.1645e-05 | 0.00015 | [5 empty] | 119.69 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 26 | 650 | 26 | [5 empty] | 0.469 | [8 empty] | 25.062 | 493.3116 | 2.0885 | 3.4258 | 7.1822e-05 | 0.00015 | [5 empty] | 128 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 26 | 650 | 26 |  |  |  | XS | 20 | 0.5 | [8 empty] | 25 | 490.8739 | 2.0833 | 3.4088 | 7.2e-05 | 0.00015 | [5 empty] | 136.3 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 26 | 650 | 26 | [5 empty] | 0.562 | [8 empty] | 24.876 | 486.0165 | 2.073 | 3.3751 | 7.2359e-05 | 0.00015 | [5 empty] | 152.83 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 26 | 650 | 26 | [5 empty] | 0.625 | [8 empty] | 24.75 | 481.1055 | 2.0625 | 3.341 | 7.2727e-05 | 0.00015 | [5 empty] | 169.54 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 26 | 650 | 26 | [5 empty] | 0.688 | [8 empty] | 24.624 | 476.2194 | 2.052 | 3.3071 | 7.3099e-05 | 0.00015 | [5 empty] | 186.16 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 26 | 650 | 26 | [5 empty] | 0.75 | [8 empty] | 24.5 | 471.4352 | 2.0417 | 3.2739 | 7.3469e-05 | 0.00015 | [5 empty] | 202.44 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 26 | 650 | 26 | [5 empty] | 0.812 | [8 empty] | 24.376 | 466.6752 | 2.0313 | 3.2408 | 7.3843e-05 | 0.00015 | [5 empty] | 218.64 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 26 | 650 | 26 | [5 empty] | 0.875 | [8 empty] | 24.25 | 461.8632 | 2.0208 | 3.2074 | 7.4227e-05 | 0.00015 | [5 empty] | 235.01 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 26 | 650 | 26 | [5 empty] | 0.938 | [8 empty] | 24.124 | 457.0761 | 2.0103 | 3.1741 | 7.4614e-05 | 0.00015 | [5 empty] | 251.3 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 26 | 650 | 26 | [5 empty] | 1 | [8 empty] | 24 | 452.3893 | 2 | 3.1416 | 7.5e-05 | 0.00015 | [5 empty] | 267.25 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 28 | 700 | 28 | [5 empty] | 0.25 | [8 empty] | 27.5 | 593.9574 | 2.2917 | 4.1247 | 6.5455e-05 | 0.00015 | [5 empty] | 74.16 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 28 | 700 | 28 | [5 empty] | 0.281 | [8 empty] | 27.438 | 591.2822 | 2.2865 | 4.1061 | 6.5602e-05 | 0.00015 | [5 empty] | 83.26 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 28 | 700 | 28 |  |  |  |  | 10 | 0.312 | [8 empty] | 27.376 | 588.613 | 2.2813 | 4.0876 | 6.5751e-05 | 0.00015 | [5 empty] | 92.35 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 28 | 700 | 28 | [5 empty] | 0.344 | [8 empty] | 27.312 | 585.8641 | 2.276 | 4.0685 | 6.5905e-05 | 0.00015 | [5 empty] | 101.7 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 28 | 700 | 28 |  |  |  | STD |  | 0.375 | [8 empty] | 27.25 | 583.2072 | 2.2708 | 4.0501 | 6.6055e-05 | 0.00015 | [5 empty] | 110.74 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 28 | 700 | 28 | [5 empty] | 0.406 | [8 empty] | 27.188 | 580.5564 | 2.2657 | 4.0316 | 6.6206e-05 | 0.00015 | [5 empty] | 119.76 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 28 | 700 | 28 | [5 empty] | 0.438 | [8 empty] | 27.124 | 577.8264 | 2.2603 | 4.0127 | 6.6362e-05 | 0.00015 | [5 empty] | 129.05 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 28 | 700 | 28 | [5 empty] | 0.469 | [8 empty] | 27.062 | 575.1878 | 2.2552 | 3.9944 | 6.6514e-05 | 0.00015 | [5 empty] | 138.03 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 28 | 700 | 28 |  |  |  | XS | 20 | 0.5 | [8 empty] | 27 | 572.5553 | 2.25 | 3.9761 | 6.6667e-05 | 0.00015 | [5 empty] | 146.99 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 28 | 700 | 28 | [5 empty] | 0.562 | [8 empty] | 26.876 | 567.3083 | 2.2397 | 3.9396 | 6.6974e-05 | 0.00015 | [5 empty] | 164.84 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 28 | 700 | 28 |  |  |  |  | 30 | 0.625 | [8 empty] | 26.75 | 562.0015 | 2.2292 | 3.9028 | 6.729e-05 | 0.00015 | [5 empty] | 182.9 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 28 | 700 | 28 | [5 empty] | 0.688 | [8 empty] | 26.624 | 556.7196 | 2.2187 | 3.8661 | 6.7608e-05 | 0.00015 | [5 empty] | 200.87 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 28 | 700 | 28 | [5 empty] | 0.75 | [8 empty] | 26.5 | 551.5459 | 2.2083 | 3.8302 | 6.7925e-05 | 0.00015 | [5 empty] | 218.48 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 28 | 700 | 28 | [5 empty] | 0.812 | [8 empty] | 26.376 | 546.3963 | 2.198 | 3.7944 | 6.8244e-05 | 0.00015 | [5 empty] | 236 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 28 | 700 | 28 | [5 empty] | 0.875 | [8 empty] | 26.25 | 541.1884 | 2.1875 | 3.7583 | 6.8571e-05 | 0.00015 | [5 empty] | 253.72 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 28 | 700 | 28 | [5 empty] | 0.938 | [8 empty] | 26.124 | 536.0055 | 2.177 | 3.7223 | 6.8902e-05 | 0.00015 | [5 empty] | 271.36 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 28 | 700 | 28 | [5 empty] | 1 | [8 empty] | 26 | 530.9292 | 2.1667 | 3.687 | 6.9231e-05 | 0.00015 | [5 empty] | 288.63 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 |  |  |  |  | 5 | 0.25 | [8 empty] | 29.5 | 683.4928 | 2.4583 | 4.7465 | 6.1017e-05 | 0.00015 | [5 empty] | 79.51 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 | [5 empty] | 0.281 | [8 empty] | 29.438 | 680.6228 | 2.4532 | 4.7265 | 6.1145e-05 | 0.00015 | [5 empty] | 89.27 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 |  |  |  |  | 10 | 0.312 | [8 empty] | 29.376 | 677.7589 | 2.448 | 4.7067 | 6.1275e-05 | 0.00015 | [5 empty] | 99.02 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 | [5 empty] | 0.344 | [8 empty] | 29.312 | 674.8089 | 2.4427 | 4.6862 | 6.1408e-05 | 0.00015 | [5 empty] | 109.06 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 |  |  |  | STD |  | 0.375 | [8 empty] | 29.25 | 671.9572 | 2.4375 | 4.6664 | 6.1538e-05 | 0.00015 | [5 empty] | 118.76 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 | [5 empty] | 0.406 | [8 empty] | 29.188 | 669.1116 | 2.4323 | 4.6466 | 6.1669e-05 | 0.00015 | [5 empty] | 128.44 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 | [5 empty] | 0.438 | [8 empty] | 29.124 | 666.1805 | 2.427 | 4.6263 | 6.1805e-05 | 0.00015 | [5 empty] | 138.42 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 | [5 empty] | 0.469 | [8 empty] | 29.062 | 663.3472 | 2.4218 | 4.6066 | 6.1937e-05 | 0.00015 | [5 empty] | 148.06 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 |  |  |  | XS | 20 | 0.5 | [8 empty] | 29 | 660.5199 | 2.4167 | 4.5869 | 6.2069e-05 | 0.00015 | [5 empty] | 157.68 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 | [5 empty] | 0.562 | [8 empty] | 28.876 | 654.8833 | 2.4063 | 4.5478 | 6.2336e-05 | 0.00015 | [5 empty] | 176.86 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 |  |  |  |  | 30 | 0.625 | [8 empty] | 28.75 | 649.1807 | 2.3958 | 4.5082 | 6.2609e-05 | 0.00015 | [5 empty] | 196.26 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 | [5 empty] | 0.688 | [8 empty] | 28.624 | 643.5029 | 2.3853 | 4.4688 | 6.2884e-05 | 0.00015 | [5 empty] | 215.58 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 | [5 empty] | 0.75 | [8 empty] | 28.5 | 637.9397 | 2.375 | 4.4301 | 6.3158e-05 | 0.00015 | [5 empty] | 234.51 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 | [5 empty] | 0.812 | [8 empty] | 28.376 | 632.4005 | 2.3647 | 4.3917 | 6.3434e-05 | 0.00015 | [5 empty] | 253.36 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 | [5 empty] | 0.875 | [8 empty] | 28.25 | 626.7968 | 2.3542 | 4.3528 | 6.3717e-05 | 0.00015 | [5 empty] | 272.43 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 | [5 empty] | 0.938 | [8 empty] | 28.124 | 621.218 | 2.3437 | 4.314 | 6.4002e-05 | 0.00015 | [5 empty] | 291.41 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 | [5 empty] | 1 | [8 empty] | 28 | 615.7522 | 2.3333 | 4.2761 | 6.4286e-05 | 0.00015 | [5 empty] | 310.01 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 | [5 empty] | 1.062 | [8 empty] | 27.876 | 610.3104 | 2.323 | 4.2383 | 6.4572e-05 | 0.00015 | [5 empty] | 328.53 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 | [5 empty] | 1.125 | [8 empty] | 27.75 | 604.8057 | 2.3125 | 4.2 | 6.4865e-05 | 0.00015 | [5 empty] | 347.26 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 | [5 empty] | 1.188 | [8 empty] | 27.624 | 599.3259 | 2.302 | 4.162 | 6.5161e-05 | 0.00015 | [5 empty] | 365.9 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 30 | 750 | 30 | [5 empty] | 1.25 | [8 empty] | 27.5 | 593.9574 | 2.2917 | 4.1247 | 6.5455e-05 | 0.00015 | [5 empty] | 384.17 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 | [5 empty] | 0.25 | [8 empty] | 31.5 | 779.3113 | 2.625 | 5.4119 | 5.7143e-05 | 0.00015 | [5 empty] | 84.85 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 | [5 empty] | 0.281 | [8 empty] | 31.438 | 776.2466 | 2.6198 | 5.3906 | 5.7256e-05 | 0.00015 | [5 empty] | 95.28 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 |  |  |  |  | 10 | 0.312 | [8 empty] | 31.376 | 773.1879 | 2.6147 | 5.3694 | 5.7369e-05 | 0.00015 | [5 empty] | 105.69 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 | [5 empty] | 0.344 | [8 empty] | 31.312 | 770.0368 | 2.6093 | 5.3475 | 5.7486e-05 | 0.00015 | [5 empty] | 116.41 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 |  |  |  | STD |  | 0.375 | [8 empty] | 31.25 | 766.9904 | 2.6042 | 5.3263 | 5.76e-05 | 0.00015 | [5 empty] | 126.78 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 | [5 empty] | 0.406 | [8 empty] | 31.188 | 763.95 | 2.599 | 5.3052 | 5.7715e-05 | 0.00015 | [5 empty] | 137.12 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 | [5 empty] | 0.438 | [8 empty] | 31.124 | 760.8179 | 2.5937 | 5.2835 | 5.7833e-05 | 0.00015 | [5 empty] | 147.78 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 | [5 empty] | 0.469 | [8 empty] | 31.062 | 757.7897 | 2.5885 | 5.2624 | 5.7949e-05 | 0.00015 | [5 empty] | 158.08 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 |  |  |  | XS | 20 | 0.5 | [8 empty] | 31 | 754.7676 | 2.5833 | 5.2414 | 5.8065e-05 | 0.00015 | [5 empty] | 168.37 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 | [5 empty] | 0.562 | [8 empty] | 30.876 | 748.7416 | 2.573 | 5.1996 | 5.8298e-05 | 0.00015 | [5 empty] | 188.87 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 |  |  |  |  | 30 | 0.625 | [8 empty] | 30.75 | 742.6431 | 2.5625 | 5.1572 | 5.8537e-05 | 0.00015 | [5 empty] | 209.62 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 |  |  |  |  | 40 | 0.688 | [8 empty] | 30.624 | 736.5695 | 2.552 | 5.1151 | 5.8777e-05 | 0.00015 | [5 empty] | 230.29 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 | [5 empty] | 0.75 | [8 empty] | 30.5 | 730.6166 | 2.5417 | 5.0737 | 5.9016e-05 | 0.00015 | [5 empty] | 250.55 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 | [5 empty] | 0.812 | [8 empty] | 30.376 | 724.688 | 2.5313 | 5.0326 | 5.9257e-05 | 0.00015 | [5 empty] | 270.72 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 | [5 empty] | 0.875 | [8 empty] | 30.25 | 718.6884 | 2.5208 | 4.9909 | 5.9504e-05 | 0.00015 | [5 empty] | 291.14 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 | [5 empty] | 0.938 | [8 empty] | 30.124 | 712.7138 | 2.5103 | 4.9494 | 5.9753e-05 | 0.00015 | [5 empty] | 311.47 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 | [5 empty] | 1 | [8 empty] | 30 | 706.8583 | 2.5 | 4.9087 | 6e-05 | 0.00015 | [5 empty] | 331.39 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 | [5 empty] | 1.062 | [8 empty] | 29.876 | 701.0271 | 2.4897 | 4.8682 | 6.0249e-05 | 0.00015 | [5 empty] | 351.23 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 | [5 empty] | 1.125 | [8 empty] | 29.75 | 695.1265 | 2.4792 | 4.8273 | 6.0504e-05 | 0.00015 | [5 empty] | 371.31 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 | [5 empty] | 1.188 | [8 empty] | 29.624 | 689.2508 | 2.4687 | 4.7865 | 6.0762e-05 | 0.00015 | [5 empty] | 391.3 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 32 | 800 | 32 | [5 empty] | 1.25 | [8 empty] | 29.5 | 683.4928 | 2.4583 | 4.7465 | 6.1017e-05 | 0.00015 | [5 empty] | 410.9 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 | [5 empty] | 0.25 | [8 empty] | 33.5 | 881.4131 | 2.7917 | 6.1209 | 5.3731e-05 | 0.00015 | [5 empty] | 90.2 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 | [5 empty] | 0.281 | [8 empty] | 33.438 | 878.1536 | 2.7865 | 6.0983 | 5.3831e-05 | 0.00015 | [5 empty] | 101.29 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 |  |  |  |  | 10 | 0.312 | [8 empty] | 33.376 | 874.9001 | 2.7813 | 6.0757 | 5.3931e-05 | 0.00015 | [5 empty] | 112.36 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 | [5 empty] | 0.344 | [8 empty] | 33.312 | 871.548 | 2.776 | 6.0524 | 5.4035e-05 | 0.00015 | [5 empty] | 123.77 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 |  |  |  | STD |  | 0.375 | [8 empty] | 33.25 | 868.3068 | 2.7708 | 6.0299 | 5.4135e-05 | 0.00015 | [5 empty] | 134.79 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 | [5 empty] | 0.406 | [8 empty] | 33.188 | 865.0716 | 2.7657 | 6.0074 | 5.4236e-05 | 0.00015 | [5 empty] | 145.8 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 | [5 empty] | 0.438 | [8 empty] | 33.124 | 861.7384 | 2.7603 | 5.9843 | 5.4341e-05 | 0.00015 | [5 empty] | 157.14 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 | [5 empty] | 0.469 | [8 empty] | 33.062 | 858.5155 | 2.7552 | 5.9619 | 5.4443e-05 | 0.00015 | [5 empty] | 168.11 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 |  |  |  | XS | 20 | 0.5 | [8 empty] | 33 | 855.2986 | 2.75 | 5.9396 | 5.4545e-05 | 0.00015 | [5 empty] | 179.06 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 | [5 empty] | 0.562 | [8 empty] | 32.876 | 848.883 | 2.7397 | 5.895 | 5.4751e-05 | 0.00015 | [5 empty] | 200.89 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 |  |  |  |  | 30 | 0.625 | [8 empty] | 32.75 | 842.3886 | 2.7292 | 5.8499 | 5.4962e-05 | 0.00015 | [5 empty] | 222.99 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 |  |  |  |  | 40 | 0.688 | [8 empty] | 32.624 | 835.9192 | 2.7187 | 5.805 | 5.5174e-05 | 0.00015 | [5 empty] | 245 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 | [5 empty] | 0.75 | [8 empty] | 32.5 | 829.5768 | 2.7083 | 5.761 | 5.5385e-05 | 0.00015 | [5 empty] | 266.58 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 | [5 empty] | 0.812 | [8 empty] | 32.376 | 823.2586 | 2.698 | 5.7171 | 5.5597e-05 | 0.00015 | [5 empty] | 288.08 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 | [5 empty] | 0.875 | [8 empty] | 32.25 | 816.8632 | 2.6875 | 5.6727 | 5.5814e-05 | 0.00015 | [5 empty] | 309.84 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 | [5 empty] | 0.938 | [8 empty] | 32.124 | 810.4927 | 2.677 | 5.6284 | 5.6033e-05 | 0.00015 | [5 empty] | 331.52 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 | [5 empty] | 1 | [8 empty] | 32 | 804.2477 | 2.6667 | 5.5851 | 5.625e-05 | 0.00015 | [5 empty] | 352.77 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 | [5 empty] | 1.062 | [8 empty] | 31.876 | 798.0269 | 2.6563 | 5.5419 | 5.6469e-05 | 0.00015 | [5 empty] | 373.94 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 | [5 empty] | 1.125 | [8 empty] | 31.75 | 791.7304 | 2.6458 | 5.4981 | 5.6693e-05 | 0.00015 | [5 empty] | 395.36 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 | [5 empty] | 1.188 | [8 empty] | 31.624 | 785.4589 | 2.6353 | 5.4546 | 5.6919e-05 | 0.00015 | [5 empty] | 416.7 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 34 | 850 | 34 | [5 empty] | 1.25 | [8 empty] | 31.5 | 779.3113 | 2.625 | 5.4119 | 5.7143e-05 | 0.00015 | [5 empty] | 437.62 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 36 | 900 | 36 | [5 empty] | 0.25 | [8 empty] | 35.5 | 989.798 | 2.9583 | 6.8736 | 5.0704e-05 | 0.00015 | [5 empty] | 95.54 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 36 | 900 | 36 | [5 empty] | 0.281 | [8 empty] | 35.438 | 986.3437 | 2.9532 | 6.8496 | 5.0793e-05 | 0.00015 | [5 empty] | 107.3 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 36 | 900 | 36 |  |  |  |  | 10 | 0.312 | [8 empty] | 35.376 | 982.8955 | 2.948 | 6.8257 | 5.0882e-05 | 0.00015 | [5 empty] | 119.03 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 36 | 900 | 36 | [5 empty] | 0.344 | [8 empty] | 35.312 | 979.3423 | 2.9427 | 6.801 | 5.0974e-05 | 0.00015 | [5 empty] | 131.12 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 36 | 900 | 36 |  |  |  | STD |  | 0.375 | [8 empty] | 35.25 | 975.9063 | 2.9375 | 6.7771 | 5.1064e-05 | 0.00015 | [5 empty] | 142.81 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 36 | 900 | 36 | [5 empty] | 0.406 | [8 empty] | 35.188 | 972.4763 | 2.9323 | 6.7533 | 5.1154e-05 | 0.00015 | [5 empty] | 154.48 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 36 | 900 | 36 | [5 empty] | 0.438 | [8 empty] | 35.124 | 968.9421 | 2.927 | 6.7288 | 5.1247e-05 | 0.00015 | [5 empty] | 166.51 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 36 | 900 | 36 | [5 empty] | 0.469 | [8 empty] | 35.062 | 965.5244 | 2.9218 | 6.705 | 5.1338e-05 | 0.00015 | [5 empty] | 178.14 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 36 | 900 | 36 |  |  |  | XS | 20 | 0.5 | [8 empty] | 35 | 962.1128 | 2.9167 | 6.6813 | 5.1429e-05 | 0.00015 | [5 empty] | 189.75 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 36 | 900 | 36 | [5 empty] | 0.562 | [8 empty] | 34.876 | 955.3076 | 2.9063 | 6.6341 | 5.1611e-05 | 0.00015 | [5 empty] | 212.9 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 36 | 900 | 36 |  |  |  |  | 30 | 0.625 | [8 empty] | 34.75 | 948.4174 | 2.8958 | 6.5862 | 5.1799e-05 | 0.00015 | [5 empty] | 236.35 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 36 | 900 | 36 | [5 empty] | 0.688 | [8 empty] | 34.624 | 941.5521 | 2.8853 | 6.5386 | 5.1987e-05 | 0.00015 | [5 empty] | 259.71 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 36 | 900 | 36 |  |  |  |  | 40 | 0.75 | [8 empty] | 34.5 | 934.8202 | 2.875 | 6.4918 | 5.2174e-05 | 0.00015 | [5 empty] | 282.62 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 36 | 900 | 36 | [5 empty] | 0.812 | [8 empty] | 34.376 | 928.1124 | 2.8647 | 6.4452 | 5.2362e-05 | 0.00015 | [5 empty] | 305.44 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 36 | 900 | 36 | [5 empty] | 0.875 | [8 empty] | 34.25 | 921.3211 | 2.8542 | 6.3981 | 5.2555e-05 | 0.00015 | [5 empty] | 328.55 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 36 | 900 | 36 | [5 empty] | 0.938 | [8 empty] | 34.124 | 914.5548 | 2.8437 | 6.3511 | 5.2749e-05 | 0.00015 | [5 empty] | 351.57 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018
IV | Characteristics of Piping Materials | A | Steel Pipe | 1 | Steel pipe - welded and seamless wrought | 36 | 900 | 36 | [5 empty] | 1 | [8 empty] | 34 | 907.9203 | 2.8333 | 6.305 | 5.2941e-05 | 0.00015 | [5 empty] | 374.15 | [15 empty] | Pages 3 - 16 | Table 2-1 | ANSI/ASME B36.10M-2018

## Flange Data
Date last modified: 11-June-2019 (J.DAWLEY)
EDB Section | Section Name | Group | Group Name | Sub-Division | Sub-Division Name | Flange Class | Nominal Pipe Size | Outside Diameter of Flange D | Flange Thickness (Min) - Flange C | Flange Thickness (Min) - Fitting C | Drilling - Diameter of Bolt Circle | Drilling - Diameter of Bolt Holes | Drilling - Number of Bolts | Drilling - Diameter of Bolts | Length of Bolts L - Stud Bolts - 0.006 In. Raised Face | Length of Bolts L - Stud Bolts - RIng Joint | Length of Bolts L - Machine Bolts - 0.006 In. Raised Face | Length of Bolts L - Stud Bolts - 1/4 In. Raised Face | Length of Stud Bolts L - Male and Female also Tongue & Groove | Length of Stud Bolts L - RIng Joint
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 0.5 | 3.5 | 0.4375 | -- | 2.375 | 0.625 | 4 | 0.5 | 2.5 | 3 | 2.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 0.75 | 3.875 | 0.5 | -- | 2.75 | 0.625 | 4 | 0.5 | 3 | 3.5 | 2.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 1 | 4.25 | 0.5625 | 0.4375 | 3.125 | 0.625 | 4 | 0.5 | 3 | 3.5 | 2.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 1.25 | 4.625 | 0.625 | 0.5 | 3.5 | 0.625 | 4 | 0.5 | 3.25 | 3.75 | 2.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 1.5 | 5 | 0.6875 | 0.5625 | 3.875 | 0.625 | 4 | 0.5 | 3.5 | 4 | 3
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 2 | 6 | 0.75 | 0.625 | 4.75 | 0.75 | 4 | 0.625 | 3.5 | 4 | 3
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 2.5 | 7 | 0.875 | 0.6875 | 5.5 | 0.75 | 4 | 0.625 | 4 | 4.5 | 3.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 3 | 7.5 | 0.9375 | 0.75 | 6 | 0.75 | 4 | 0.625 | 4.25 | 4.75 | 3.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 3.5 | 8.5 | 0.9375 | 0.8125 | 7 | 0.75 | 8 | 0.625 | 4.25 | 5 | 3.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 4 | 9 | 0.9375 | 0.9375 | 7.5 | 0.75 | 8 | 0.625 | 4.25 | 5 | 3.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 5 | 10 | 0.9375 | 0.9375 | 8.5 | 0.875 | 8 | 0.75 | 4.75 | 5.25 | 4.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 6 | 11 | 1 | 1 | 9.5 | 0.875 | 8 | 0.75 | 4.75 | 5.5 | 4.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 8 | 13.5 | 1.125 | 1.125 | 11.75 | 0.875 | 8 | 0.75 | 5.5 | 6 | 4.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 10 | 16 | 0.8125 | 0.8125 | 14.25 | 1 | 12 | 0.875 | 6.25 | 6.75 | 5.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 12 | 19 | 1.25 | 1.25 | 17 | 1 | 12 | 0.875 | 6.75 | 7.25 | 5.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 14 | 21 | 1.375 | 1.375 | 18.75 | 1.125 | 12 | 1 | 7 | 7.5 | 6.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 16 | 23.5 | 1.4375 | 1.4375 | 21.25 | 1.125 | 16 | 1 | 7.5 | 8 | 6.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 18 | 25 | 1.5625 | 1.5625 | 22.75 | 1.25 | 16 | 1.125 | 7.75 | 8.25 | 6.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 20 | 27.5 | 1.6875 | 1.6875 | 25 | 1.25 | 20 | 1.125 | 8 | 8.75 | 7.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 150-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 150 | 24 | 32 | 1.875 | 1.875 | 29.5 | 1.25 | 20 | 1.25 | 9 | 10 | 8
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 0.5 | 3.75 | 0.5625 |  | 2.625 | 0.625 | 4 | 0.5 | 2.5 | 3 | 2.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 0.75 | 4.625 | 0.625 |  | 3.25 | 0.75 | 4 | 0.625 | 3 | 3.5 | 2.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 1 | 4.875 | 0.6875 |  | 3.5 | 0.75 | 4 | 0.625 | 3 | 3.5 | 2.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 1.25 | 5.25 | 0.75 |  | 3.875 | 0.75 | 4 | 0.625 | 3.25 | 3.75 | 2.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 1.5 | 6.125 | 0.8125 |  | 4.5 | 0.875 | 4 | 0.75 | 3.5 | 4 | 3
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 2 | 6.25 | 0.875 |  | 5 | 0.75 | 4 | 0.625 | 3.5 | 4 | 3
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 2.5 | 7.5 | 1 |  | 5.4375 | 0.875 | 8 | 0.75 | 4 | 4.5 | 3.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 3 | 8.25 | 1.125 |  | 6.625 | 0.875 | 8 | 0.75 | 4.255 | 4.75 | 3.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 3.5 | 9 | 1.1875 |  | 7.25 | 0.875 | 8 | 0.75 | 4.25 | 5 | 3.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 4 | 10 | 1.25 |  | 7.875 | 0.875 | 8 | 0.75 | 4.5 | 5 | 3.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 5 | 11 | 1.375 |  | 9.25 | 0.875 | 8 | 0.75 | 4.75 | 5.25 | 4.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 6 | 12.5 | 1.4375 |  | 10.625 | 0.875 | 12 | 0.75 | 4.75 | 5.5 | 4.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 8 | 15 | 1.625 |  | 13 | 1 | 12 | 0.875 | 5.5 | 6 | 4.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 10 | 17.5 | 1.875 |  | 15.25 | 1.125 | 16 | 1 | 6.25 | 6.75 | 5.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 12 | 20.5 | 2 |  | 17.75 | 1.25 | 16 | 1.125 | 6.75 | 7.25 | 5.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 14 | 23 | 2.125 |  | 20.25 | 1.25 | 20 | 1.125 | 7 | 7.5 | 6.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 16 | 25.5 | 2.25 |  | 22.5 | 1.375 | 20 | 1.25 | 7.5 | 8 | 6.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 18 | 28 | 2.375 |  | 24.75 | 1.375 | 24 | 1.25 | 7.75 | 8.25 | 6.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 20 | 30.5 | 2.5 |  | 27 | 0.1375 | 24 | 1.25 | 8 | 8.75 | 7.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 300-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 300 | 24 | 36 | 2.75 |  | 32 | 1.625 | 24 | 1.5 | 9 | 10 | 8
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 0.5 | 3.75 | 0.5625 |  | 2.625 | 0.625 | 4 | 0.5 |  |  |  | 3 | 2.75 | 3
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 0.75 | 4.625 | 0.625 |  | 3.25 | 0.75 | 4 | 0.625 |  |  |  | 3.5 | 3.25 | 3.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 1 | 4.875 | 0.6875 |  | 3.5 | 0.75 | 4 | 0.625 |  |  |  | 3.5 | 3.25 | 3.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 1.25 | 5.25 | 0.8125 |  | 3.875 | 0.75 | 4 | 0.625 |  |  |  | 3.75 | 3.5 | 3.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 1.5 | 6.125 | 0.875 |  | 4.5 | 0.875 | 4 | 0.75 |  |  |  | 4.25 | 4 | 4.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 2 | 6.5 | 1 |  | 5 | 0.75 | 8 | 0.625 |  |  |  | 4.25 | 4 | 4.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 2.5 | 7.5 | 1.125 |  | 5.875 | 0.875 | 8 | 0.75 |  |  |  | 4.75 | 4.5 | 4.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 3 | 8.25 | 1.25 |  | 6.625 | 0.875 | 8 | 0.75 |  |  |  | 5 | 4.75 | 5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 3.5 | 9 | 1.375 |  | 7.25 | 1 | 8 | 0.875 |  |  |  | 5.5 | 5.25 | 5.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 4 | 10 | 1.375 |  | 7.875 | 1 | 8 | 0.875 |  |  |  | 5.5 | 5.25 | 5.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 5 | 11 | 1.5 |  | 9.25 | 1 | 8 | 0.875 |  |  |  | 5.75 | 5.5 | 5.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 6 | 12.5 | 1.625 |  | 10.625 | 1 | 12 | 0.875 |  |  |  | 6 | 5.75 | 6
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 8 | 15 | 1.875 |  | 13 | 1.125 | 12 | 1 |  |  |  | 6.75 | 6.5 | 6.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 10 | 17.5 | 2.125 |  | 15.25 | 1.25 | 16 | 1.125 |  |  |  | 7.5 | 7.25 | 7.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 12 | 20.5 | 2.25 |  | 17.75 | 1.375 | 16 | 1.25 |  |  |  | 8 | 7.75 | 8
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 14 | 23 | 2.375 |  | 20.25 | 1.375 | 20 | 1.25 |  |  |  | 8.25 | 8 | 8.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 16 | 25.5 | 2.5 |  | 22.5 | 1.5 | 20 | 1.375 |  |  |  | 8.75 | 8.5 | 8.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 18 | 28 | 2.625 |  | 24.75 | 1.5 | 24 | 1.375 |  |  |  | 9 | 8.75 | 9
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 20 | 30.5 | 2.75 |  | 27 | 1.625 | 24 | 1.5 |  |  |  | 9.5 | 9.25 | 9.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 400-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 400 | 24 | 36 | 3 |  | 32 | 1.875 | 24 | 1.775 |  |  |  | 10.5 | 10.25 | 11
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 0.5 | 3.75 | 0.5625 |  | 2.625 | 0.625 | 4 | 0.5 |  |  |  | 3 | 2.75 | 3
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 0.75 | 4.625 | 0.625 |  | 3.25 | 0.75 | 4 | 0.625 |  |  |  | 3.5 | 3.25 | 3.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 1 | 4.875 | 0.6875 |  | 3.5 | 0.75 | 4 | 0.625 |  |  |  | 3.5 | 3.25 | 3.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 1.25 | 5.25 | 0.8125 |  | 3.875 | 0.75 | 4 | 0.625 |  |  |  | 3.75 | 3.5 | 3.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 1.5 | 6.125 | 0.875 |  | 4.5 | 0.875 | 4 | 0.75 |  |  |  | 4.25 | 4 | 4.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 2 | 6.5 | 1 |  | 5 | 0.75 | 8 | 0.625 |  |  |  | 4.25 | 4 | 4.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 2.5 | 7.5 | 1.125 |  | 5.875 | 0.875 | 8 | 0.75 |  |  |  | 4.75 | 4.5 | 4.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 3 | 8.25 | 1.25 |  | 6.625 | 0.875 | 8 | 0.75 |  |  |  | 5 | 4.75 | 5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 3.5 | 9 | 1.375 |  | 7.25 | 1 | 8 | 0.875 |  |  |  | 5.5 | 5.25 | 5.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 4 | 10.75 | 1.5 |  | 8.5 | 1 | 8 | 0.875 |  |  |  | 5.75 | 5.5 | 5.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 5 | 13 | 1.75 |  | 10.5 | 1.125 | 8 | 1 |  |  |  | 6.5 | 6.25 | 6.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 6 | 14 | 1.875 |  | 11.5 | 1.125 | 12 | 1 |  |  |  | 6.75 | 6.5 | 6.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 8 | 16.5 | 2.1875 |  | 13.75 | 1.25 | 12 | 1.125 |  |  |  | 7.5 | 7.25 | 7.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 10 | 20 | 2.5 |  | 17 | 1.375 | 16 | 1.25 |  |  |  | 8.5 | 8.5 | 8.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 12 | 22 | 2.625 |  | 19.25 | 1.375 | 20 | 1.25 |  |  |  | 8.75 | 8.5 | 8.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 14 | 23.75 | 2.75 |  | 20.75 | 1.5 | 20 | 1.375 |  |  |  | 9.25 | 9 | 9.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 16 | 27 | 3 |  | 23.75 | 1.625 | 20 | 1.5 |  |  |  | 10 | 9.75 | 10
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 18 | 29.25 | 3.25 |  | 25.75 | 1.75 | 20 | 1.625 |  |  |  | 10.75 | 10.5 | 10.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 20 | 32 | 3.5 |  | 28.5 | 1.75 | 24 | 1.625 |  |  |  | 11.25 | 11 | 11.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 600-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 600 | 24 | 37 | 4 |  | 33 | 2 | 24 | 1.875 |  |  |  | 13 | 12.75 | 13.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 0.5 | 4.75 | 0.875 |  | 3.25 | 0.875 | 4 | 0.75 |  |  |  | 4.5 | 4 | 4.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 0.75 | 5.125 | 1 |  | 3.5 | 0.875 | 4 | 0.75 |  |  |  | 4.5 | 4.25 | 4.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 1 | 5.875 | 1.125 |  | 4 | 1 | 4 | 0.875 |  |  |  | 5 | 4.75 | 5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 1.25 | 6.25 | 1.125 |  | 4.375 | 1 | 4 | 0.875 |  |  |  | 5 | 4.75 | 5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 1.5 | 7 | 1.25 |  | 4.875 | 1.125 | 4 | 1 |  |  |  | 5.5 | 5.25 | 5.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 2 | 8.5 | 1.5 |  | 6.5 | 1 | 8 | 0.875 |  |  |  | 5.75 | 5.5 | 5.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 2.5 | 9.375 | 1.625 |  | 7.5 | 1.125 | 8 | 1 |  |  |  | 6.25 | 6 | 6.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 3 | 9 | 1.5 |  | 7.5 | 1 | 8 | 0.875 |  |  |  | 5.75 | 5.5 | 5.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 4 | 11.5 | 1.75 |  | 9.25 | 1.25 | 8 | 1.125 |  |  |  | 6.75 | 6.5 | 6.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 5 | 13.75 | 2 |  | 11 | 1.375 | 8 | 1.25 |  |  |  | 7.5 | 7.25 | 7.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 6 | 15 | 2.1875 |  | 12.5 | 1.25 | 12 | 1.125 |  |  |  | 7.5 | 7.25 | 7.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 8 | 18.5 | 2.5 |  | 15.5 | 1.5 | 12 | 1.375 |  |  |  | 8.75 | 8.5 | 8.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 10 | 21.5 | 2.75 |  | 18.5 | 1.5 | 16 | 1.375 |  |  |  | 9.25 | 9 | 9.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 12 | 24 | 3.125 |  | 21 | 1.5 | 20 | 1.375 |  |  |  | 10 | 9.75 | 10
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 14 | 25.25 | 3.375 |  | 22 | 1.625 | 20 | 1.5 |  |  |  | 10.75 | 10.5 | 11
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 16 | 27.75 | 3.5 |  | 24.25 | 1.75 | 20 | 1.625 |  |  |  | 11.25 | 11 | 11.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 18 | 31 | 4 |  | 27 | 2 | 20 | 1.875 |  |  |  | 12.75 | 12.5 | 13.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 20 | 33.25 | 4.25 |  | 29.5 | 2.125 | 20 | 2 |  |  |  | 13.75 | 13.5 | 14.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 900-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 900 | 24 | 41 | 5.5 |  | 35.5 | 2.625 | 20 | 2.5 |  |  |  | 17.25 | 17 | 18
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 0.5 | 4.75 | 0.875 |  | 3.25 | 0.875 | 4 | 0.75 |  |  |  | 4.5 | 4 | 4.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 0.75 | 5.125 | 1 |  | 3.5 | 0.875 | 4 | 0.75 |  |  |  | 4.5 | 4.25 | 4.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 1 | 5.875 | 1.125 |  | 4 | 1 | 4 | 0.875 |  |  |  | 5 | 4.75 | 5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 1.25 | 6.25 | 1.125 |  | 4.375 | 1 | 4 | 0.875 |  |  |  | 5 | 4.75 | 5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 1.5 | 7 | 1.25 |  | 4.875 | 1.125 | 4 | 1 |  |  |  | 5.5 | 5.25 | 5.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 2 | 8.5 | 1.5 |  | 6.5 | 1 | 8 | 0.875 |  |  |  | 5.75 | 5.5 | 5.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 2.5 | 9.375 | 1.625 |  | 7.5 | 1.125 | 8 | 1 |  |  |  | 6.25 | 6 | 6.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 3 | 10.5 | 1.875 |  | 8 | 1.25 | 8 | 1.125 |  |  |  | 7 | 6.75 | 7
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 4 | 12.25 | 2.125 |  | 9.5 | 1.375 | 8 | 1.25 |  |  |  | 7.75 | 7.5 | 7.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 5 | 14.75 | 2.875 |  | 11.5 | 1.625 | 8 | 1.5 |  |  |  | 9.75 | 9.5 | 9.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 6 | 15.5 | 3.25 |  | 12.5 | 1.5 | 12 | 1.375 |  |  |  | 10.5 | 10 | 10.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 8 | 19 | 3.625 |  | 15.5 | 1.75 | 12 | 1.625 |  |  |  | 11.5 | 11.25 | 12.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 10 | 23 | 4.25 |  | 19 | 2 | 12 | 1.875 |  |  |  | 13.25 | 13 | 13.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 12 | 26.5 | 4.875 |  | 22.5 | 2.125 | 16 | 2 |  |  |  | 14.75 | 14.5 | 15.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 14 | 29.5 | 5.25 |  | 25 | 2.375 | 16 | 2.25 |  |  |  | 16 | 15.75 | 16.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 16 | 32.5 | 5.75 |  | 25.75 | 2.625 | 16 | 2.5 |  |  |  | 17.5 | 17.25 | 18.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 18 | 36 | 6.375 |  | 30.5 | 2.875 | 16 | 2.75 |  |  |  | 19.5 | 19.25 | 20.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 20 | 38.75 | 7 |  | 32.75 | 3.125 | 16 | 3 |  |  |  | 21.5 | 21 | 22.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 1500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 1500 | 24 | 46 | 8 |  | 39 | 3.625 | 16 | 3.5 |  |  |  | 24.25 | 24 | 25.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 2500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 2500 | 0.5 | 5.25 | 1.1875 |  | 3.5 | 0.875 | 4 | 0.75 |  |  |  | 4.75 | 4.5 | 4.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 2500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 2500 | 0.75 | 5.5 | 1.25 |  | 3.75 | 0.875 | 4 | 0.75 |  |  |  | 5 | 4.75 | 5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 2500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 2500 | 1 | 6.25 | 1.375 |  | 4.25 | 1 | 4 | 0.875 |  |  |  | 5.5 | 5.25 | 5.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 2500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 2500 | 1.25 | 7.25 | 1.5 |  | 5.125 | 1.125 | 4 | 1 |  |  |  | 6 | 5.75 | 6
IV | Characteristics of Piping Materials | E | Flanges | 1 | 2500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 2500 | 1.5 | 8 | 1.75 |  | 5.75 | 1.25 | 4 | 1.125 |  |  |  | 6.75 | 6.5 | 6.75
IV | Characteristics of Piping Materials | E | Flanges | 1 | 2500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 2500 | 2 | 9.25 | 2 |  | 6.75 | 1.125 | 8 | 1 |  |  |  | 7 | 6.75 | 7
IV | Characteristics of Piping Materials | E | Flanges | 1 | 2500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 2500 | 2.5 | 10.5 | 2.25 |  | 7.75 | 1.25 | 8 | 1.125 |  |  |  | 7.75 | 7.5 | 8
IV | Characteristics of Piping Materials | E | Flanges | 1 | 2500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 2500 | 3 | 12 | 2.625 |  | 9 | 1.375 | 8 | 1.25 |  |  |  | 8.75 | 8.5 | 9
IV | Characteristics of Piping Materials | E | Flanges | 1 | 2500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 2500 | 4 | 14 | 3 |  | 10.75 | 1.625 | 8 | 1.5 |  |  |  | 10 | 9.75 | 10.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 2500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 2500 | 5 | 16.5 | 3.625 |  | 12.75 | 1.875 | 8 | 1.75 |  |  |  | 11.75 | 11.5 | 12.25
IV | Characteristics of Piping Materials | E | Flanges | 1 | 2500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 2500 | 6 | 19 | 4.25 |  | 14.5 | 2.125 | 8 | 2 |  |  |  | 13.5 | 13.25 | 14
IV | Characteristics of Piping Materials | E | Flanges | 1 | 2500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 2500 | 8 | 21.75 | 5 |  | 17.25 | 2.125 | 12 | 2 |  |  |  | 15 | 14.75 | 15.5
IV | Characteristics of Piping Materials | E | Flanges | 1 | 2500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 2500 | 10 | 26.5 | 6.5 |  | 21.25 | 2.625 | 12 | 2.5 |  |  |  | 19.25 | 19 | 20
IV | Characteristics of Piping Materials | E | Flanges | 1 | 2500-LB STEEL PIPE FLANGES AND FLANGED FITTINGS | 2500 | 12 | 30 | 7.25 |  | 24.375 | 2.875 | 12 | 2.75 |  |  |  | 21.25 | 21 | 22
[7 empty] | 0.5 | [13 empty] | 1.375 | 0.71875 | 1.375
[7 empty] | 0.75 | [13 empty] | 1.6875 | 0.9375 | 1.6875
[7 empty] | 1 | [13 empty] | 2 | 1.1875 | 1.875
[7 empty] | 1.25 | [13 empty] | 2.5 | 1.5 | 2.25
[7 empty] | 1.5 | [13 empty] | 2.875 | 1.75 | 2.5
[7 empty] | 2 | [13 empty] | 3.625 | 2.25
[7 empty] | 2.5 | [13 empty] | 4.125 | 2.6875
[7 empty] | 3 | [13 empty] | 5 | 3.3125
[7 empty] | 3.5 | [13 empty] | 5.5 | 3.8125
[7 empty] | 4 | [13 empty] | 6.1875 | 4.3125
[7 empty] | 5 | [13 empty] | 7.3125 | 5.375
[7 empty] | 6 | [13 empty] | 8.5 | 6.375
[7 empty] | 8 | [13 empty] | 10.625 | 8.375
[7 empty] | 10 | [13 empty] | 12.75 | 10.5
[7 empty] | 12 | [13 empty] | 15 | 12.5
[7 empty] | 14 | [13 empty] | 16.25 | 13.75
[7 empty] | 16 | [13 empty] | 18.5 | 15.75
[7 empty] | 18 | [13 empty] | 21 | 17.75
[7 empty] | 20 | [13 empty] | 23 | 19.75
[7 empty] | 24 | [13 empty] | 27.25 | 23.75

## Sources
Pipe Roughness Factor
Material | e (feet) | Souce